## Sheet1
SR.No. | Zone | Incident no | Creation Date | KVA | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Run hours | Observation | Incident Status | ASM Name | HO remark | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22
12 | South | 211642000 | 25-01-2025 09:52 | 40 | 3H.8951.../2421079 | ErrorCode Problem Call by : Customer Name :Dhinesh Kumar Contact :9442651353 | Closed | PKP Educational Trust | Electro Controls - Erode | 7 | VISITED THE SITE FOUND ERROR CODE DISPLAYED SPN 5838 FMI-1,SPN 2791 FMI 18, SO flash the ECU after checking parameters | Closed | Mr. Sanjaimon S
13 | South | 211641954 | 25-01-2025 09:39 | 82.5 | 5H.8901.../2420824 | Voltage Fluctuation | Closed | PR TIJO THOMAS | G-Care Diesels Private Limited - Ernakulam | 13 | Connect I Konnect tool and clear the error (SPN=3031,FMI =14 in I Konnect tool)code and checked engine Start and stopping after work DG started working available load now dg running performance satisfactory.voltage fluctuation not in this site . | Closed | Mr. Sanjaimon S
55 | South | 211653335 | 28-01-2025 15:57 | 125.4 | 4H.8041.../2420579 | Alarm issue Call by : Customer Name : Uthya Kumar Contact : 8610530397 | Closed | Sathana Mahal | Bharath Diesel Sales and Service - Karaikal | 27.4 | Inspected the DG set found. Error code spn 1761 FMI 16 checked the DEF level low alarm 36% so new DEF level filled found ok. Error code clear found ok | Closed | Mr. NandhaGopal
43 | North | 211674420 | 2025-01-02 15:54 | 400 | DV8.8542.C4../2420137 | ECU Amber Alarm Issue Call By Customer Name - Suresh Kumar Number - 9465181003 | Closed | RR JAIN INDUSTRIES | Industrial Power Solutions - LUDHIANA | 43 | SPN/FMI-523584/15;AdBlue Level Low in Tank 2 so advised same to fill AdBlue before it comes below 50% | Closed | Ved Prakash Gupta
4 | East | 211664444 | 31-01-2025 10:22 | 250 | F6.8841.../2420132 | Starting Issue. Call By Customer. Name:- Lasto Mobile No.:-6000647321 | Closed | M/S Majena Infra Project | Hibreed Engineering Pvt. Ltd. - Jorhat | 118 | SPN 1761 FMI 16 low urea level alarm so top up the DEF and cleared the code also educated customer to maintain minimum 50% DEF | CLOSED | Ujjwal Das
7 | East | 211662254 | 30-01-2025 17:04 | 58.5 | T4.8941.../2422791 | Abnormal sound issue Call by customer Name: Amrendra Kumar Number:8873967757 | Task Start | apna awas const pvt ltd | Globalline India Services Private Limited - Patna | 14.2 | SPN: 2791,FMI: 1/6/18 fault code were present in Ikonnect so SE checked EGR it found ok no clogging then cleared Code and flash the ECU by normal app file code cleared issue resolved but in under observation as SE not flashed the dummy file so on next visit dummy file neede to flash. | CLOSED | Prabhakar Kumar
8 | WEST | 211664638 | 31-01-2025 10:55 | 125.4 | 4H.8041.../2420093 | Under Speed Alarm Call By Customer Name - Vishal No - 9730711011 | Closed | Rhenus Contract Logistics India Private Limited | Transcreek Engineers Pvt. Ltd. - Bhiwandi | 153 | SPN: 1761 FMI: 16 ,Low adblue level , top up adblue level. | closed | Jagdeep saini
23 | North | 211676829 | 2025-02-02 12:10 | 40 | 3H.8951.../2320061 | Starting Issue Call By Customer Name :- Aashu Jaiswal Mobile No :- 9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 715.35 | SPN/FMI 97/2 check in water seprator found no water traces in seprator check in tank found no issue so, clear the code then issue resolve | Closed | Kapil Solanki
39 | North | 211664604 | 31-01-2025 10:46 | 15 | GP3.8501.../2420094 | fuel alram | Closed | Dhani Power Solutions | SAAN Royal Power Solutions Private Limited - Rohtak | 109 | SPN/FMI-96/0 ; High Fuel Level ;Reduce some Fuel & same educated to customer to top-up fuel max. 95% | Closed | Ved Prakash Gupta
43 | North | 211675255 | 2025-01-02 17:40 | 320 | F6.8802.../2420279 | Genset Trip | Closed | Orchid Hospitality Services Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 41 | SPN/FMI-1761/16 ; Found AdBlue 18% ; Top-up the same & resolved the same | Closed | Ved Prakash Gupta
45 | North | 211673445 | 2025-01-02 11:54 | 57 | T4.8941.../2320042 | Starting/Stopping Issue | Closed | Sceptre Medical India Pvt Ltd | SAAN Royal Power Solutions Private Limited - Sonipat | 786.44 | SPN/FMI-97/2 Water in Fuel;drain fuel from water separator & found water traces in fuel,same found from tank also;clean the tank & water separator filter & run the DG after re-fill the Fuel ,issue resolved | Closed | Ved Prakash Gupta
8 | East | 211678007 | 2025-03-02 11:21 | 125.4 | 4H.8042.C4../2420815 | Starting/Stopping Issue | Open | Sailaja Commercial Construction Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 39 | SPN: 3031,FMI: 14 - SCR Monitoring - Urea Tank Temperature - Bank 1 - Special In | OPEN | Ujjwal Das
9 | East | 211676998 | 2025-02-02 20:46 | 30 | 3H.8902.../2420962 | Starting/Stopping Issue | Task Start | Guwahati Industrial Sales & Service. | M T Enterprises - Bomdila | 54 | SPN: 2791,FMI: 31, SPN: 5838,FMI: 1 cleaned EGR but EGR was jammed due to customer maximum time operate in DG no load ,today SE again visit site with new EGR | OPEN | Ujjwal Das
4 | West | 211678994 | 2025-03-02 15:10 | 40 | 3H.8951.../2421054 | Starting/Stopping Issue | Task Start | ATC Telecom Infrastructure Private Limited | Natraj Power Tech - Gwalior | 1 | SPN/FMI- 2802/4, Battery and charging alternator connections were checked, found OK. ECU power supply 4 and 6(+) were checked, no power supply was found, so all wires on distribution block XDBK2 were tightened and problem was solved. | OPEN | Vijay Patil
11 | South | 211682239 | 2025-04-02 14:50 | 320 | F6.8802.../2420189 | AMF Pannel Problem Call by : Customer Name :Ramachandharen Contact :9445727472 | Task Start | Cosmo City Residents Welfare Association | Bharath Diesel Sales and Service - Karappakkam | 58.1 | Visit the site checked the generator found engine tripping in ECU malfunction. Connect the ikonnect ERROR CODE showing SPN=4375/16 and removed the DEF tank filter checked the allingmant refitted and checked the other parameters found normal started the generator run with load found normal. | Closed | Mr. NandhaGopal
10 | North | 211681008 | 2025-04-02 11:16 | 58.5 | T4.8941.../2422858 | Egr jamed | Task Start | PROFFESSIONAL | Suraj Motor Store - Srinagar |  | SPN/FMI 2791/5 EGR valve jammed, Replace the same clear the code with i-konnect tool then issue resolve | Closed | Ved Prakash Gupta
17 | North | 211679229 | 2025-03-02 16:13 | 50 | T4.8941.../2420659 | Starting Issue Call By Customer Name : Virendra Singh No : 7889601565 | Task Start | Administrative Reforms Department Uttar Pradesh. | Deep Jyoti Electricals and Services - Moradabad | 212 | SPN/FMI 2802/4 , 157/14 DG Fail to start check and found voltage drop after that Relay will be interchange | Closed | Sudhir Awasthi
3 | East | 211685802 | 2025-05-02 15:52 | 250 | F6.8841.../2420332 | Starting/Stopping Issue | Open | Bishop Westcot School | HACS Engineering and Tech Private Limited - Ranchi | 30 | SPN -3031 Fmi 1, SPN 516166 FMI 0 and SPN 1761 FMI 16 so cleared the code from DTC first two code cleared but SPN 1761 was there duet to the DEF level was 40 % so need to topup | CLOSED | Prabhakar Kumar
20 | South | 211685563 | 2025-05-02 15:04 | 250 | F6.8842.C4../2420081 | ECU MALFUNCTIONING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the dg ECU override time ECU malfunction alarm blinking, so connected the I connect check the spn 4363 fmi 3 error coad not clear, so need new ecu for checking | Tast Start | Mr. NandhaGopal
19 | West | 211695219 | 2025-08-02 09:43 | 58.5 | T4.8941.../2422980 | starting issue | Task Start | POPULAR MARKETING & SERVICES. | Unique Techno Services Pvt Ltd. - Dahej | LR | SPN/FMI-97/5(Water in Fuel_ Self test) Engine was not starting so checked and found sometimes power was getting to the sensor and sometimes not. Tightened the 2A1(4B) wire in distribution block 2. 2A4 (Fuel pump) wire should be in distribution block 2 while it was in distribution block 4 so fixed it. | Closed | Amit Shandilya
21 | West | 211693350 | 2025-07-02 15:25 | 160 | 6H.8475.../2420091 | Red Lamp Alarm & sound issue Call by : Customer Name :Kumar Contact : 9095810926 | Task Start | SOWPARNIKA PROJECTS AND INFRASTRUCTURE (P) LTD., | Shree Engineering Service - Satna | 70 | Low coolant level in radiator so filled the coolant. SPN/FMI- 110/3 So the coolant sensor connector was refitted and the DTC was cleared | Closed | Vijay Patil
23 | West | 211691995 | 2025-07-02 11:01 | 58.5 | T4.8941.../2420788 | Starting Issue Call By Customer Name :- Yagnik Parmar Mobile No :-9904654660 | Closed | BND TECHNOLOGIES PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Vapi | 32 | SPN/FMI- 157/14 Tightened all wire connections in panel and started engine but did not start so replaced relay board. | Closed | Amit Shandilya
36 | North | 211697077 | 2025-08-02 17:06 | 58.5 | T4.8941.../2421614 | Starting Issue. Call By Customer. Name:- Abhishek Mobile No.:-8550048008 | Closed | Hotel Gurukripa INN. | Espiem Engines & Machines (P) Limited - Agra | 37 | Found MCB wire loose in panel tightness the same & SPN/FMI 2802/4 & 97/5 clear the code then issue resolve | Closed | Sudhir awasthi
38 | North | 211696803 | 2025-08-02 16:05 | 125.4 | 4H.8041.../2320108 | Starting Issue Call By Customer Name - Vijay Kumar Number - 9829973147 | Closed | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 170 | Found SPN/FMI 51/0 throttle valve jammed need to be replace SD team was EDO of ITV | open | Gourav Sharma
51 | North | 211694019 | 2025-07-02 17:21 | 30 | 3H.8902.../2421211 | Starting/Stopping Issue | Open | BHARAT GENERAL STORE | Suraj Motor Store - Jammu | 102.05 | SPN/FMI-2791/18;EGR High voltage ;will flash the same by tomorrow | Open | Ved Prakash Gupta
55 | North | 211692823 | 2025-07-02 13:19 | 20 | GP3.8601.../2421115 | Red Light Alarm issue Call By Customer Name :- Ajaz Mobile No :- 7889926045 | Task Start | HILAL BAKERY.. | Suraj Motor Store - Srinagar | 15 | SPN/FMI-2791/18;check the EGR valve & clean the same but code exists yet;need to flash the same | Open | Ved Prakash Gupta
70 | North | 211685649 | 2025-05-02 15:26 | 57 | T4.8941.../2320042 | Error code issue | Closed | Sceptre Medical India Pvt Ltd | SAAN Royal Power Solutions Private Limited - Sonipat | 786.45 | SPN/FMI-97/5 ; water in fuel sensor with protect Lamp on ; No water traces found after drain from water separator but carbon particle found in connector comes across ECU to Pannel;Clean the same & remove the code,issue resolved | Closed | Ved Prakash Gupta
72 | North | 211685282 | 2025-05-02 13:37 | 750 | DV2.8501.C4../2320030 | Tripping Issue Call By Customer Name - Santosh Number - 9588115616 | Closed | Shree Cement Ltd. | SAAN Royal Power Solutions Private Limited - Panipat | 152 | SPN/FMI-516166/0 , 656/3& 523576/0;DG was in running condition on site,Checkthe AdBlue Level & Line found ok,Check continuity in cylinder no.5 & 6 found ok,reset the alarm & resolve the issue | Closed | Ved Prakash Gupta
4 | East | 211693420 | 2025-07-02 15:36 | 125.4 | 4H.8041.../2420938 | Maintanance due alarm issue Called by customer Name : Shobit Number : 7549039250 | Task Start | Shantidoot Infra Services Pvt. LTd. | HACS Engineering and Tech Private Limited - Ranchi | 253 | SPN: 1761,FMI: 16 - Urea Tank Level low alarm, So SE top up the Adblue and restore the issue. | CLOSED | Prabhakar Kumar
6 | East | 211691587 | 2025-07-02 09:58 | 160 | 6H.8475.../2420166 | Supply module issue | Task Start | M/s. Fifeo Energy Station | Green Powerline - Tezpur | 328 | SPN: 4376,FMI: 5, SPN: 4358,FMI: 2, SPN: 4095,FMI: 2, SPN: 1761,FMI: 17 so as per the fault code SE checked the supply module relative pressure in IKonnect found only 76 hPa - 300 hPa so checked the its voltage at connector found OK and cotinuity also found OK checked its filter all found OK, replaced supply module then started and checked relative pressue found 5002 hPa. | CLOSED | Ujjwal Das
4 | North | 211699635 | 2025-10-02 12:18 | 125.4 | 4H.8041.../2320066 | Starting Issue Call By Customer Name :- Anil Kumar Mobile No :- 9971230939 | Task Start | VK GENSET & POWER SOLUTION | Paluck Technologies Ltd. - Gurgaon | 5249 | Found SPN/FMI 51/1 ITV jammed, When Engineer open the ITV connector then, DG running ok, but when he connect the connector then DG trip So, I suggest to replace the ITV | Closed | Kapil Solanki
12 | North | 211698894 | 2025-10-02 09:22 | 125 | F6.9840.../2420003 | Electrical Problems | Task Start | Venu Eye Institute & Research Centre. | Vidyut Engineers - New Delhi | 48 | found EUGO sensor faulty then we have change Lambada Make EUGO sensor and Extension pipe for catalyst outlet replace after that check engine working ok but alarm same SPN:3227 FMI:15 SE contact to ASE he say for flashing | Open | Kapil Solanki
14 | North | 211698546 | 2025-10-02 07:37 | 125.4 | 4H.8041.../2320090 | Starting Issue Call By Customer Name - Rajesh Kumar Number - 7042659373 | Task Start | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi | 3081 | Found SPN/FMI 4095/1, 4095/0, 4339/2, 3031/14 Check the DEF tank condition found ok, then check Inlet & Outlet line found ok, after trial on load the DG about 30 min. found No, any alarm but_ Found also Radiator chocked & Service due So, Educate the Customer for kindly cleaning the Radiator & Service due | Closed | Kapil Solanki
8 | East | 211702192 | 2025-10-02 15:55 | 30 | 3H.8902.../2422420 | Abnormal Sound Issue. Call By Customer. Name:-Parshant Byanth Mobile No.:-7551878476 | Open | Presidency Infracon LLP. | HACS Engineering and Tech Private Limited - Ranchi |  | SPN: 5838,FMI: 1, SPN: 2791,FMI: 31 fault code showing on KRM visit pending | OPEN | Prabhakar Kumar
5 | North | 211704877 | 2025-11-02 10:27 | 25 | GP3.8702.../2420302 | error code | Open | Aryadhenu Misthanshala | SAAN Royal Power Solutions Private Limited - Hisar | 333.3 | SPN/FMI-636/8 ; Cam Sensor flt error ; check the continuity to sensor & voltage supply from ECU found ok,Flash the ECU but issue remains same,RRT team will attend | Open | Ved Prakash Gupta
6 | North | 211704687 | 2025-11-02 09:40 | 82.5 | 5H.8901.../2320076 | Starting/Stopping Issue | Closed | Sandhu Construction | SAAN Royal Power Solutions Private Limited - Karnal | 2280 | SPN/FMI-6595/0 & 3031/14 ; Fopund ECU AVS Value 57600 so change the value to 25600,clean the dosing module with hot water & changed the AdBlue filter kit,clean the AdBlue tank & remove the code,run the DG on Load,issue resolved | Closed | Ved Prakash Gupta
1 | East | 211704805 | 2025-11-02 10:10 | 30 | 3H.8902.../2420408 | Starting/Stopping Issue | Task Start | Shine Enterprise | Green Powerline - Dhemaji | 1031 | SPN 520528FMI 31, SPN 105 FMI 3, SP 5838 FMI 3/2/1 SPN 2791 FMI 1/31 were present in DTC so as per fault code description SE checked for the the EGR valve found jammed so replaced the EGR valve. | CLOSED | Ujjwal Das
3 | East | 211702192 | 2025-10-02 15:55 | 30 | 3H.8902.../2422420 | Abnormal Sound Issue. Call By Customer. Name:-Parshant Byanth Mobile No.:-7551878476 | Open | Presidency Infracon LLP. | HACS Engineering and Tech Private Limited - Ranchi |  | SPN: 5838,FMI: 1, SPN: 2791,FMI: 31 fault code showing on KRM visit pending | OPEN | Prabhakar Kumar
6 | East | 211699675 | 2025-10-02 12:25 | 10 | GP3.8301.../2420135 | Low Voltage Alarm Issue Call By Customer Name :- KHEKTO . Mobile No :- 9863164425 | Open | Catsm | Hibreed Engineering Pvt. Ltd. - Jorhat | 2 | SPN: 2802,FMI: 4,(today service cordinator will share update by end of day) | OPEN | Ujjwal Das
3 | North | 211707555 | 2025-11-02 17:51 | 58.5 | T4.8941.../2420013 | Error code issue Call By Customer Name :-Kamal Kanth Sare Number:- 9873088378 | Task Start | Vinod Kumar | Vidyut Engineers - Noida | 131 | SPN/FMI, 100/1 & 100/3 clear the code with i-konnect tool | Closed | Kapil Solanki
28 | North | 211704623 | 2025-11-02 08:07 | 200 | 6H.8435.../2420243 | Alarm Issue Call By Customer Name - SHIVRAJ ... Number - 8869907969 | Closed | Sri Chaitanya Seva Trust | Espiem Engines & Machines (P) Limited - Agra | 101 | Found low def level SPN/FMI 1761/16 , 5462/18 after that fill the DEF then clear the fault code then issue resolve | Closed | Sudhir Awasthi
29 | North | 211703686 | 2025-10-02 19:46 | 160 | 6H.8475.../2420394 | Starting issue Call By Customer Name ;- Rohit .. No;- 9634382881 | Closed | Tulsi Dham | Espiem Engines & Machines (P) Limited - Agra | 42 | Found V belt loose so, tightness the same & SPN/FMI 2802/4 & 516166/0 then clear thew code by I-konnect then issue resolve | Closed | Sudhir Awasthi
6 | East | 211702192 | 2025-10-02 15:55 | 30 | 3H.8902.../2422420 | Abnormal Sound Issue. Call By Customer. Name:-Parshant Byanth Mobile No.:-7551878476 | Open | Presidency Infracon LLP. | HACS Engineering and Tech Private Limited - Ranchi | 120 | SPN: 5838,FMI: 1, SPN: 2791,FMI: 31 fault code showing so SE check for EGR voltage continuity found OK so removed and Check EGR found clogging so cleaned and refitted issue then clear fault code issue resolved SE also recommended to operate DG above 30% load | OPEN | Prabhakar Kumar
7 | East | 211699675 | 2025-10-02 12:25 | 10 | GP3.8301.../2420135 | Low Voltage Alarm Issue Call By Customer Name :- KHEKTO . Mobile No :- 9863164425 | Open | Catsm | Hibreed Engineering Pvt. Ltd. - Jorhat | 2 | SPN: 2802,FMI: 4,(ASE will update by morning) | OPEN | Ujjwal Das
25 | South | 211707792 | 2025-11-02 19:39 | 10 | GP3.8301.../2420458 | engine not starting | Task Start | SUTARIA AUTO CENTRE | KALA Care Global LLP - Hubli | LR | As per we are cc sr attend the site then we are started the dg is not started because of error code showing in display. Then we are check the error code is SPN 110 AND FMI 0 and SPN 100 FMI 1 AND SPN 158 FMI 0 and SPN 190 FMI 1 and SPN 96 FMI 4 And then we are check the error code related sensor and wiring found is ok, then connect the 645C controller cable and programming the controller, and then start the dg running good | Task Start | Mr. Anil Kumar H G
30 | South | 211706047 | 2025-11-02 14:23 | 30 | 3H.8902.../2420062 | Starting Issue Call By Customer Name - Ashok . Number - 7795509438 | Closed | Classic Associates | KALA Care Global LLP - Hubli | 25 | As per the customer's complete, we visited the site to observe the DG; it then did not start and then checked the alarm and the SPN 97 and FMI 5 and then checked the fuel water in the fuel sensor removed the connection and then cleared the sensor and corrected the communication pins reconnected the sensor and then cleared the alarm and then start the engine working good. | Closed | Mr. Anil Kumar H G
50 | South | 211699331 | 2025-10-02 11:11 | 250 | F6.8841.../2420106 | Error Code Issue Call By Customer Name :- Abhishek .. Mobile No :-9164239659 | Closed | Sanoh India Private Limited | Surya Power Services - Bommasandra, Bangalore | 45 | Visit the site check the engine not starting due to spn 3364 FMI 8 clear the code and ecu flashing as done and check running found ok check the all parameters working engine running found ok | Closed | Mr. Anil Kumar H G
57 | South | 211698410 | 2025-09-02 22:38 | 125.4 | 4H.8041.../2420261 | Engine not starting-Error code problem | Closed | Selvakumar | Bharath Diesel Sales and Service - Karaikal | 18 | Check the engine side fully.also checked the wiring found ok but engine not starting.because many error code SPN 51,3229,653,3029 found.so flashing the ECU and reprogrammed.After Flashed engine starting normally.engine performance is normal.checked the dg with load condition safety unit working normally. | Closed | Mr. NandhaGopal
70 | South | 211695306 | 2025-08-02 10:08 | 58.5 | T4.8941.../2423081 | Starting/Stopping Issue | Closed | Acecret Adhesions India Private Limited | Prasad Power Engineers - Mangalore | 332 | Engine not starting due to spn 2791,FMI 18,6 so clear the alam ,ecu calibration done and all so oil level is low so done thae oil service now DG running properly and all the parameters are found ok | Closed | Mr. Anil Kumar H G
74 | South | 211694038 | 2025-07-02 17:19 | 125.4 | 4H.8042.C4../2420468 | high temperature Alarm Issue Call By Customer Name:Mehaboob .. No :9746143389 | Closed | ORANGALLA PARAMBAN SHAJI | G-Care Diesels Private Limited - Malappuram | 42 | Engine high clnt temp fit alarm showing and shutdown issue SPN:110 FMI:16 and ecu flashing it found ok kept under observation for 2day engine working found ok check engine oil level radiator coolant level battery water level radiator air filter clean and refttted v belt tension correct check fuel hose radiator hose adblue level engine wiring panel wiring engine working found ok | Closed | Mr. Sanjaimon S
88 | South | 211690465 | 2025-06-02 17:32 | 82.5 | 5H.8901.../2420591 | Error showing in controller | Closed | Rudhra Dental Clinic | Bharath Diesel Sales and Service - Salem | 27 | FOUND SPN 6595 ,FMI 0.,ERROR SHOWN IN CONTROLLER. ERROR CODE CLEARED WITH IKONNECT. CHECKED THE D.G ON/OFF AND WORKING FINE.ALSO CHECKED THE NOX SENSOR AND TEMPERATURE SENSOR LOOSEN. IT HAS BEEN TIGHTEN. | Closed | Mr. NandhaGopal
98 | South | 211692075 | 07-02-2025 11:13 | 200 | 6H.8435.../2420081 | Starting/Stopping Issue | Open | Nanki Automotives & Enterprises Pvt Ltd. | KALA Care Global LLP - Hubli | 80 | As per the customer's complaint, we are attending the site and observed the dg error code SPN 516166 FMI 0 We connected the tool and cleared the error code and top-up the AdBlue and top-up the coolant and then started the dg running is ok. | Closed | Mr. Anil Kumar H G
12 | North | 211712985 | 13-02-2025 13:21 | 40 | 3H.8951.../2520140 | Starting Problem | Closed | TARUN DUA | Vidyut Engineers - Noida | 6 | SPN/FMI 97/5 Check & found no any water traces in seprator after that clear the DTC | Closed | Kapil Solanki
17 | North | 211711886 | 13-02-2025 09:52 |  | GP3.8501.../2520007 | Fuel Rack Position Short | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | LR-1.2 | Found error code show SPN/FMI 1210/4 then check 2&3pin connector continuity found in D1 wire not get the Continuity then change the new wiring harness then issue resolve | Closed | Sudhir Awasthi
10 | East | 211699675 | 2025-10-02 12:25 | 10 | GP3.8301.../2420135 | Low Voltage Alarm Issue Call By Customer Name :- KHEKTO . Mobile No :- 9863164425 | Open | Catsm | Hibreed Engineering Pvt. Ltd. - Jorhat | 2 | SPN: 2802,FMI: 4, SE checked and found F3 fuse(wire 2A - M2) which is used in ECU +ve supply wire was defective after replacing issue resolved. | CLOSED | Ujjwal Das
7 | South | 211713100 | 13-02-2025 13:40 | 0 | F6.8802.../2420306 | ECU MALFUNTIONING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the dg noticed the alarm for ecu malfunction, check the I connect DTC spn 4363 fmi 3 error display clear the error not done, after change the other ecu error not display | Task Start | Mr. NandhaGopal | Check ECU
13 | South | 211712671 | 13-02-2025 12:32 | 160 | 6H.8475.../2420418 | High coolant temperature | Closed | KVR AUTO CARS PVT LTD | G-Care Diesels Private Limited - Kannur | 1483 | High coolant temperature flt+Abnormal sound, corrected the error code in ecu (SPN:110 FMI=0 )Customer complaining about abnormal sound issues, as per customer request site visited and found that fan belt is in loosen condition ,and current hmr is 148hours,so discussed the same matter with ASM Sanjaimon.s and as per his instructions fan belt tightened | Closed | Mr. Sanjaimon S | KRM Check
5 | North | 211717931 | 14-02-2025 15:43 | 750 | DV2.8513.C4../2520001 | starting issue | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Found SPN/FMI 1244/3 error code Clear the DTC KG 1500 programming | Closed | Gourav Sharma | Details Required
26 | North | 211721532 | 15-02-2025 16:44 | 125.4 | 4H.8041.../2320108 | Starting/Stopping Issue | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 171 | SPN/FMI 51/0 change the trottle valve but problem same, | Open | Gourav Sharma
32 | North | 211720503 | 15-02-2025 13:00 | 320 | F6.8802.../2320073 | Alarms. E C U malfunc | Closed | Vedic Cosmeceuticals Private Limited | Vidyut Engineers - Noida | 124 | SPN/FMI 97/2 ,3364//8, 1761/16, 4225/1, 3031/14, 520527/16, 4365/2 Clear the DCT | Open | Kapil Solanki
3 | East | 211720900 | 15-02-2025 14:43 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, SE is not answering | OPEN | Prabhakar Kumar
3 | WEST | 211717498 | 14-02-2025 14:09 | 30 | 3H.8902.../2420699 | Starting Issue Call By Customer Name Nayar .. No : 8291603287 | Closed | PERFECT FABRICATORS | Transcreek Engineers Pvt. Ltd. - Mumbai | 369 | Dg is not start due to air lock issue , remove air lock ,SPN 157 FMI 14( Pres relief vlv fault)Connect ikonnect and clear DTC. | closed | Jagdeep Saini
23 | WEST | 211708564 | 2025-12-02 09:40 | 160 | 6H.8475.../2420307 | Error Code Issue Call By Customer Name :- Deepak Pawar Mobile No :-9975566453 | Closed | Khuspal Home Textile LLP. | Transcreek Engineers Pvt. Ltd. - Vasai | 19 | SPN=516166 FMI=0, SPN=1761 FMI=16, this codes are showing inform to customer for fill the adblue , and connect ikonnoect and clear code. | closed | Jagdeep Saini
3 | NORTH | 211724189 | 17-02-2025 12:13 | 250 | F6.8841.../2320008 | Starting Issue Call By Customer Name :- Sughar Mobile No :- 8076601980 | Task Start | Charu Apparel Manufacturing Company Private Limited | Vidyut Engineers - Noida | 63 | Low def level alarm SPN/FMI 1761/16 | Closed | Kapil Solanki
10 | NORTH | 211723321 | 17-02-2025 09:39 | 125.4 | 4H.8042.C4../2420571 | Amber lamp on alarm Call by Customer Name : Gajendra No : 8287266787 | Closed | AVON COATINGS | Paluck Technologies Ltd. - Faridabad | 3 | Found SPN/FMI 516166/0 reset thealarm | Closed | Kapil Solanki
14 | NORTH | 211722664 | 16-02-2025 18:19 | 250 | F6.8841.../2320050 | Error Code Issue. Call By Customer. Name:-Pradeep Yadav Mobile No.:-8368321282 | Open | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 260 | SPN/FMI 5461/0 reset the alarm & flash the file then issue resolve | Closed | Kapil Solanki
27 | South | 211720088 | 15-02-2025 12:00 | 320 | F6.8802.../2420228 | Error will come | Closed | SABARI WOOD AND PLYWOODS | Bharath Diesel Sales and Service - Karur | 13 | Visited the customer site checked the engine starting problem due to error code showing in controller SPN: 516166 /0ECU Internal fault so connected the I Konnect tool and clear the problem code , oil level checked ok fan belt tension checked ok radiator coolant level checked ok started the engine check with load found Running condition normal | Closed | Mr. NandhaGopal
4 | East | 211720900 | 15-02-2025 14:43 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, visit pending | OPEN | Prabhakar Kumar
14 | NORTH | 211728633 | 18-02-2025 09:27 | 500 | DV8.8501.C4../2320061 | Throthle body to be change | Closed | Goodworth Electronics Private Limited | Vidyut Engineers - Noida | 99 | Found SPN/FMI 3465/1 , 1761/15, 523584/15, 516166/0 clear the DTC but repeat a code 3465/1 after replace the throttle valve then issue resolve | Closed | Kapil Solanki
20 | NORTH | 211727071 | 17-02-2025 16:17 | 58.5 | T4.8941.../2423190 | AMF pannel istallation Call By Customer Name :- Sandip morya Mobile No:-8459683275 | Closed | The Samrat Palace | S. R Engines Sales And Service - Gorakhpur | 37 | SPN/FMI 5838/1 remove the EGR connector then again refitted issue resolve after clear the code | Closed | Sudhir Awasthi
38 | North | 211722528 | 16-02-2025 11:42 | 500 | DV8.8501.C4../2320026 | Genset locked out issue Call by Customer Name: Javed Number:7006686329 | Task Start | M/s. Mas Agro Fresh | Suraj Motor Store - Srinagar | 285 | SPN/FMI-1761/15 ; DEF Coupler found loose on site so re-connected the same & same educated to customer. | Closed | Ved Prakash Gupta
41 | North | 211720379 | 15-02-2025 12:44 | 40 | 3H.8951.../2421168 | error code problem | Closed | ICICI Bank Limited | SAAN Royal Power Solutions Private Limited - Zirakpur | 29 | SPN/FMI-2791/5 ,Related to EGR,Open the EGR Valve & found it jammed so clean the same by Diesel & re-fitted the same,DG running fine after clear code | Closed | Ved Prakash Gupta
44 | North | 211719610 | 15-02-2025 10:09 | 125.4 | 4H.8041.../2420234 | Tripping Issue Call By Customer Name - Ravindra Number - 8930092565 | Closed | T. Rituinsan | SAAN Royal Power Solutions Private Limited - Hisar | 77 | SPN/FMI-1761/16 ,Low AdBlue Level,Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
45 | North | 211717969 | 14-02-2025 15:53 | 15 | GP3.8501.../2420719 | Starting/Stopping Issue | Closed | Dela Chemical. | Industrial Power Solutions - LUDHIANA | 24 | SPN/FMI-2802/3, with Under speed alarm,Battery Voltage found ok,check the charging alternator & self-starter connection , found ok,reset the code & resolve the issue | Closed | Ved Prakash Gupta
46 | North | 211717637 | 14-02-2025 14:49 | 25 | GP3.8702.../2420165 | Electrical Problems | Closed | Ms. Ranjit Kaur | SAAN Royal Power Solutions Private Limited - Zirakpur | 92 | SPN/FMI-97/5,Water in Fuel,clean the fuel filter & reset the code,DG running fine | Closed | Ved Prakash Gupta
5 | East | 211720900 | 15-02-2025 14:43 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, visit pending | OPEN | Prabhakar Kumar
2 | West | 211716720 | 14-02-2025 11:00 | 50 | T4.8941.../2423324 | ENGINE NOT STARTING | Task Start | Bharti Airtel Limited | Shree Engineering Service - Satna | LR | The SPN/FMI code 97/5 was displayed. Upon inspection, it was found that a wire in the engine controlle panel connector had become dislodged. This was corrected. Subsequently, a test was performed to address the engine WIF sensor error. While the original error was resolved, a communication error with the controller is now being reported. Checked the resistance and found 0ohm. No any parameters was showing in controller related to DEF. | OPEN | Vijay Patil
7 | West | 211719663 | 15-02-2025 10:22 | 40 | 3H.8951.../2420844 | Starting Issue Call By Customer Name :-RAM Mobile No :-7757992893 | Closed | HAWARE LEGACCY | Transcreek Engineers Pvt. Ltd. - Mumbai | 10 | active SPN 637 and FMI -2 which is related to crank sensor . So checked its voltage in wake up mode it is 2.5 vdc . So as per troubleshooting tree diagnostic increased its gap between flywheel and sensor then checked for four to five times, now it is found working properly. | Closed | Jagdeep saini
10 | West | 211728693 | 18-02-2025 09:53 | 82.5 | 5H.8901.../2420327 | Error code | Task Start | METAL MORPHOSIS PRIVATE LIMITED | Shree Engineering Service - Raipur | 550 | spn 516166 fmi 0 connect ikonnect and clear error code. | Closed | Jagdeep saini
11 | West | 211713499 | 13-02-2025 14:54 | 40 | 3H.8951.../2421352 | Red Lamp On Alarm Issue Call By Customer Name :-Ujjal Bajaj Mobile No :-8879171661 | Closed | Mr.Ujjal Bajaj | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 32 | spn 2719/18 EGR issue showed so that all properly wires checked in voltage and continuity no issues in wiring connect ikonnect and clear error code. Calibrated the ECU. | Closed | Jagdeep saini
13 | West | 211707558 | 45963.7444 | 40 | 3H.8951.../2421757 | AUTO START ISSUE | Closed | Gaikwad Develoipers | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 3 | spn 2719/18 EGR issue showed so that all properly wires checked in voltage and continuity no issues in wiring connect ikonnect and clear error code but still error code showing so flash the ecu. | Closed | Jagdeep saini
1 | West | 211732917 | 19-02-2025 10:43 | 25 | GP3.8702.../2421817 | Error code issue | Task Start | Jai Ashapura Container Terminals | Unique Techno Services Pvt Ltd. - Gandhidham | 12 | The customer complained that there was a problem in starting the genset in auto mode due to the error code. SPN/FMI- 7026/5(Meetering Unint) in controller & 7026/3 in iKonnect app. Tightened the 2A4(Fuel pump wire) on distribution block 2. Checked the Voltage on IMV- between both pins of IMV:10V, Between IMV 2A4 wire pin with respect to ground:13V and between 88 wire pin with respect to ground: 3V. Checked and refited the Engine and panel connector. And started the DG in manual & Auto mode, running OK. | Closed | Amit sandlya
2 | West | 211732676 | 19-02-2025 09:51 | 58.5 | T4.8941.../2423223 | Leakage Issue | Task Start | Mr. Mahindara | Unique Techno Services Pvt Ltd. - Baroda | 8 | SPN/FMI-2791/18,2791/01,5838/01 Flashed the ECU. This DG is mounted on vehicale. No any fuel leakage from fuel tank. | Closed | Amit sandlya
3 | West | 211728952 | 18-02-2025 10:43 | 125.4 | 4H.8042.C4../2420589 | Starting/Stopping Issue | Task Start | KP. Energy | Unique Techno Services Pvt Ltd. - Gandhidham | 312 | SPN/FMI- 516166/0 and 1761/14 Filled the DEF and cleared the DTC. | Closed | Amit sandlya
7 | West | 211724872 | 17-02-2025 12:42 | 40 | 3H.8951.../2421166 | MIL lamp alarm Issue Call By Customer Name :- Mohammad anas patel Mobile No :-9770123628 | Open | Patel Poultry farm | Natraj Power Tech - Ratlam | 9.9 | SPN/FMI- 2791/1,5 & 5838/1 & 2802/3 Engineer visited on site without iKonnect tool. Checked the wiring continuity & cross continuity from ECU to EGR valve connectyor found OK. Load on DG- 5%. Today engineer will visit again. | Closed | Vijay patil
11 | West | 211726868 | 17/2/2025 12:00:00 AM | 30 | 3H.8902.../2422017 | CC SR | Task Start | Reliable Motors | Unique Techno Services Pvt Ltd. - Ankleshwar | CSP | SPN/FMI- 2791/18- Calibrated the ECU with Dummy file. Opend the ECU connector and found that 73(1 Injector pin) bent and wiring ECU connector pin was backed out from its position. | Closed | Amit sandlya
6 | North | 211733834 | 19-02-2025 13:16 | 82.5 | 5H.8901.../2420458 | Starting/Stopping Issue | Task Start | Mastersmith | Deep Jyoti Electricals and Services - Moradabad | 25 | Found SPN/FMI 516166/0, & DEF level low | Closed | Sudhir Awasthi
34 | North | 211732786 | 19-02-2025 10:20 | 35 | 3H.8902.../2422394 | Starting/Stopping Issue | Closed | Axis Bank Ltd | Suraj Motor Store - Srinagar | 19 | SPN/FMI-5838/1,2791/1 ;Related to EGR;found choked the same so clean the valve & re-fitted,DG running under load most of the time,same communicated to customer | Closed | Ved Prakash Gupta
36 | North | 211732607 | 19-02-2025 09:25 | 125.4 | 4H.8042.C4../2420719 | Alarm issue | Closed | VIRENDER | SAAN Royal Power Solutions Private Limited - Sonipat | 47.8 | SPN/FMI-516166/0 ; ECU flt error,re-fit the ECU connector & remove the code;issue resolved | Closed | Ved Prakash Gupta
39 | North | 211717472 | 14-02-2025 13:54 | 15 | GP3.8501.../2420328 | Amber Lamp Alarm Issue Call By Customer Name - Saksham No - 8700988806 | Task Start | Hra Rice Mills | Dynamic Engineering Services - Jalandhar | 67 | SPN/FMI-2802/4 ; Related to Battery,Battery Voltage found low(10.4V)New 75AH battery installation for testing purpose instead of 65AH battery as advise by koel team.Old Battery sent for testing to vendor | Closed | Ved Prakash Gupta
9 | East | 211720900 | 15-02-2025 14:43 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, also found low DEF level alarm so top up and tighten all connection of control panel after that cleared code cleared issue resolved | CLOSED | Prabhakar Kumar
14 | East | 211733381 | 19-02-2025 11:59 | 125.4 | 4H.8042.C4../2420006 | Starting/Stopping Issue | Task Start | KALYAN JEWELLERS INDIA LTD | K.C. Diesel Services - SILIGURI | 385 | SE found code (SPN-516166 FMI -0) ,(SPN-1761FMI-16) after that top up the DEF level and clear the code Issue resolved | CLOSED | Prosanjit saha
8 | North | 211738492 | 20-02-2025 15:20 | 82.5 | 5H.8901.../2320094 | Genset Trip | Task Start | RAO TENT HOUSE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 456 | Found SPN/FMI 51/5 & 51/0 ITV required Change | open | Kapil Solanki
18 | North | 211737044 | 20-02-2025 10:50 | 125.4 | 4H.8042.C4../2420016 | loading Issue Call By Customer Name :- Akshay Jain Mobile No :- 8800616123 | Closed | STARCO METAPLAST PVT. LTD. | Paluck Technologies Ltd. - Ghaziabad | 63 | Adblue lavel low and code show spn 520528 fmi 31 , 1761/16, 516166/0 urea required with service due | Closed | Kapil Solanki
2 | WEST | 211737085 | 20-02-2025 11:01 | 250 | F6.8841.../2420175 | Add blue Consomtion Call By Customer Name :- Mobile No :- | Closed | SHREYA CONSTRUCTION | Dhanashree Technocrats Pvt. Ltd. - Jalgaon | 605 | SPN 4095 DEF not supply from supply module to dosing module , so changed the supply module. | Closed | ECU fault
19 | North | 211746698 | 22-02-2025 14:58 | 58.5 | T4.8941.../2423190 | Starting Issue Call By Customer Name :- Sandip morya Mobile No:-8459683275 | Task Start | The Samrat Palace | S. R Engines Sales And Service - Gorakhpur | 42 | SPN/FMI 2791/18, 5838/1 Flash the ECU after that issue resolve | Closed | Sudhir Awasthi
27 | North | 211746277 | 22-02-2025 13:28 | 125.4 | 4H.8042.C4../2420601 | Urea Level Issue | Completed | Bindal Cotex Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 33 | SPN/FMI-516166/0 with Amber Lamp On ; reset the DTC & run on load ,Issue resolved | Closed | Ved Prakash Gupta
33 | North | 211745091 | 22-02-2025 08:59 | 200 | 6H.8435.../2420175 | Ncd Lamp ALarm Issue Call By Customer Name :-Nandkishor Sharma Mobile No :-7732910730 | Task Start | Decora Kitchen Interiors Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 39 | SPN/FMI-1761/16 ; AdBlue Level Low , on site found below 50%,Top-up the same & educate customer to keep AdBlue minimum 50% | Closed | Ved Prakash Gupta
38 | North | 211742376 | 21-02-2025 14:21 | 40 | 3H.8951.../2320109 | tarting Issue Call By Customer Name :- Satish Kumar Mobile No :- 8803349159 | Task Start | Jammu Kashmir Cricket Association | Suraj Motor Store - Jammu | 23 | SPN/FMI-637/2 Clean the crank sensor & remove the code,run the DG,Issue resolved | Closed | Ved Prakash Gupta
2 | West | 211745130 | 22-02-2025 09:27 | 15 | GP3.8501.../2421182 | Amber Lamp Alarm Issue Call By Service Dealer Name-Mukesh No.-7583889815 | Closed | Kalinga Commercial Corporation Limited | Shree Engineering Service - KORBA | 350.26 | This DG is in mining area. After starting for 5 minutes engine temperature went above 100 degrees and controller displayed SPN 602, FMI 16( high ECT warning), due to radiator external choke up, so radiator was cleaned. DG is in covered area. Engineer educated the customer. | Closed | Vijay patil
3 | West | 211744437 | 21-02-2025 21:21 | 125.4 | 4H.8042.C4../2420790 | Starting issue Called by customer Name : Brajesh Number : 9826249509 | Closed | NEHA AUTOMOBILES | Shree Engineering Service - Chhatarpur | 95 | SPN/FMI- 3031/14,Calibrated the ECU with dummy file. | Closed | Vijay patil
11 | West | 211741856 | 21-02-2025 12:23 | 58.5 | T4.8941.../2422344 | amber lamp alram Issue Call By Customer Name :- Ashok Sir Mobile No :- 9712906022 | Closed | SPACE GENERATOR | Unique Techno Services Pvt Ltd. - Hathijan | 660 | SPN/FMI- 2791/18 Calibrated the ECU. | Closed | Amit sandlya
12 | West | 211741844 | 21-02-2025 12:22 | 58.5 | T4.8941.../2423141 | red lamp alarm Call By Customer Name :- Aman ... Mobile No :-9664961222 | Task Start | Asian Paints. | Unique Techno Services Pvt Ltd. - Surat | 2 | SPN/FMI- 2791/18 Calibrated the ECU. | Closed | Amit sandlya
14 | West | 211745275 | 22-02-2025 10:04 | 40 | 3H.8951.../2420859 | Starting Issue Call By Customer Name :- Sandeep Poojari Mobile No :-9833132999 | Closed | SAI KESHAR RESIDENCY | Transcreek Engineers Pvt. Ltd. - Panvel | 19 | SPN 97 FMI 5 , reconnect the sensor and tighten the distribution block wire | Closed | Jagdeep Saini
64 | South | 211744205 | 21-02-2025 18:07 | 40 | 3H.8951.../2421294 | Starting/Stopping Issue | Closed | Novella Jacqueline jays fitness | Surya Power Services - Kalyan Nagar | 20 | check the egr valve fault then remove fault code spn 3216-2 and FMI 18 the senor connection then check RECONNECT the wire and start the engine check the load and observe engine running condition normal. | Closed | Mr. Anil Kumar H G
1 | East | 211751675 | 24-02-2025 16:16 | 160 | 6H.8475.../2420432 | Protect Lamp alam Issue Call By Customer Name :- Mobile No :- | Task Start | V. Retail Ltd. | HACS Engineering and Tech Private Limited - Ranchi | 148 | ECU protect lamp 56166, inducement SPN: 520528,FMI: 31 alarm and Adblue level low alarm SPN 1761 SPN 18 need to topup the DEF and need to clear the code. visit pending | OPEN | Prabhakar Kumar
1 | North | 211741951 | 21-02-2025 12:40 | 57 | T4.8941.../2320139 | STARTING ISUE Call By Customer Name :-Manish Mobile No :-9625939742 | Task Start | Msafe | Vidyut Engineers - Noida | 208 | SPN/FMI 157/14 PRV open fault then check & found 12RB1, RL2 Voltage drop so, check with other Relay found ok after need to Replace the Relay | open | Kapil Solanki
9 | North | 211751325 | 24-02-2025 15:20 | 125.4 | 4H.8041.../2420460 | Display Issue Call By Customer Name :- Sarjeet Ji Mobile No :- 9810090015 | Task Start | Ankur Generators | Vidyut Engineers - Noida | 173 | found Alarm show in Ems Display spn 516166 FMI 0 ECU flt After that We Re set the Alarm | Closed | Kapil Solanki
12 | North | 211750117 | 24-02-2025 11:10 | 160 | 6H.8475.../2320002 | Indicator Lamp Alaram Issue Call By Customer Name :- Harish Mobile No :- 9720331726 | Closed | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 94 | found Alarm show in Ems Display High Adblue temp flt spn 3031 & FMI 14 After that We Re set the Alarm and check the DG set found | Closed | Kapil Solanki
18 | North | 211748845 | 23-02-2025 11:32 | 125.4 | 4H.8042.C4../2420344 | Starting/Stopping Issue | Closed | Master Packaging | SAAN Royal Power Solutions Private Limited - Sonipat | 44.1 | SPN/FMI-516166/0 & also Fuel level showing wrong parameter (8% instead of 100%) due to float stuck so re-fitted the same & remove the code,issue resolved | Closed | Ved Prakash Gupta
2 | West | 211746360 | 22-02-2025 13:45 | 125.4 | 4H.8041.../2420541 | Tripping Issue Call By Customer Name :- MAHESH JAGTAP Mobile No:-919930262638 | Closed | VIJAY SALES (INDIA) PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 397 | SPN 157 FMI 14 cheack all the connection connect ikonnect and clear error code. | Closed | Jagdeep Saini
11 | West | 211735796 | 19-02-2025 18:30 | 320 | F6.8802.../2420178 | Starting Problem Call by : Customer Name :kuluthip Contact :8668566570 | Closed | MIMSR MEDICAL COLLEGE | KALA Care Global LLP - Latur | 114 | SPN 1761 FMI 16 Abdlue level low so top up adblue. | Closed | Jagdeep Saini
12 | West | 211736867 | 20-02-2025 10:19 | 200 | 6H.8435.../2420130 | Adblue issue | Closed | R.D.SAMANT CONTRACTORS PVT.LTD | Mahalaxmi Diesels - Ratnagiri | 19 | Error code P1079 , SPN 4225 FMI 2 pipe from tank to supply module found chocked so clean it with hot water and fitted . | Closed | Jagdeep Saini
18 | West | 211745275 | 22-02-2025 10:04 | 40 | 3H.8951.../2420859 | Starting Issue Call By Customer Name :- Sandeep Poojari Mobile No :-9833132999 | Closed | SAI KESHAR RESIDENCY | Transcreek Engineers Pvt. Ltd. - Panvel | 19 | SPN 97 FMI 5 , reconnect the sensor and tighten the distribution block wire | Closed | Jagdeep Saini
20 | West | 211733206 | 19-02-2025 11:36 | 500 | DV8.9313.../2400001 | Genset Trip | Task Start | SENIOR SECTION ENGINEERS | Transcreek Engineers Pvt. Ltd. - Mumbai | 607.22 | SPN/FMI - 522100, 7,522122,7 & 3513/3 Checked the continuity from DCU2 to Nox sensor, Can line & power supply found ok. Checked the temperature sensor continuity found OK. Suspected B bank NOx sensor need to be replaced.checked both Bank Urea tank level sensor resistance and observed that Bank A tank level resistance 86 & Bank B tank level resistance 76. SE observed the fuel leak from the diesel flow meter. After restricting fuel leak the errors 157/14, 3513/3 got cleared but the 522100/7, 522122/7 got uncleared. Suspected the Nox Sensor of the B bank is having the issue. | open | Jagdeep Saini
10 | North | 211754394 | 25-02-2025 12:22 | 750 | DV2.8501.C4../2420165 | DG Issue | Task Start | Vodafone | R K Engineers - Meerut | 103 | SPN/FMI 658/13 injector No. 8 show the open fault so, check physically found ok then clear the code after trial on load no any issue found | Closed | Sudhir Awasthi
11 | North | 211754244 | 25-02-2025 11:53 | 125.4 | 4H.8041.../2320094 | Oil sensor Issue. Call By Customer Name :-Gopal Mobile No :-8439579873 | Task Start | SS. Creation | Paluck Technologies Ltd. - Ghaziabad | 138 | SPN/FMI 1761/16 & 3031/14 Clear the DTC & flash the file issue resolve | Closed | Kapil Solanki
12 | North | 211754055 | 25-02-2025 11:21 | 320 | F6.8802.../2420135 | CAM SENSOR FAULTY | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Fault code - SPN - 636 FMI - 8 ( Cam sensor fault) Engineer checked supply voltage at Sensor found 5 vdc and checked continuity of wiring harness found ok. then Sensor also replaced but problem not resolved. | open | Gourav Sharma
1 | West | 211754913 | 25-02-2025 14:22 | 250 | F6.8842.C4../2520002 | Error Code Issue. Call By Customer. Name :- Jay Pokhya Mobile No :-8758222728 | Task Start | SUZLON GLOBAL SERVICES LIMITED | Unique Techno Services Pvt Ltd. - Jamnagar | 4.26 | SPN/FMI- 516166/0, Cleared the DTC & educated to the customer. | Closed | Amit Sandlya
2 | West | 211754533 | 25-02-2025 12:48 | 250 | F6.8841.../2420409 | Genset Trip | Task Start | N. K. INFRASPACE | Unique Techno Services Pvt Ltd. - Baroda | 5 | SPN/FMI-516166/0 & 1761/16 Filled the DEF & cleared the DTC. | Closed | Amit Sandlya
4 | East | 211757986 | 26-02-2025 11:10 | 82.5 | 5H.8901.../2420159 | Fuel Leakage Issue Email By KGD Name -Power Generators | Task Start | Radheshyam Tea Industries | Almas Engineers - Sivsagar | 49 | SPN 6595 FMI 0 additional dosing chk error , and SPN 516166 ECU flt pop on display so SE disconnected the dosing module and supply module connector and refitted properly then cleared code and tested for 2 3 time no fault code popup | CLOSED | Ujjwal Das
8 | North | 211754958 | 25-02-2025 14:37 | 250 | F6.8842.C4../2420013 | NCD lamp alarm | Closed | Arihant Machinery Store | SAAN Royal Power Solutions Private Limited - Sonipat | 228.1 | SPN/FMI-1761/16 & 516166/0 ,AdBlue level found low so top-up the same & remove the code ,issue resolved | Closed | Ved Prakash Gupta
15 | WEST | 211757700 | 26-02-2025 09:57 | 125.4 | 4H.8042.C4../2420152 | Tripping Issue Call By Customer Name :- Krishna Yadav Mobile No :- 8999245339 | Task Start | PSOVL RAILONE PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Surat | 163 | SPN/FMI- 6595,0(Malfuntioning of Supply Module & Dosing Module) Checked the DEF line, dosing module & supply module. Nox sensor connector fitted again. Cleared the DTC. Under Observation. | Closed | Amit sandlya
5 | North | 211758341 | 26-02-2025 12:12 | 125.4 | 4H.8041.../2320097 | Voltage issue Call By Customer Name :- Sandip Kumar Mobile No :- 9560094118 | Task Start | DAYA EXPO | Paluck Technologies Ltd. - Faridabad | 213 | SPN/FMI 1761/16 , 51/0 Low Def level alarm & Throttle val jammed top up the DEF then Flash the file & Clean the ITV issue resolve | Closed | Kapil Solanki
8 | North | 211757806 | 26-02-2025 10:28 | 40 | 3H.8951.../2420096 | Tripping issue Call by customer Name: Ramjna Number: 8130797147 | Task Start | Purvanchal Projects Pvt Ltd | Vidyut Engineers - Noida | 3213 | SPN/FMI 105/3 checked and found Intake Air Tmp -vlt high, checked Alarm Riset , start the Engine put on Load 20 minutes found ok. | Closed | Kapil Solanki
13 | North | 211754970 | 25-02-2025 14:33 | 750 | DV2.8501.C4../2420098 | Mall Facing Alarm And Display Issue And Red Lamp On Alarm Call By Customer Name :- Devendra Singh Mobile No :-9891950132 | Task Start | Vodafone Idea Limited | Vidyut Engineers - New Delhi | 9 | SPN/FMI 4358/21, 523576/0 Check the complete def line found all ok but found return line to Def tank found blockage after clean the def line with hot water then trial on load near 1 hour found no issue | Closed | Kapil Solanki
33 | North | 211760643 | 26-02-2025 21:52 | 125.4 | 4H.8041.../2420606 | Tripping Issue Call By Customer Name :-Gurpreet Singh. Mobile No :-9536777118 | Task Start | JEET CONSTRUCTION | R K Engineers - Meerut | 245 | SPN/FMI 157/14, 4095/1, 110/3, 1761/16 Check & found override switch off then on the switch then issue resolve | Closed | Sudhir Awasthi | KRM Check
36 | North | 211764247 | 27-02-2025 17:06 | 82.5 | 5H.8901.../2320034 | Inspection/Maintenance | Closed | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 338 | Found SPN/FMI 1761/16 ,4375/3 ,6595/0 ,51/0 reset the alarm with i-konnect tool | Closed | Kapil Solanki
43 | North | 211763206 | 27-02-2025 15:15 | 125.4 | 4H.8041.../2320172 | Inspection/Maintenance | Closed | Petty Petal Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 498 | SPN/FMI 1761/16, 110/0 & Maintenance due alarm reset the alarm | Closed | Kapil Solanki | KRM Check
54 | North | 211761579 | 27-02-2025 10:57 | 160 | 6H.8475.../2420104 | Error code issue | Task Start | Worldnext Realty LLP. | Industrial Power Solutions - LUDHIANA | 988 | SPN/FMI-2802/4,Battery Voltage low,V-belt found loose on site so replace with 4K belt & check tension found 121 HZ,Battery water level found slightly low so same communicated to customer | Closed | Ved Prakash Gupta
56 | North | 211759803 | 26-02-2025 15:47 | 500 | DV8.9313.../2420024 | starting issue | Closed | RAIL COACH FACTORY RCF | Dynamic Engineering Services - Jalandhar | 1 | SPN/FMI-652/5 ; Injector 2 firing order alarm occurred in Power Car,change the injector,Crank & Cam sensor one by one but issue remains the same ,Change the wiring harness,issue resolved | Closed | Ved Prakash Gupta
57 | North | 211758998 | 26-02-2025 14:45 | 250 | F6.8841.../2420411 | Code issue | Task Start | Winntra PEB And Roofing Systems Private Limited | SAAN Royal Power Solutions Private Limited - Sonipat | 45.11 | SPN/FMI-3031/14,I-Konnect tool not able to be connected so will attend Today again | Open | Ved Prakash Gupta
6 | WEST | 211760420 | 26-02-2025 17:49 | 500 | DV8.9313.../2420038 | STARTING ISSUE | Task Start | Powercare | Unique Techno Services Pvt Ltd. - Surat | LR | SPN/FMI- 100/3 oil pressure sensor and low coolant level. Oil pressure and tem sensor found broken so EDO placed for the same. Radiator was empty of coolant. SE will visit today for controller data log. | Closed | Amit Sandlya