## Jan 24
Sr. No | Incident Id | Creation Date | KVA Rating | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Running Hrs | Observation | Incident Status | ASM Name | Review remark
1 | 210346054 | 2024-01-30 10:04 | 320 | F6.8802.../2320031 | ENGINE OIL LEAKAGE ISSUE DUE Email By-Service Dealer Name:-SUNITA | Task Start | Sanspareils Greenlands Pvt. Ltd. | R K Engineers - Meerut | 19.9 | Oil leakage from LLOP sensor, tighten the same, Issue resolved. | Closed | Sudhir Awasthi
2 | 210346292 | 2024-01-30 10:47 | 57 | T4.8941.../2320216 | Starting Issue and Error Code issue Call By Customer Name: Raj Number: 9891838651 | Open | Sahyog Projects Private Limited | Vidyut Engineers - Noida | 5.57 | Low Battery Voltage alarm due to Wiring damaged, Repaired by SD team, Issue resolved. | Closed | Kapil Solanki
3 | 210346506 | 2024-01-30 11:18 | 500 | DV8.8501.C4../2320033 | Load Issue Call By Customer Name : M.I Khan Mobile No :9306952708 | Task Start | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 16 | DG over-current alarm (Previously event log in GCU), Issue form Load end. | Closed | Kapil Solanki
4 | 210346708 | 211304379 | 400 | DV8.8542.C4../2320006 | Coolant Leakage Issue Call By Customer Name:Iqbal. Mobile No :9034549209 | Task Start | Push Up Tools Udyog Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Rohtak | 11.33 | Coolant leakage from Recovery tank's Pipe, Clamp replaced, Issue resolved. | Closed | Kapil Solanki
5 | 210346830 | 2024-01-30 11:57 | 30 | 3H.8902.../2320009 | Automation Issue Call By Service Dealer Name :Narendra Tomer Mobile No :8194003404 | Open | ZX. Sporting Pvt. Ltd. | R K Engineers - Meerut | 13 | DG auto starting issue, Mains sensing missing from Panel, Just connected the same, Issue resolved. | Closed | Sudhir Awasthi
6 | 210347450 | 2024-01-30 13:41 | 250 | F6.8841.../2320028 | Coolant Leakage Issue Call By Customer Name :Azad .. Mobile No :7082519209 | Task Start | ALFA FLEXITUBES PVT.LTD. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 19 | Coolant leakage from Radiator bottom to Water Pump hose, Tighten Hose clip, Issue resolved. | Closed | Kapil Solanki
7 | 210347519 | 2024-01-30 13:57 | 125.4 | 4H.8041.../2320059 | Diesel Leakage issue Call By Customer Name :- Chander Dev Mobile No :-9810778173 | Open | Sudh Investments Private Limited | Vidyut Engineers - Noida | 91 | Diesel leakage issue from Loose Pipe. Tighten the same, Issue resolved. | Closed | Kapil Solanki
8 | 210347583 | 2024-01-30 14:14 | 750 | DV2.8501.C4../2320028 | ENGINE STARTING PROBLEM | Task Start | Merino Industries Ltd. | Diesel Engineers Sales & Service - Ghaziabad | 3.5 | No DEF Consumption in 1st bank (SPN/FMI: 523576/0), SD team replaced Dosing module, Issue resolved. | Closed | Kapil Solanki
9 | 210347619 | 2024-01-30 14:21 | 125.4 | 4H.8041.../2320198 | Starting Issue Email By - Service Dealer Name -Sonu Rai | Open | BKD.J.Packagings Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 26 | No DEF Consumption (SPN/FMI : 4358/2 & 4095/1), Voltage Supply at Supply module Ok, Seems SM faulty arranged with Dealer Sister branch, will replace tomorrow. | Open | Kapil Solanki
10 | 210347811 | 2024-01-30 15:06 | 125.4 | 4H.8041.../2320110 | DG Is Not Start In First Crank Email By Customer Name:- Manoj K Saini | Task Start | Oceanica Infratech LLP. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 6 | Engine starting issue. As During HPP replacement activity multiple times Fuel line removd & connected, SD team replaced all Copper washer, Issue resolved. | Closed | Kapil Solanki
11 | 210347907 | 2024-01-30 15:22 | 320 | F6.8802.../2320080 | Return Pipe replace | Completed | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 4 | Injector leak-off Pipe damaged, replaced the same, issue resolved. | Closed | Kapil Solanki
12 | 210348015 | 2024-01-30 15:40 | 30 | 3H.8902.../2320048 | Starting Issue Email By - Service Dealer Name -Rakesh Singh | Task Start | PARNAMI PUMP PROJECT PVT LTD | Vidyut Engineers - Noida | 106 | SPN/FMI: 2791/31, 5838/3 520528/31, 5838/2 & 5838/1, EGR Valve chocked due to excessive Carbon deposition, cleaned the same, Issue resolved. | Closed | Kapil Solanki
13 | 210348049 | 2024-01-30 15:45 | 30 | 3H.8902.../2320025 | Starting Issue Call By Customer Name :-Bhupendr Singh Mobile No :-9354306513 | Task Start | Gabsons Group | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 20 | Y-Phase under Voltage alarm, Fuse blown out, replaced fuse, issue resolved. | Closed | Kapil Solanki
14 | 210348377 | 2024-01-30 16:28 | 125.4 | 4H.8041.../2320101 | Starting Issue Email By Service Dealer Name:- Madan Chhimpa | Task Start | ALTOS ENGINEERS PVT LTD. | Paluck Technologies Ltd. - Gurgaon | 19 | ECM Fault (516166/0), Just reset the alarm, Issue resolved. | Closed | Kapil Solanki
15 | 210348473 | 2024-01-30 16:43 | 125.4 | 4H.8041.../2320129 | Starting Issue Call By Customer Name-Birjesh No-7011027591 | Task Start | MANOJ KUMAR | Vidyut Engineers - New Delhi | 9.16 | DEF tank temp High alarm, SD team just reset DTC, Issue resolved | Closed | Kapil Solanki
16 | 210348789 | 2024-01-30 17:30 | 320 | F6.8802.../2320020 | Tripping Issue Call By Customer Name :-Raju .. Number :-8700943607 | Open | SSF POLYMERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 74 | SPN/FMI : 655/5, 2 no Injector's wiring damaged, temporarily fixed by SD team, issue still open as multiple case for observed wirning damaged | Open | Kapil Solanki
1 | 210345213 | 2024-01-29 18:13 | 320 | F6.8802.../2320060 | Power Supply Issue Call By customer Name-Rohit No-9149075750 | Open | Ghaziabad Mechfab Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Aligarh | 10 | DG running overload also Jerk load upto 430 Amp, Educated Customer to operate DG in @ 80 % load to obtain higher efficiency . | Closed | Sudhir Awasthi
2 | 210344501 | 2024-01-29 16:26 | 125.4 | 4H.8041.../2320128 | Diesel leakage Issue Call By Customer Name:- :- Akshay ... Number :- 9781007797 | Task Start | Powermech Disels | OVN Industries Private Limited - New Delhi | 6.6 | Diesel leakage from Line (Technician not specified Pipe) will collect more update. | Closed | Kapil Solanki
3 | 210343652 | 2024-01-29 14:12 | 320 | F6.8802.../2320021 | Dosing Module Gasket Change Email By Service Dealer Name-Madhu Sudan Sharma | Task Start | Marvel Ceramic Pvt. Ltd. | Power Trading Company - ALWAR | 62.5 | SR generated for DM Gasket campaign activity (Campaign SR not generated from HO) | Closed | Gourav Sharma
4 | 210343530 | 2024-01-29 13:52 | 320 | F6.8802.../2320034 | Engine KRM Not Working Email By-Service Dealer Name:- Neetu Kaushik | Open | Maxwel Exporters | R K Engineers - Meerut | 11.3 | KRM unit not active, SD team connected with ASE for activation, Mail done by ASE to KRM team. | Open | Sudhir Awasthi
5 | 210343448 | 2024-01-29 13:32 | 125.4 | 4H.8041.../2420022 | Red lamp alarm issue Call By Customer Name :-Rajeet Number :-9992255442 | Task Start | NAV. Ambika Agro LLP. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 3.5 | DEF level sensor stuck, Cleaned the same, Issue resolved. | Closed | Kapil Solanki
6 | 210343058 | 2024-01-29 12:13 | 200 | 6H.8435.../2320023 | Starting issue Call By Customer Name :Rohit ... Number :7017202883 | Task Start | Maxwel Exporters | R K Engineers - Meerut | 11 | Starting issue due to e-Feed Pump not working as Logic from GCU not enabled (Preheat time), corrected the same, Issue resolved | Closed | Kapil Solanki
7 | 210342380 | 2024-01-29 10:12 | 82.5 | 5H.8901.../2320069 | AD Blue Faulty Issue Call By Customer Name:- Chandrasain .. Number:- 9717984068 | Task Start | Fashion Makers Industries Pvt. Ltd. | Vidyut Engineers - Noida | 55 | Low DEF level @ 30% (SPN 1761), Topup done, Issue resolved | Closed | Kapil Solanki
8 | 210342335 | 2024-01-29 10:04 | 500 | DV8.8501.C4../2320033 | Load Issue Call By Customer Name : M.I Khan Mobile No :9306952708 | Task Start | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 16 | Updated Slow Ramp up file (DV.1234) Cal file, also mains contactor burnt,Customer replaced itself. Issue resolved. | Closed | Kapil Solanki
3 | 210338012 | 2024-01-27 11:16 | 125.4 | 4H.8041.../2320101 | 9711360601 | Task Start | ALTOS ENGINEERS PVT LTD. | Paluck Technologies Ltd. - Gurgaon |  | DG not started in first crank. Customer registered complain later again started. DG got started, no visit done by SD team, SR cancelled. | Cancelled | Kapil Solanki
4 | 210338115 | 2024-01-27 11:33 | 25 | GP3.8702.../2320025 | starting complaint Email By - KGD Name - Yash Dev Dahiya | Task Start | Ind Spinx Precision Limited (Unit-B) | Royal Power Solution - Zirakpur |  | Engine starting issue, SPN/FMI: 102/3, 2802/4 & 2791/1, ECU not responding, somewhwer loose connection in Panel, Team still working | Open | Ved Gupta | Need to check
5 | 210338756 | 2024-01-27 13:12 | 250 | F6.8841.../2320017 | Coolant Leakage Issue Call By Customer Name :Rajinder Saini Satvik Mobile No :9716627693 | Task Start | Power Control System | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 20 | Coolant leakage from Hose due to loose clip(Thrmostat housing to Radiator), Tighten the same, Issue resolved. | Open | Kapil Solanki
6 | 210338851 | 2024-01-27 13:32 | 40 | 3H.8951.../2320001 | Starting Issue Email By Service Dealer Name:- Neetu Kaushik | Task Start | Mr. Vinay Khanna | R K Engineers - Meerut | 24.8 | Engine starting issue, SPN/FMI: 157/3, Battery Possitive (2a) wire loose in XDBK4 Connector, tighten the same, Issue resolved. | Closed | Sudhir Awasthi | Detail to be share to QA
1 | 210338867 | 2024-01-27 13:44 | 57 | T4.8941.../2320043 | Starting Issue Call By KGD Name :Gurpreet Kaur Mobile No :9311523743 | Open | M/s. Classic Generatos | Vidyut Engineers - New Delhi | 1.4 | Battery charger connection not done during Commissioning (as Wire not provided by Customer), Yesterday Connection done, Issue resolved. | Closed | Kapil Solanki | To be check CC efsr
2 | 210341178 | 2024-01-28 11:12 | 82.5 | 5H.8901.../2320012 | NPD lamp alarm issue Call By Customer Name :Aman Mobile No :9034678749 | Open | Supercircle Private Limited | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 40 | Low DEF level alarm @ 7%, Topup done, Issue resolved. | Closed | Kapil Solanki
3 | 210335248 | 2024-01-25 19:43 | 200 | 6H.8435.../2320023 | .Starting Issue Call By Customer Name: Ankur Number :7895999777 | Open | Maxwel Exporters | R K Engineers - Meerut | 10 | Starting issue due to e-Feed Pump not working (Low Voltage supply at Motor 8 Volts only), issue still Open SD team will revisit the site. | Open | Sudhir Awasthi
4 | 210334014 | 2024-01-25 17:07 | 82.5 | 5H.8901.../2320093 | Alarm Issue Call By Customer Name :-Sumit Mongia Number :-9818430800 | Task Start | GENERAL AUTOMOTIVES COMPONENTS | Paluck Technologies Ltd. - Gurgaon | 53 | Amber Lamp On due to Low DEF level @ 38 %, Educate to top up the same timely, Issue resolved. | Closed | Kapil Solanki
5 | 210332925 | 2024-01-25 14:50 | 82.5 | 5H.8901.../2320082 | Vinod Jai Regidancy | Task Start | Jai Residency | M/s OM Diesels Pvt. Ltd. - Rohtak | 1 | SPN/FMI: 100/3. DG Tripping due to High Oil Pressure alarm, No solution from HO side. | Open | Kapil Solanki
6 | 210332725 | 2024-01-25 14:16 | 20 | GP3.8601.../2320025 | Battery voltage high issue Call By OEM Name :- Rajesh No :9996788584 | Open | Supreme Enterprises. | M/s OM Diesels Pvt. Ltd. - HISAR | 5 | Alternator High Voltage issue, SD team just checked Alternator Output voltage & Kept under observation. | Open | Kapil Solanki
7 | 210332701 | 2024-01-25 14:05 | 125.4 | 4H.8041.../2320020 | Starting Issue Call By Customer Name :Sonu Mobile No :9716630077 | Task Start | Rush Enterprises | Vidyut Engineers - New Delhi | 153 | e-Feeder Pump NRV Valve faulty also SPN 51/0 in DM2 & 5461/0 on DM1, NRV replaced but not carried out any job on DTC | Open | Kapil Solanki
8 | 210332589 | 2024-01-25 13:34 | 320 | F6.8802.../2320017 | Tripping issue Call By Service Dealer Name:-Vikas Saini Mobile No:- 7027820033 | Task Start | MT. Autocraft | M/s OM Diesels Pvt. Ltd. - Rohtak | 13 | Amber Lamp On due to Low DEF level @ 30 %, Educate to top up the same timely, Issue resolved. | Closed | Kapil Solanki
9 | 210332119 | 2024-01-25 12:04 | 40 | 3H.8951.../2320025 | MCB Issue & Preventive Maintenance Call By Customer Name :-Chetan Number :-9034113888 | Task Start | Kanha Nature Oils | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 19 | MCB tripping issue, SD team just mentioned 'Negative wire faulty' issue still Open, will conenct with SD team. | Open | Kapil Solanki
10 | 210332069 | 2024-01-25 11:55 | 500 | DV8.8501.C4../2320017 | Oil Leakage Issue call by customer Name:-Sanjiv Kumar Number:-8814828270 | Open | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat | 43.8 | Fuel leakage from High pressure Line, Tighten the same, Issue resolved. | Closed | Kapil Solanki | Need to confirm location
1 | 210331700 | 2024-01-25 10:59 | 125.4 | 4H.8041.../2320059 | AD Blue Faulty Issue Call By Customer Name:- Chandrasain .. Number:- 9717984068 | Open | Sudh Investments Private Limited | Vidyut Engineers - Noida | 85 | No DEF in Tank, Top up done also Educated Customer to top up the same timely, Issue resolved. | Closed | Kapil Solanki
2 | 210331026 | 2024-01-25 07:41 | 62.5 | T4.8941.../2320015 | Starting Problem Call By:- Customer Name:- Azad Singh No:- 9694431404 | Open | OM MULTISPECIALITY HOSPITAL | Power Trading Company - Bhiwadi ( Alwar) | 11 | Starting issue due to Air Lock in Fuel line, Bleed the system, Issue resolved. | Closed | Gourav Sharma | Need to confirm location
3 | 210345213 | 2024-01-29 18:13 | 320 | F6.8802.../2320060 | Power Supply Issue Call By customer Name-Rohit No-9149075750 | Open | Ghaziabad Mechfab Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Aligarh | 10 | 420690425 | 631035637 | 2024-01-29 18:13 | 320
4 | 210344501 | 2024-01-29 16:26 | 125.4 | 4H.8041.../2320128 | Diesel leakage Issue Call By Customer Name:- :- Akshay ... Number :- 9781007797 | Task Start | Powermech Disels | OVN Industries Private Limited - New Delhi | 6.6 | 420689000 | 631033499 | 2024-01-29 16:26 | 125.4
5 | 210343652 | 2024-01-29 14:12 | 320 | F6.8802.../2320021 | Dosing Module Gasket Change Email By Service Dealer Name-Madhu Sudan Sharma | Task Start | Marvel Ceramic Pvt. Ltd. | Power Trading Company - ALWAR | 62.5 | 420687301 | 631030950 | 2024-01-29 14:12 | 320
6 | 210343530 | 2024-01-29 13:52 | 320 | F6.8802.../2320034 | Engine KRM Not Working Email By-Service Dealer Name:- Neetu Kaushik | Open | Maxwel Exporters | R K Engineers - Meerut | 11.3 | 420687056 | 631030582 | 2024-01-29 13:52 | 320
7 | 210343448 | 2024-01-29 13:32 | 125.4 | 4H.8041.../2420022 | Red lamp alarm issue Call By Customer Name :-Rajeet Number :-9992255442 | Task Start | NAV. Ambika Agro LLP. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 3.5 | DEF level sensor stuck, Cleaned the same, Issue resolved. | Closed | Kapil Solanki
8 | 210343058 | 2024-01-29 12:13 | 200 | 6H.8435.../2320023 | Starting issue Call By Customer Name :Rohit ... Number :7017202883 | Task Start | Maxwel Exporters | R K Engineers - Meerut | 11 | Starting issue due to e-Feed Pump not working as Logic from GCU not enabled (Preheat time), corrected the same, Issue resolved | Closed | Kapil Solanki
| 210342380 | 2024-01-29 10:12 | 82.5 | 5H.8901.../2320069 | AD Blue Faulty Issue Call By Customer Name:- Chandrasain .. Number:- 9717984068 | Task Start | Fashion Makers Industries Pvt. Ltd. | Vidyut Engineers - Noida | 55 | Low DEF level @ 30% (SPN 1761), Topup done, Issue resolved | Closed | Kapil Solanki
| 210342335 | 2024-01-29 10:04 | 500 | DV8.8501.C4../2320033 | Load Issue Call By Customer Name : M.I Khan Mobile No :9306952708 | Task Start | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 16 | Updated Slow Ramp up file (DV.1234) Cal file, also mains contactor burnt,Customer replaced itself. Issue resolved. | Closed | Kapil Solanki