## JAN 25
\ | Zone | Incident Id | Creation Date | KVA Rating | Engine no | Customer VOC | SR Status | Account Name | Running Hrs | Observation | Incident Status | ASM Name | HO remark
1 | NORTH | 211556864 | 2025-01-01 18:28 | 15 | GP3.8501.../2421248 | Error Code Issue. Call by Customer Name :Umakant No :8840402728 | Open | RIYA MISHRA | 75 | Found EGR valve chocked, replace the EGR issue resolve | Closed | Sudhir Awasthi
2 | NORTH | 211556473 | 2025-01-01 17:18 | 58.5 | T4.8941.../2421724 | Leakage Issue | Task Start | Amit Chopra | 76 | Coolant Leakage found frome hose of Thermo-stat to water body assembly,Tightened the same & resolve the issue | Closed | Ved Prakash Gupta
3 | NORTH | 211556459 | 2025-01-01 16:58 | 125.4 | 4H.8041.../2320111 | Starting/Stopping Issue | Task Start |  | 160 | SR Opened as per KRM Tracker;AdBlue Level found Low,Voltage supply to SM connector found ok,Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
4 | NORTH | 211555666 | 2025-01-01 16:46 | 58.5 | T4.8941.../2423040 | Leakage Issue | Task Start | TA CONSTRUCTION COMPANY | 23 | krm not working R wire removed from KRM after refitted the wire then KRM working ok with all parameter | Closed | Sudhir Awasthi
5 | NORTH | 211554667 | 2025-01-01 16:20 | 250 | F6.8841.../2420428 | Low Fuel Level Call By Customer Name :- Deepak Gupta Mobile No :- 8708530033 | Task Start | Svasca Industries ( Ind) Ltd | 19 | Fuel level sensor not proper working, remove the sensor after refitted again issue resolve | Closed | Kapil Solanki
6 | NORTH | 211554622 | 2025-01-01 16:01 | 57 | T4.8941.../2320041 | Starting issue Call By Customer Name :- Rajesh Mobile No :- 9810247079 | Task Start | Shyam Packers (India) | 646 | Electrolite level low, top the electrolite battery charge after start the DG with another battery found no issue | Closed | Kapil Solanki
7 | NORTH | 211554422 | 2025-01-01 15:16 | 40 | 3H.8951.../2421028 | INSTANCE ID:-100787876 SITE ID:- PUNQJL0561 CALL BY CUSTOMER\\ DG ISSUE:-automation issue NAME:-ranjit sing NUMBER:-9875944510 | Task Start | ATC Telecom Infrastructure Private Limited | 42 | DG Auto stopping issue due to issue found in customer's pannel so same advised to customer to corrected the mains connections | Closed | Ved Prakash Gupta
8 | NORTH | 211554151 | 2025-01-01 14:37 | 125.4 | 4H.8042.C4../2420719 | Load and Amber Lamp Alarm and Tripping issue Call By Customer Name :- Rakesh Mobile No :- 9050086860 | Task Start | VIRENDER | 11.34 | SR Opened as per KRM Tracker SPN/FMI-1761/16 AdBlue Level Low ; Top-up the same & resolve the issue,same educated to Customer | Closed | Ved Prakash Gupta
9 | NORTH | 211554137 | 2025-01-01 14:23 | 500 | DV8.8501.C4../2420055 | SYNCHRONIZATION | Task Start | Sobha Ltd. | 5 | under load testing synchronisation and start engine working on manual testing done | Closed | Kapil Solanki
10 | NORTH | 211554091 | 2025-01-01 14:14 | 500 | DV8.8501.C4../2420105 | SYNCHRONIZATION | Task Start | Sobha Ltd. | NA | under load testing synchronisation and start engine working on manual testing done | Closed | Kapil Solanki
11 | NORTH | 211553835 | 2025-01-01 13:02 | 58.5 | T4.8941.../2422414 | Electrical Problems | Open | Anshu global Trade |  | Under Cancellation | Cancelled | Ved Prakash Gupta
12 | NORTH | 211553768 | 2025-01-01 12:27 | 125.4 | 4H.8041.../2420994 | Starting/Stopping Issue | Task Start | PINNACLE DENTAL | 20.5 | Oil dipstick removed After refitted the dipstick then start the DG start but auto shutdown without alarm, tightness EMS connector then Start the DG for 30min. Issue resolve | Closed | Kapil Solanki | Under obs
13 | NORTH | 211553676 | 2025-01-01 11:53 | 250 | F6.8841.../2320011 | Water Into DG Issue Email by Customer Name - Mahesh Thakur | Open | Advantec Wheels Pvt. Ltd. |  | Under Cancellation | Cancelled | Ved Prakash Gupta
14 | NORTH | 211553487 | 2025-01-01 10:51 | 30 | 3H.8902.../2420988 | VOC-ENGINE NOT STARTING - AIR LOCK IN FUEL SYSTEM Customer Name -Sanjeev Mahajan Customer Number-9417308225 Mode- SR Generated through CDI calling. | Task Start | Shiva Foam House | 20 | Starting issue due to 2A wire found loose on RL1 at 12RB1 Relay caed so connected the same & resolve the issue | Closed | Ved Prakash Gupta
15 | NORTH | 211553425 | 2025-01-01 10:22 | 125.4 | 4H.8042.C4../2420057 | Diesel Leakage Issue Call By Customer Name :- Virendra Pal Mobile No :- 8779904318 | Closed | SHUBHAM RMC SERVICES PRIVATE LIMITED | 726 | Lub oil leakage from rocker cover, paste with anabond now no leakage found | Closed | Sudhir Awasthi
16 | NORTH | 211553386 | 2025-01-01 09:48 | 62.5 | T4.8941.../2420261 | Starting/Stopping Issue | Closed | Amson Transformers | 575 | Voltage flactuation issue due to 3 motor used as load,No issue in DG when motor is not running on load side,same educated to customer | Closed | Ved Prakash Gupta
17 | NORTH | 211553384 | 2025-01-01 09:45 | 30 | 3H.8902.../2420414 | Under Speed Alarm And Red lamp on alarm issue Call By Customer Name - Vicky .. Number - 9548694250 | Task Start | Tanu Engineering Products Private Limited.** | 1910 | EGR valve alarm 633 Clear the code i-konnect then issue resolve | Closed | Kapil Solanki
18 | NORTH | 211560268 | 2025-02-01 13:40 | 320 | F6.8802.../2320018 | Battery Replacement Issue Call By Customer Name :- Manoj Mobile No :- 9660005612 | Task Start | Geeta Metal | 185 | Old battery replace with new battery, Old battery electrolite not found then change with new After check the battery with topup electrolite after refitted old start the Dg found ok, issue resolve | Closed | Gourav Sharma
19 | NORTH | 211560264 | 2025-02-01 13:39 | 500 | DV8.8501.C4../2420057 | Tripping Â Issue Call By Customer Name :- Shubhas .. Mobile No :-9990046306 | Task Start | INDIA GOVERMENT MINT (A UNIT OF SECURITY PRINTING & MINTING CORPN. OF INDIA LTD.) | 33.25 | AMF panel issue from customer end jackson panel | Closed | Kapil Solanki
20 | NORTH | 211560116 | 2025-02-01 13:14 | 320 | F6.8802.../2320081 | ECU alarm issue & Loading issue Call By Customer Name - Punit Gupta Number - 8233536121 | Task Start | G P AUTO INDUSTRIES | 119 | Under speed- Air remove & found no issue run the DG for 20min. With load | Closed | Gourav Sharma
21 | NORTH | 211560038 | 2025-02-01 12:41 | 320 | F6.8802.../2420009 | Loading Issue Call By Customer Name :- Nitesh .. Mobile No :- 9528212304 | Task Start | DIVYANSH HOMES PRIVATE LIMITED | 458 | unbalance load - Advice to customer please balancin the load all three phases | Closed | Kapil Solanki
22 | NORTH | 211559945 | 2025-02-01 12:22 | 15 | GP3.8501.../2420509 | Stopping Issue Call By Customer Name :- Satpal ... Mobile No :-9501967345 | Task Start | Cliff Computers. | 49 | Customer raised complaint as automatic starting but no such issue found on site | Closed | Ved Prakash Gupta
23 | NORTH | 211559874 | 2025-02-01 12:08 | 40 | 3H.8951.../2420102 | Automation issue Call By Customer Name - Ashish Goel Number - 8800192923 | Task Start | Admach Auto Inustries India Pvt. Ltd. | 2 | DG panel MCB in OFF condition so DG not start after check and ON the MCB then start the DG both condition AUTO/MAN. Found no issue | Closed | Kapil Solanki
24 | NORTH | 211559812 | 2025-02-01 12:00 | 125.4 | 4H.8041.../2420019 | Not taking load | Task Start | Rahee Infratech Ltd. | 3666 | found ECU Falt, Throttle valve Jammed, check All wiring Connector and clear alarm with i connect and test generator on load check manual found alarm spn -4095,4339. Uria DEF tank cleaning required with Pipe line and filter. customer last service 4 APR 2024 ko 12 hours doing with our company Now service with on paid basis | Closed | Kapil Solanki
25 | NORTH | 211559788 | 2025-02-01 11:49 | 20 | GP3.1021.../2420345 | INSTANCE ID:-100777978 SITE ID:- I-UE-KEAT-ENB-G002 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- RAAMPRAKASH NUMBER:- 8299599379 | Open | Reliance Jio Infocomm Limited | 279 | Found relay card defective, replace with new then issue resolve | Closed | Sudhir Awasthi
26 | NORTH | 211559783 | 2025-02-01 11:42 | 20 | GP3.8601.../2421121 | Automation Issue Call By Customer Name :- Shabir Khan Mobile No :- 8430299043 | Task Start | THE MUSLIM EDUCATION WELFARE SOCIETY | 2 | Customer side panel issue- auto connection ok to our side | Closed | Sudhir Awasthi
27 | NORTH | 211559780 | 2025-02-01 11:42 | 160 | 6H.8475.../2420027 | Starting issue Call by customer Name: Pawan Number:9821823936 | Task Start | AVL36GURGAON Apartment Owners Association | 140 | Electric feed pump wiring broken, refitted again issue resolve | Closed | Kapil Solanki
28 | NORTH | 211559777 | 2025-02-01 11:42 | 125.4 | 4H.8041.../2420071 | Oil Compunction Issue Call By Customer Name :Atish Kumar No : 9910890730 | Task Start | L Artisan Products | 92 | Found no leakage in Engine, but low oil level need to be topup | Closed | Kapil Solanki
29 | NORTH | 211559118 | 2025-02-01 10:38 | 58.5 | T4.8941.../2423031 | VOC- Displayed issue . Customer Name - Bhawani Singh Customer Number -9785201587 Mode- SR Generated through CDI calling. | Task Start | SHRI BANDE KA BALAJI |  | Cancelled-Customer not approve | Cancelled | Gourav Sharma
30 | NORTH | 211559097 | 2025-02-01 10:35 | 82.5 | 5H.8901.../2320005 | Starting issue | Task Start | Noxon Blowers Pvt. Ltd. | 139.31 | Starting issue due to 2AB fuse found faulty due to which AdBlue Level not showing to controller so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
31 | NORTH | 211558983 | 2025-02-01 10:12 | 125 | F6.9840.../2420030 | Starting Problem | Task Start | Cinturones Alvi (India) Pvt. Ltd. | LR-3.19 | GAS ENGINE- Dg commissioning hold due to silencer not ok & Gas pressure set through PRV trial without load 1 hour DG running good condition | OPEN | Kapil Solanki
32 | NORTH | 211558971 | 2025-02-01 10:07 | 15 | GP3.8501.../2420684 | Under Speed Alarm & Under Voltage Alarm & Amber Lamp On Alarm. Issue Call By Customer. Name:- Rajiv Kumar Gupta Mobile No.:- 9520134444 | Task Start | Rajat Communication | 84 | SPN/FMI 2802/4, 2791/14 remove the EGR connector after clean and refitted clear the all fault code issue resolve | Closed | Sudhir Awasthi
33 | NORTH | 211558965 | 2025-02-01 10:06 | 320 | F6.8802.../2420059 | Starting issue Call By Customer Name :-Sunil Kumar Mobile No :-8447109874 | Closed | Radius Synergies International Pvt Ltd. | 75.55 | Low coolant level topup 5L coolant & found SPN/FMI 97/2, 3031/14, 2802/4, 6595/0, 520527/2 clear the all fault code with i-konnect tool | Closed | Kapil Solanki
34 | NORTH | 211558889 | 2025-02-01 09:58 | 500 | DV8.8501.C4../2320075 | Starting Issue Call By Customer Name :- Amresh Kumar Mobile No :-9319831265 | Task Start | C.E. INFO SYSTEMS LIMITED | 58.22 | Morning time DG not start in auto showing the alarm Under speed,Under frequency, Under Voltage after run the Dg in manual mode start the DG ok condition now flash the ECU after | Closed | Kapil Solanki | ECU datA
35 | NORTH | 211558879 | 2025-02-01 09:55 | 500 | DV8.8501.C4../2320078 | Starting issue Call By Customer Name :- Amresh Kumar Mobile No :- 9319831265 | Task Start | C.E. INFO SYSTEMS LIMITED | 67 | Morning time DG not start in auto showing the alarm Under speed,Under frequency, Under Voltage after run the Dg in manual mode start the DG ok condition now flash the ECU after | Closed | Kapil Solanki
36 | NORTH | 211558864 | 2025-02-01 09:48 | 0 | GP3.8501.../2421907 | FIP CALLIBRATION | Task Start | Electro Equipments | LR- | fuel pump fitment work then replace new pump and start engine on load running normally | Closed | Sudhir Awasthi
37 | NORTH | 211558506 | 2025-02-01 09:04 | 40 | 3H.8951.../2420813 | Starting Issue And Low Speed Alarm Call By Customer Name :- Ajay Chauhan Mobile No :-8368286524 | Closed | Asha Gadia. | 20.9 | Emergency switch was pressed, Realease the same & unbalance load advice to customer for balancing the load | Closed | Kapil Solanki
1 | East | 211560578 | 2025-02-01 14:33 | 20 | GP3.8601.../2420650 | Starting/Stopping Issue | Task Start | STATE BANK OF INDIA |  | Update pending | OPEN | Subhrajit Roy
2 | East | 211560109 | 2025-02-01 13:14 | 58.5 | T4.8941.../2421415 | Fan belt Loosing Issue Call By Customer Name- Subodh kumar Mo.No.- 9382163206 | Task Start | KALYAN JEWELLERS INDIA LTD | 324 | SE found belt loose so tighten the belt | CLOSED | Prabhakar Kumar
3 | East | 211559779 | 2025-02-01 11:42 | 125.4 | 4H.8041.../2420334 | Mobil Oil Leakage Call by Customer Name : Prem Kumar No : 7033285136 | Task Start | M/s. Om Hosiery | 70 | Lube oil leakage was from the Oil sump welded drain plug nut. Need to replace | OPEN | Prabhakar Kumar
4 | East | 211559734 | 2025-02-01 11:38 | 58.5 | T4.8941.../2422214 | Doorlock Issue & Fuel Level Issue Call By Customer. Name:- Shivam Kumar Mobile No.:-9334993361 | Task Start | TIRUPATI ICON | 35 | Due to the bending of Door locking hook it do not close so adjusted and restored | CLOSED | Prabhakar Kumar
5 | East | 211545217 | 31-12-2024 12:12 | 15 | GP3.8501.../2421125 | Shut Down Alarm Issue Call By Customer Name :- Pramod .. Mobile No :-9934351151 | Open | NUCOMB ENGINEERING PRIVATE LIMITED |  | Today SE will visit | OPEN | Subhrajit Roy
6 | East | 211560595 | 2025-02-01 14:43 | 625 | DV0.8501.C4…/2420080 | Leakage Issue | Task Start | Shiv Shakti Industries | 24 | There was ECU amber alarm due to low Urea level (30%) and on inspection found raditor fan and its cover was wet by lube oil. Lube oil leakage was from oil cooler allen bolt and hexabolt loose, Bolt was loose from the plant as the torque mark found Ok. So tighten and test found no leakage. | CLOSED | Prosanjit saha
7 | East |  |  | 20 | GP3.8604../2420083 | lube oil dilution | Task Start | RELIANCE JIO INFOCOMM LIMITED | 2 | As per complaint SE checked the lube oil by dipstick and drain it found coolant diluted with coolant and check for valve condition found OK. Under observation | OPEN | Prabhakar Kumar
8 | East | 211559026 | 2025-02-01 10:29 | 30 | 3H.8902.../2420192 | Loading issue & White Smoke issue Call By Customer Name :- Chinmay Malik Mobile No :- 9337888506 | Task Start | Chinmayee Mallick. | 222 | SE found DG not start due to fuel level low and air lock in fuel line after top up the fuel level and release the air in fuel line then start the DG running ok & educated to customer maintain fuel in fuel tank minimum 50 percent ,this problem not happen in future. | CLOSED | Ujjwal Das
1 | West | 211553597 | 2025-01-01 11:29 | 200 | 6H.8435.../2420077 | Air Lock Issue Call By Customer Name :-Pravin Pujari Mobile No :-7387288933 | Closed | Starnext Innovations Private Limited. | 3.34 | Genset fail to start & Low fuel level alarm. Tightened the start relay wires. | Closed
2 | West | 211559014 | 2025-02-01 10:19 | 160 | 6H.8475.../2420118 | Red Lamp On Alarm Issue Call By Customer Name :- 9623196273 Mobile No :- Mahadev .. | Task Start | Lifeline Mauli Hospital LLP. | 155 | SPN/FMI- 5461/8, Calibrated the ECU with Dummy file. | Closed
3 | West | 211553568 | 2025-01-01 11:16 | 58.5 | T4.8941.../2422058 | Starting Issue Call By Customer Name - Siddhanath Shetye Number - 9823994468 | Task Start | Shetye Sales | 588 | SPN/FMI-5841-10-Diesel Exhaust Fluid Quality Malfunction - Abnormal Rate of Change. After cleared the DTC,Problem resolved. | Closed
4 | West | 211558895 | 2025-02-01 10:07 | 40 | 3H.8951.../2420705 | Automation Issue Call By Service Dealer Name :- Mukesh Mobile No :- 7583889815 | Task Start | M/S Banerjee Electrical Repairing Shop | 29 | Customer Side panel on/off issue. | Closed
5 | West | 211559106 | 2025-02-01 10:39 | 5.5 | CC1.1013.../2400593 | Starting Issue Email By KGD Name:-Poonam Shedage | Task Start | Accurate Powertech India Private Limited | Na | The panel power supply fuse was blown. | Closed
6 | West | 211559908 | 2025-02-01 12:08 | 750 | DV2.8501.C4../2420178 | ECU alarm issue Call by customer Name: Satyandar Number:9657932174 | Closed | Sairama Realty. | 6.19 | SPN/FMI- 656/3(Short circuit of the power stage low side cylinder 6 injector A circuit high) was showing in the controller. This case is under observation. | Task Start
7 | West | 211556781 | 2025-01-01 17:57 | 320 | F6.8802.../2420276 | Tripping issue Call By Customer Name :-Gaurav Pandey Mobile No :- 9879609299 | Task Start | Sardar Smarak Hospital | 22 | Low DEF level. 48% | Closed
8 | West | 211554407 | 2025-01-01 15:09 | 58.5 | T4.8941.../2420788 | Starting Issue Call By Customer Name :- Jagnik Pamar Customer :- 9904654660 | Closed | BND TECHNOLOGIES PRIVATE LIMITED | 22 | SPN/FMI- 157/14, tightened all panel wires and cleared DTC. | Closed
3 | NORTH | 211568745 | 2025-04-01 12:58 | 30 | 3H.8902.../2421005 | we are not able to start DG. 500396 | Task Start | ICICI Bank Limited | 56 | Charging alternator not working then he repaired after check and found working normally | Closed | Sudhir Awasthi
4 | NORTH | 211568679 | 2025-04-01 12:51 | 200 | 6H.8435.../2420020 | Leakage Issue | Task Start | Shanti Prakash Associates. |  | Wrong report Sr | Closed | Kapil Solanki
5 | NORTH | 211568461 | 2025-04-01 12:11 | 125.4 | 4H.8041.../2420252 | Display issue Call By Customer Name :- Ayesha Mobile No :-9958891400 | Task Start | Green Energy Diesel Engines Private Limited. | 42 | Customer panel side problem | Closed | Kapil Solanki
6 | NORTH | 211568065 | 2025-04-01 10:58 | 58.5 | T4.8941.../2422051 | Starting Issue Call By OEM Name :- Niraj kumar Mobile No :-9996728387 | Task Start | Zensho Food India Private Limited. | 11 | Customer machine side problem, DG is ok running both condition Auto & Manu. | Closed | Kapil Solanki
7 | NORTH | 211567911 | 2025-04-01 10:19 | 0 | F6.8841.../2420393 | Lub Oil Leakage Issue | Task Start | Western Consolidated Private Ltd. | LR-0.5 | lub oil leakage from oil cooler O ring change then issue resolve | Closed | Sudhir Awasthi
8 | NORTH | 211567697 | 2025-04-01 09:28 | 125.4 | 4H.8041.../2420019 | Radiator & diesel tank need cleaning | Completed | Rahee Infratech Ltd. | 3697 | Radiator choke and Adblue tank choke Now Radatior cleaning done with k-cool super and clean fuel tank and Ad Blue tank with filter and clear error code and test generator no load check manual found ok because customer not provide by load. | Closed | Kapil Solanki
9 | NORTH | 211567645 | 2025-04-01 09:20 | 250 | F6.8842.C4../2420062 | Starting Issue And Door Lock Issue Call By Customer Name :- Rajender . Mobile No :-9414501616 | Closed | The Savoy And Holidays Resorts | 19.56 | Control panel wiring all connection tight then clear the fault code , then start the DG running ok, | Closed | Gourav Sharma
10 | NORTH | 211567608 | 2025-04-01 08:41 | 20 | GP3.8604.../2420198 | INSTANCE ID:-100742275 SITE ID:- I-UE-GKPR-ENB-9091 CALL BY CUSTOMER\\ DG ISSUE:- DG NOT STARTING NAME:-shailesh NUMBER:-8299698446 | Task Start | Reliance Jio Infocomm Limited | 150 | ECU programming because hunting issue | Closed | Sudhir Awasthi
11 | NORTH | 211567391 | 2025-04-01 01:57 | 400 | DV8.8542.C4../2320009 | Trip_Genset_Low_Voltage | Task Start | T. C. Health Care Pvt. Ltd. | 210 | SPN 523531,523539,523541,523543,523545,523535,523592 FMI 7 and Adblue line check and All alarm clear and file flash the file After start the DG found running ok | Closed | Kapil Solanki
12 | NORTH | 211566017 | 2025-03-01 18:05 | 125.4 | 4H.8042.C4../2420110 | Canopy Door Issue Call By Customer Name :- Prabhakar Pandey Mobile No :- 9911105274 | Closed | SAMSONIC | 10.5 | canopy door problem from canopy door repairing done with screw driver | Closed | Kapil Solanki
13 | NORTH | 211565394 | 2025-03-01 17:34 | 100 | 4H.8041.../2420416 | Starting Issue Call By Sales Dealer Name :-Surendar Sharma Mobile No :-9919119666 | Task Start | Shree Ram Machinery Sales | 157 | Customer panel side VMR setting | Closed | Sudhir Awasthi
14 | NORTH | 211565176 | 2025-03-01 16:49 | 30 | 3H.8902.../2421423 | DG not starting,GD not working kindly resolve urgently 500246 | Closed | ICICI Bank Limited | 48.63 | Auto Panel issue, DG not start in Auto but when check the Manual found ok running conditon | Closed | Sudhir Awasthi
15 | NORTH | 211565111 | 2025-03-01 16:26 | 125.4 | 4H.8041.../2420070 | Starting Issue Email By KGD Name:-Neeraj Saini | Task Start | Rivah Industries | 410 | Control panel 2e fuse defective change the same issue resolve | Closed | Gourav Sharma
16 | NORTH | 211565083 | 2025-03-01 16:22 | 30 | 3H.8902.../2420621 | Automation Issue Call By Customer Name - SK Sharma Mobile No -9810012472 | Closed | MAPSAN ENGINEERING PRIVATE LIMITED | 587 | Found engine not starting on auto panel due to auto panel not working now we advice to customer please check the Auto panel | Closed | Kapil Solanki
17 | NORTH | 211564908 | 2025-03-01 16:02 | 500 | DV8.8501.C4../2320046 | Starting Issue Call By Customer Name :- Ram Prasad Singh Mobile No :- 9625865970 | Task Start | Green Field Enterprises | 19 | Interface box relay wire loose tightness the same issue resolve | Closed | Kapil Solanki
18 | NORTH | 211564840 | 2025-03-01 15:33 | 100 | 4H.8042.C4../2420049 | Tripping Â Issue Call By Customer Name :- Sudhir Kumar Sharma Mobile No :-8868803183 | Task Start | DIPRA OVERSEAS | 35 | Found fuel filter was chocked so Dg was trip after clean the filter and again refiitted the filter issue resolve | Closed | Sudhir Awasthi
19 | NORTH | 211564769 | 2025-03-01 15:17 | 20 | GP3.8601.../2420279 | Load Issue And Over Voltage Issue Call By Customer Name :- Brijesh Kumar Mobile No :-6392429266 | Task Start | VIPUL KAUSTUB AGRO PRIVATE LIMITED | 435 | found engine start but show in the over current alarm, check found r phase over load so balance the load all 3 phase and again start the engine, issue resolve | Closed | Sudhir Awasthi
20 | NORTH | 211564597 | 2025-03-01 14:53 | 320 | F6.8802.../2420059 | Coolant Leakage issue Call By Customer Name :-Sunil Kumar Mobile No :-8447109874 | Closed | Radius Synergies International Pvt Ltd. | 78.13 | Found the radiator hoses clamp Loose to coolant Leakage and DG EMS KG 7320 unit alarm show SPN:3031 & FMI :14 and fitted the ikonnect tool and all active alarm clear and check the engine coolant hose pipe clamp proper fitted and check the dg set found ok | Closed | Kapil Solanki
21 | NORTH | 211564589 | 2025-03-01 14:52 | 320 | F6.8802.../2420127 | Genset Trip | Task Start | Vikas Polyplast Pvt. Ltd. | 11.3 | Fan belt broken, replace the same issue resolve | Closed | Gourav Sharma
22 | NORTH | 211564555 | 2025-03-01 14:48 | 30 | 3H.8902.../2420414 | FUEL FILTER REPLACE | Completed | Tanu Engineering Products Private Limited.** | 1924 | fuel filter assembly, fuel pipe copper washer & change v belt | Closed | Kapil Solanki
23 | NORTH | 211564571 | 2025-03-01 14:47 | 200 | 6H.8435.../2420255 | Starting Issue Call By Customer Name :- Kamal Mobile No :- 9650057636 | Closed | Delhi RMC Pvt Ltd / Surendra Spun Pipes | 36 | Engine cranking but not start, battery voltage 9vDC when cranking battery and found v belt loose tighten belt, ecu flashing done issue resolve | Closed | Kapil Solanki
24 | NORTH | 211564393 | 2025-03-01 14:16 | 200 | 6H.8435.../2320011 | Abnormal Sound Â Issue Call By Customer Name :- Babalu Bansal Mobile No :- 9717418942 | Closed | Permeshwar Creations Private Limited. | 1121 | Fan belt loose tightness the same, radiator guard loose tightness the same issue resolve | Closed | Kapil Solanki | Failed Part
25 | NORTH | 211564350 | 2025-03-01 14:09 | 125.4 | 4H.8041.../2420075 | Starting/Stopping Issue | Closed | M. F. INDUSTRIES | 86 | To start found battery terminal is faulty so replaced the same and check to start ems have ecu lamp issue check urea level its low so top up the urea level above 50% | Closed | Kapil Solanki
26 | NORTH | 211564334 | 2025-03-01 13:53 | 20 | GP3.1021.../2420461 | INSTANCE ID:-100784731 SITE ID:-I-UE-ABDD-ENB-0934 CALL BY CUSTOMER// DG ISSUE:- DG ALARM ISSUE NAME:- KRISHNAKANT NUMBER:- 8299698840 | Closed | Reliance Jio Infocomm Limited | 4 | Low voltage alarm, reset the alarm | Closed | Sudhir Awasthi
27 | NORTH | 211564311 | 2025-03-01 13:48 | 20 | GP3.1021.../2420351 | DG BD ( LLOP ISSUE) | Task Start | Reliance Jio Infocomm Limited | 343 | Found Controller 24 no. pin wire loose tightness the same after that issue resolve | Closed | Sudhir Awasthi
28 | NORTH | 211564284 | 2025-03-01 13:47 | 125.4 | 4H.8041.../2420068 | Starting issue Call By Customer Name - Suman .. Mobile No.:- 9546131032 | Closed | A P ASSOCIATES | 55 | Low fuel level, Air in fuel line remove the air issue resolve | Closed | Kapil Solanki
29 | NORTH | 211564047 | 2025-03-01 12:49 | 20 | GP3.8601.../2421048 | Trip_Genset_Low_Voltage | Open | BHAGWATI STONE CRUSHER |  | Cancelled-problem solve in telephonic discussion | CANCELLED | Sudhir Awasthi
30 | NORTH | 211564045 | 2025-03-01 12:48 | 320 | F6.8802.../2420330 | Inspection/Maintenance | Cancelled | Hirohama India Pvt. Ltd. |  | Cancelled-problem solve in PM visit | CANCELLED | Gourav Sharma
31 | NORTH | 211564027 | 2025-03-01 12:40 | 125.4 | 4H.8041.../2420914 | Starting/Stopping Issue | Closed | FINE ENGINEERS AND GENERATORS | 28.34 | Air lock in fuel, removed the air Engine testing on load issue resolve | Closed | Kapil Solanki
32 | NORTH | 211563879 | 2025-03-01 12:19 | 125.4 | 4H.8041.../2420717 | Emergency stop issue Call By Customer Name :Kunal Yadav No :9696814089 | Closed | Hotel Golden Stone. | 19 | found emergency stop swich was pressed, reset the same issue resolve | Closed | Sudhir Awasthi
33 | NORTH | 211563871 | 2025-03-01 12:14 | 30 | 3H.8902.../2421547 | Exhaust Fan Not Working,Direction of Smoke to be changed 499754 | Closed | ICICI Bank Limited | 16 | Exhaust pipe extended required | Closed | Sudhir Awasthi
34 | NORTH | 211563720 | 2025-03-01 11:59 | 20 | GP3.8601.../2420082 | AMF PANEL Issue Email By KGD Name:- Abhimanyu Sharma | Open | Abhishek Medical Hall |  | Cancelled | CANCELLED | Sudhir Awasthi
35 | NORTH | 211563694 | 2025-03-01 11:55 | 125.4 | 4H.8041.../2420641 | Urea Cap Issue Call By Customer Name :- Raja . Mobile No :-7026302584 | Open | KALYAN JEWELLERS INDIA LTD |  | Cancelled-problem solve in telephonic discussion | CANCELLED | Kapil Solanki
36 | NORTH | 211563449 | 2025-03-01 11:02 | 500 | F6.8843.C4../2420002 & 2420002 | Dg lord in stop | Closed | Brij Healthcare & Research Centre. | 126 | DG not taking the load, after load distribute load 60% done after check the DgG on load no issue found SPN/FMI , 4365/2 , 4095/1, 1761/16 , 520527/18, 4365/16 , 3031/14, 3364/8, 1761/16 , 2802/4 Reset the code i-konnect issue resolve | Closed | Sudhir Awasthi
37 | NORTH | 211563444 | 2025-03-01 10:59 | 57 | T4.8941.../2420204 | Starting Issue Call By Customer Name :-Sumit Gupta Mobile No :-9868092364 | Closed | Sumit Gupta Children Hospital. | 251 | Found Battery voltage low, Maintenance due alarm, reset the alarm issue resolve | Closed | Gourav Sharma
38 | NORTH | 211563347 | 2025-03-01 10:40 | 125.4 | 4H.8041.../2420712 | Red Lamp Alarm Call By Customer Name - Ajay . Number - 9953427214 | Closed | SPAN INDIA PRIVATE LIMITED | 11.6 | Reset the alarm with i-konnect tool not mention in the efsr | Closed | Kapil Solanki
39 | NORTH | 211563151 | 2025-03-01 10:18 | 400 | DV8.8542.C4../2420044 | Alarm issue | Closed | A. B. E. C. O. Infrastructures Pvt. Ltd. | 567 | ECU malfunction alarms found SPN/FMI 523582/0, 516166/0 reset with i-konnect tool | Closed | Sudhir Awasthi
40 | NORTH | 211562942 | 2025-03-01 10:07 | 400 | DV8.8542.C4../2420040 | Alarm issue | Closed | Snonwman Logistick Ltd. | 1174 | found ECU Malfunction alarms and 3218/20, 3257/20, 4358/1, 4411/1, 1761/15, 523584/15, 523576/0 clear the all fault code i-konnect tool issue resolve | Closed | Sudhir Awasthi | Recheck and service history
41 | NORTH | 211562871 | 2025-03-01 09:36 | 320 | F6.8802.../2420049 | Starting Issue Call By Customer Name :-Rajiv . Mobile No :-9871294310 | Closed | Vasant Valley School | 345 | Battery discharge, check battery charger AMF panel DC output 23 volt battery charger faulty, then connect DG panel charger found ok | Closed | Kapil Solanki | Charger rating
42 | NORTH | 211562857 | 2025-03-01 09:26 | 160 | 6H.8475.../2420031 | Fan Belt broken Issue Call By Customer Name :- Kunal Mobile No :-9318326116 | Task Start | TRAIN HIGH | 2534 | charging alternator support bolt damage & belt loose and sound belt and new bolt required 17 no charging alternator support bolt required | Closed | Kapil Solanki
43 | NORTH | 211562835 | 2025-03-01 08:53 | 30 | 3H.8902.../2320086 | Starting Issue Call By Customer Name :- Iqbal Mobile No :- 7466830651 | Closed | JAKSON & COMPANY | 72 | Found Water in fuel alarm after remove some water & clear the fault code then issue resolve | Closed | Sudhir Awasthi
44 | NORTH | 211562825 | 2025-03-01 07:35 | 25 | GP3.8702.../2421287 | Starting issue Call By Customer Name :Nisheet Kumar No : 9810778516 | Cancelled | NEERU MATERITY CENTRE |  | Under Cancellation-Problem solve with PM visit | CANCELLED | Kapil Solanki
45 | NORTH | 211561979 | 2025-02-01 18:17 | 250 | F6.8841.../2420254 | Electrical Problems | Closed | Ceigall India Ltd.. | 226 | Start found ems have ecu lamp issue check urea level its low so top up the urea level above 50% now urea level is 74% advice to the customer please maintained urea atleast 50 percent always. | Closed | Kapil Solanki
46 | NORTH | 211561482 | 2025-02-01 16:58 | 20 | GP3.8604.../2420082 | INSTANCE ID:-100740913 SITE ID:-I-UE-MHMD-ENB-9164 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-RAJEEV KUMAR NUMBER:-9335936806 | Cancelled | Reliance Jio Infocomm Limited |  | Under Cancellation | CANCELLED | Sudhir Awasthi
47 | NORTH | 211561147 | 2025-02-01 16:00 | 0 | 4H.8042.C4../2420345 | Line Rejection | Closed | Jakson & Company | LR-1 | ITV change, because jammed the ITV, replace the same issue resolve | Closed | Gourav Sharma
48 | NORTH | 211560867 | 2025-02-01 15:29 | 125 | F6.9840.../2420032 | sensor issue | Task Start | JM. Engineers | LR-2 | Gas Engine- Eugo senser wire damage, 3607/5, 3227/15, 3227/5 refitted the wire issue resolve | Closed | Kapil Solanki
49 | NORTH | 211560747 | 2025-02-01 15:22 | 125.4 | 4H.8042.C4../2420300 | BATTERY FAULTY | Task Start | NIRMAN E-STORE LLP | 54 | Battery defective, So New battery replace | Closed | Kapil Solanki
50 | NORTH | 211560693 | 2025-02-01 15:07 | 125.4 | 4H.8042.C4../2420737 | Oil Leakage Issue Call By Customer Name- kamlesh Rana Mo.No.- 9760647688 | Closed | MS CERAMICS. | 82 | Oil leakage from oil sump drain bolt from welding to drain side required to oil sump change | Closed | Sudhir Awasthi | Photo Required while replacing
51 | NORTH | 211560400 | 2025-02-01 14:08 | 5.5 | CC1.1013.../2400293 | LINE REJCETION | Closed | Power Link.. | LR-3.13 | Low fuel level & Earthing not proper because customer side working so customer change the location, tell the customer please when change the location Earthing connection done _ CC done to our side | Closed | Gourav Sharma | Details required
1 | East | 211568836 | 2025-04-01 13:18 | 20 | GP3.8601.../2420369 | Starting Issue. Call By Customer Name :-Anil kumar Mobile No :- 8083454471 | Task Start | Anil Kumar | 209 | Emergency stop switch was pressed after releasing it issue resolved also educated operator working of emergency Switch. | CLOSED | Prabhakar Kumar
2 | East | 211568469 | 2025-04-01 12:15 | 20 | GP3.8601.../2421241 | Starting issue Call By service Dealer Name - Yashika Number - 9693063331 | Task Start | Raunaq T. V. S. | 16.2 | DG was not starting on closing the panel door on opening it was running so on inspection found Controller on/off switch 2A1 wire found loose after tightening issue resolved | OPEN | Subhrajit Roy
3 | East | 211564573 | 2025-03-01 14:47 | 20 | GP3.8601.../2421674 | Maintenance Due Alarm Call By Customer Name :- Prashant Nayak Mobile No :- 8413058511 | Cancelled | M/S Dhar Constructions... | 209 | resolved on telephonic coummunication so cancelled SR | CANCELLED | Subhrajit Roy
4 | East | 211564435 | 2025-03-01 14:27 | 125.4 | 4H.8041.../2420715 | Starting Issue Call by Customer Name : Vikram .. No : 9079902118 | Task Start | GANPATI BHARAT PVT LTD |  | update pending | OPEN | Subhrajit Roy
5 | East | 211560578 | 2025-02-01 14:33 | 20 | GP3.8601.../2420650 | Starting/Stopping Issue | Task Start | STATE BANK OF INDIA | 78 | SE checked for any alarm so found Sweep stuck alarm so disconnected FIP connector checked for continuity found ok the open Allen bolt and checked for smooth movement of Sweep found ok then tighten allen bolt and connecting connector properly after cleaning then Crank DG start normally and also Started DG 3-4 time for trail found ok . | CLOSED | Subhrajit Roy
6 | East | 211559779 | 2025-02-01 11:42 | 125.4 | 4H.8041.../2420334 | Mobil Oil Leakage Call by Customer Name : Prem Kumar No : 7033285136 | Task Start | M/s. Om Hosiery | 70 | Lube oil leakage was from the Oil sump welded drain plug nut. Lube oil Sump under EDO | OPEN | Prabhakar Kumar
7 | East | 211545217 | 31-12-2024 12:12 | 15 | GP3.8501.../2421125 | Shut Down Alarm Issue Call By Customer Name :- Pramod .. Mobile No :-9934351151 | Open | NUCOMB ENGINEERING PRIVATE LIMITED | 4 | DG does not start few time showing Emergency Alarm so tighten all negative connection in panel as well as tighten the 3 pin connector then started for 5 - 6 for trail DG Start normally. | OPEN | Subhrajit Roy
8 | East |  |  | 20 | GP3.8604../2420083 | lube oil dilution | Task Start | RELIANCE JIO INFOCOMM LIMITED | 2 | As per complaint SE checked the lube oil by dipstick and drain it found coolant mixed with lube oil Under observation, Today SE will visit site | OPEN | Prabhakar Kumar
1 | West | 211559948 | 2025-02-01 12:22 | 160 | 6H.8475.../2420136 | Tripping issue & Heating issue Call By Customer Name :- Sitesh Mobile No :- 9420143113 | Task Start | Padam Kapada Bazar | 202 | Low DEF level. | CLOSED | Jagdeep Saini
2 | West | 211559134 | 2025-02-01 10:45 | 320 | F6.8802.../2420100 | Voltage Fluctuation | Open | Diam Display India Private Limited | 184 | Automation problem. Genset breaker opened and closed automatically for 15 seconds. | CLOSED | Jagdeep Saini
3 | West | 211554098 | 2025-01-01 14:04 | 25 | GP3.8702.../2421910 | oil leakage | Task Start | KALA GENSET PVT LTD | LR | Allen bolt was tightened by applying Teflon and sealant to prevent oil leakage from the main oil gallery. | CLOSED | Jagdeep Saini
4 | West | 211554052 | 2025-01-01 14:00 | 15 | GP3.8501.../2421970 | oil leakage | Task Start | KALA GENSET PVT LTD | LR | Allen bolt was tightened by applying Teflon and sealant to prevent oil leakage from the main oil gallery. | CLOSED | Jagdeep Saini
5 | West | 211554047 | 2025-01-01 13:55 | 15 | GP3.8501.../2421876 | Oil leakage | Task Start | KALA GENSET PVT LTD | LR | Allen bolt was tightened by applying Teflon and sealant to prevent oil leakage from the main oil gallery. | CLOSED | Jagdeep Saini
6 | West | 211554043 | 2025-01-01 13:50 | 15 | GP3.8501.../2421965 | Oil leakage | Task Start | KALA GENSET PVT LTD | LR | Allen bolt was tightened by applying Teflon and sealant to prevent oil leakage from the main oil gallery. | CLOSED | Jagdeep Saini
7 | West | 211553750 | 2025-01-01 12:27 | 15 | GP3.8501.../2421930 | OIL LEAKAGE | Task Start | KALA GENSET PVT LTD | LR | Oil leakage from oil seal so need to be replace. | CLOSED | Jagdeep Saini
8 | West | 211560654 | 2025-02-01 14:46 | 40 | 3H.8951.../2421614 | LINE REJECTION | Task Start | Perennial Technologies Pvt. Ltd | 2 | EGR VALVE malfunction. Checked the wiring continuity & Voltage found OK but problem was persist same. SO ECU calibrated with dummy file. | CLOSED | Jagdeep Saini
9 | West | 211560069 | 2025-02-01 12:59 | 125.4 | 4H.8041.../2420771 | Starting/Stopping Issue | Task Start | Deepak Industries. | 59 | SPN/FMI-3031/14, Calibrated the ECU. | CLOSED | Jagdeep Saini
10 | West | 211553858 | 2025-01-01 13:06 | 58.5 | T4.8941.../2422413 | Electrical Problems | Closed | Chandrashobha Generator | 291 | Charging alternator fuse faulty. | CLOSED | Jagdeep Saini
11 | West | 211553553 | 2025-01-01 11:21 | 82.5 | 5H.8901.../2420168 | Amber Lamp Alarm Issue Tripping Issue Call By Customer Name :- Vinod .. Mobile No :-8824847009 | Closed | Germinal Technologies P. Ltd. |  | Low DEF level. | CLOSED | Jagdeep Saini
12 | West | 211559141 | 2025-02-01 10:48 | 160 | 6H.8475.../2420267 | Leakage Issue | Task Start | Hotel Bharat | 61 | Air was present in the fuel line; therefore, the air was removed. | CLOSED | Jagdeep Saini
13 | West | 211554051 |  | 25 | GP3.8702/2420583 | CC SR | Closed | Royal Electronics. |  | WIF Sensor one of the Pin bent due to which Error Code SPN/FMI-97/5. Wiring Harness Female Connector Rubber O ring and Lock missing | CLOSED | Amit Shandilya | Goem Issue
14 | West | 211559014 | 2025-02-01 10:19 | 160 | 6H.8475.../2420118 | Red Lamp On Alarm Issue Call By Customer Name :- 9623196273 Mobile No :- Mahadev .. | Task Start | Lifeline Mauli Hospital LLP. | 155 | SPN/FMI- 5461/8, Calibrated the ECU with Dummy file. | Closed | Jagdeep Saini
1 | South | 211541275 | 30-12-2024 13:17 | 20 | GP3.8601.../2420765 | Door problem Call by : Customer Name :Joel Contact :9645327104 | Task Start | Amala Cancer Hospital Society | 20 | The door is not open on the controller side properly . Removed the door lock and fixed it back | closed | Mr. Sanjaimon S
2 | South | 211541031 | 30-12-2024 12:36 | 40 | 3H.8951.../2420740 | Starting/Stopping Issue | Task Start | M/s. Mayura Bakery | 99 | Single pole MCB 2B3 lug pin out, connected the Same. Engine running ok | closed | Mr. Anil Kumar H G
3 | South | 211540702 | 30-12-2024 11:44 | 125.4 | 4H.8041.../2420779 | Oil Leakage Problem Call by : Customer Name : Suresh Contact :9585077111 | Completed | Trichy Padalur Tollways Pvt. Ltd. | 81 | Oil Sump change | closed | Mr. NandhaGopal
4 | South | 211540486 | 30-12-2024 11:11 | 125.4 | 4H.8042.C4../2420604 | Voltage Fluctuation | Task Start | Nandalala Auditorium. | 6 | Customer side load issue | closed | Mr. Sanjaimon S
5 | South | 211540323 | 30-12-2024 10:39 | 125.4 | 4H.8042.C4../2420612 | Electrical Problems | Task Start | Radon imaging & Diagnostics | 3 | Checked dg condition controller wiring harness loose contact (EB senscing wire) so R phase voltage dropped in controller so wiring harness tighted. | closed | Mr. MD Saleem
6 | South | 211540162 | 30-12-2024 10:08 | 125.4 | 4H.8041.../2420481 | Sound/Vibration Issue | Completed | Aarthi Scans Private Limited | 46 | update pending | Completed | Mr. MD Saleem
7 | South | 211540045 | 30-12-2024 09:34 | 30 | 3H.8902.../2320026 | Starting issue Call by customer Name: Jayanth Balakrishnan Number: 9840054720 | Completed | Jayanth Balakrishnan | 106 | Alarm showing on EGR valve Jammed so Remove the EGR valve and cleaned after that Refitted same and Connect the I Konnect Tool Cleared the DTC | closed | Mr. NandhaGopal | Load Pattern check
8 | South | 211540061 | 30-12-2024 09:33 | 25 | GP3.8702.../2421357 | wire smoke | Task Start | ATC Telecom Infrastructure Private Limited | LR | we found that the control panel was burnt due to a wire making contact with the channel strip mounted bolt. When the Service Engineer (SE) connected the battery terminal, sparking occurred. Assuming wire is cut and touched with bolt. Upon further investigation, we checked the controller, MCB, and relay boards, which were found to be in working condition. | Task Start | Mr. Anil Kumar H G
9 | South | 211540006 | 30-12-2024 09:12 | 82.5 | 5H.8901.../2420198 | Starting Problem Call by : Customer Name : Durgesh Shivangi Contact : 9945463249 | Task Start | Basaveshwar Engg College | 9 | Airlock issue in diesel filter (banjo bolt loose) | closed | Mr. Anil Kumar H G
10 | South | 211539972 | 30-12-2024 08:55 | 125.4 | 4H.8042.C4../2420012 | Red lamp Alaram problem Call by : Customer Name : Prathap reddy Contact : 9063433386 | Task Start | Gaddampalli Rajender Reddy. | 533 | Adblue low, top up the adblue | closed | Mr. MD Saleem
11 | South | 211539077 | 29-12-2024 18:33 | 20 | GP3.8601.../2421527 | Over Load Issue and Tripping Issue. Call By Customer. Name:- shijil ... Mobile No.:- 9739672202 | Task Start | Mayura Bakery & sweets | 17.52 | Customer end issue. Customer using overload so educate customer also mention in report. | closed | Mr. Anil Kumar H G
12 | South | 211538787 | 29-12-2024 17:32 | 125.4 | 4H.8041.../2420708 | starting issue Call by : Customer Name :SHANKAR Contact :9047016599 | Completed | GMS ELEGANT BUILDERS (I) PVT LTD | 975 | 520528/31,4095/1,1761/16,3031/14,516166/0. adblue low, top-up the adblue and clear the DTC, fault appear again, then flash the ECU. Issue resolved | closed | Mr. NandhaGopal
13 | South | 211547618 | 31-12-2024 17:28 | 0 | T4.5201.../2300002 | Starting/Stopping Issue | Task Start | AJAX ENGINEERING PRIVATE LIMITED | NA | Cancelled | Cancelled | Mr. Anil Kumar H G
14 | South | 211547222 | 31-12-2024 16:29 | 0 | 3H.8902.../2421864 | WATER ENTRY IN CONTROLLER WHILE TRANSIENT | Closed | SUNBEAM GENERATORS PVT LTD | LR | Checked the control unit and found water enter through the control unit. Replaced the New unit with program. Started the set and tested with load found ok | closed | Mr. NandhaGopal
15 | South | 211546296 | 31-12-2024 14:45 | 25 | GP3.8702.../2420236 | Starting Problem Call by : Customer Name : Mr. Balakrishna Contact :9980440510 | Closed | Mr. Balakrishna | 12 | Check the Battery cable Disconnect corrected the battery Cable Started the dg with load working found ok oil service due inform the customer | closed | Mr. Anil Kumar H G
16 | South | 211546171 | 31-12-2024 14:06 | 58.5 | T4.8941.../2422504 | WATER IN FUEL SENSOR FAILURE ERROR CODE | Closed | SUNBEAM GENERATORS PVT LTD | LR | Visited the site and noticed that the problem due to main fuel filter sensor. Removed the main fuel filter assembly and replaced new one with sensor. Started the set and tested with load found the problem we&apos;re solved. | closed | Mr. NandhaGopal
17 | South | 211546150 | 31-12-2024 14:04 | 0 | GP3.8501.../2421974 | ABNORMAL NOISE | Task Start | SUNBEAM GENERATORS PVT LTD | LR | Inspected the set and noticed that the abnormal sound from Alternator inside. To be checked the Alternator. | Task Start | Mr. NandhaGopal
18 | South | 211545680 | 31-12-2024 12:54 | 160 | 6H.8475.../2420380 | Coolant oil leakage and engine oil leakage from oil drain plug side | Closed | Magtorq Private Limited. | 3 | checked found coolant water leakage from radiator bottom hose connection so fixed the problem then engine oil leakage from engine oil drain connection so fixed the problem then diesel float level sensor is working not properly so changed the direction of float level sensor then it&apos;s was working properly the started the engine no engine oil leakage,no coolant water leakage and diesel float working good condition | closed | Mr. NandhaGopal
19 | South | 211545578 | 31-12-2024 12:34 | 125.4 | 4H.8042.C4../2420604 | Abnormal Sound Issue Email by Customer Name - Poduval | Closed | Nandalala Auditorium. | 14 | visited the site check the engine then start engine 30 minutes check any abnormal sound and smoke not found anything unusual, smoke is normal, also sound checked , and everything is in our limit | closed | Mr. Sanjaimon S
20 | South | 211545292 | 31-12-2024 12:27 | 125.4 | 4H.8041.../2420716 | Starting/Stopping Issue | Closed | M/s. Sri Sri Ravishankar Vidya Mandir. | 1.5 | visited the site automation issue due to customer mains sensing cable connected to load side.error 520528/31 | closed | Mr. Anil Kumar H G
21 | South | 211545254 | 31-12-2024 12:23 | 40 | 3H.8951.../2421561 | Starting Problem Call by : Customer Name :Manjula Contact :9880206517 | Closed | Antioch educational trust | 0.52 | visited the site and checked the engine as per the customer complaint observed engine not starting in automode due to sensing control cable not connected in eb panel,then connect the cables & started the engine found running condition is normal.... | closed | Mr. Anil Kumar H G
22 | South | 211545193 | 31-12-2024 12:12 | 20 | GP3.8601.../2420259 | red lamp alarm problem AND speed censer broken Call by : Customer Name :Mr. C P Uthappa Contact :9008904468 | Closed | SRI OM SHANTHI CARITABLE TRUST | 185 | Emergency switch active. So no nc switch removed and refitted after started running ok. | closed | Mr. Anil Kumar H G
23 | South | 211545133 | 31-12-2024 12:01 | 58.5 | T4.8941.../2420472 | Door Lock Issue Call By Customer Name :- Rajesh Mobile No :- 9448681821 | Closed | Rajesh | 17 | DG door alignment was problem so removed door hinges and corrected it and check the door fitted found ok so started the DG set with load condition is satisfactory | closed | Mr. Anil Kumar H G
24 | South | 211545130 | 31-12-2024 12:01 | 125.4 | 4H.8042.C4../2420859 | Battery Problem Call by : Customer Name :Radha Contact :9600866830 | Task Start | ESSEN ASSOCIATES BAY | 2 | Need to be charged the battery and already adviced to be customer need to be connected the battery charger line. Recharged battery now running ok. | closed | Mr. NandhaGopal
25 | South | 211545034 | 31-12-2024 11:44 | 125.4 | 4H.8042.C4../2420214 | Electrical Problems | Task Start | P. K. Enterprises | 40 | DG not starting due to air lock in diesel lines. suspected air entering to diesel suction unit. hence need to check diesel suction pipe unit with another one. Tommorow engineer visit side and check. | Task Start | Mr. Sanjaimon S | Under obs and parts arranged
26 | South | 211544950 | 31-12-2024 11:30 | 320 | F6.8802.../2420093 | starting issue Call by : Customer Name :Balaji Contact :9791786830 | Closed | Balmer Lawrie & C/o. Ltd. | 17.1 | Attend the site check the dg, dg output problem due to alternator avr fuse is blown so replaced the fuse and start the dg and give the load trail output ok dg running condition is ok all parameters ok no leakages. (photo not taken) | closed | Mr. MD Saleem
27 | South | 211544902 | 31-12-2024 11:18 | 15 | GP3.8501.../2420650 | Starting Issue Call By Customer Name - Vinayak .. Mobile No -7019027872 | Closed | KARTHIK 3D WHEEL ALIGNMENT AND TYRE PARK | 17 | Emergency switch wire loose (H1 wire) | closed | Mr. Anil Kumar H G
28 | South | 211544849 | 31-12-2024 11:07 | 15 | GP3.8501.../2420576 | Voltage problem Call by : Customer Name :Srinivas rao Contact : 9440607864 | Closed | Gayatri Agro Service | 43 | R-phase fuse blown, replace the fuse | closed | Mr. MD Saleem
29 | South | 211544842 | 31-12-2024 11:07 | 15 | GP3.8501.../2420608 | control switch box changing Call by : Customer Name :Vishwa Contact :8861756364 | Cancelled | Swarnanjali Jewels | NA | Cancelled | Cancelled | Mr. NandhaGopal
30 | South | 211544757 | 31-12-2024 10:44 | 58.5 | T4.8941.../2420219 | Smoke issue Call By Customer Name :- Muruganpandian sir . Mobile No :-7066652739 | Closed | Oil and Natural Gas Corporation Limited Tamil Nadu | 351 | Inspected the site and noticed black smoke in DG due to rain enter into the exhaust silencer by spark arrested fitted by customer in upward direction because of that water enter into the exhaust system so that black smoke raised educate the customer to correct the direction also this failure not come under warranty (Photo attached) | closed | Mr. Nandha Gopal
31 | South | 211544624 | 31-12-2024 10:35 | 40 | 3H.8951.../2420549 | Leakage Issue | Closed | P. Ramesh | 151 | Checked the dg found that dg coolant leakage due to Radiator hose pipe clamp loose so tight and fitment then started the dg running found ok (Photo attached) | closed | Mr. MD Saleem
32 | South | 211544603 | 31-12-2024 10:28 | 30 | 3H.8902.../2421321 | KRM Problem Call by : Customer Name :Ratheesh Kumar Contact :7736717151 | Closed | Bhaskar associates | 47 | attend the site and examine the engine with the of customer representative. complain about krm wrong updation,already checked the krm on last day at the time of wet service,but now again same issue repeated,so waiting for koel HO decision,and customer not satified with our product and service due to repeated complaints,also customer not willing for sighn the report | closed | Mr. Sanjaimon S | KRM check run hr
33 | South | 211544339 | 31-12-2024 08:53 | 250 | F6.8841.../2420239 | Error Code Issue Email By KGD Name:-Kadiravan . | Closed | S. Y. S. Construction | 135 | Adblue low, top up the adblue customer using different adblue (TATA-adblue) | closed | Mr. Anil Kumar H G
34 | South | 211544313 | 31-12-2024 08:35 | 58.5 | T4.8941.../2421908 | Starting Problem Call by : Customer Name : Babavani Contact : 9959715131 | Task Start | Prakash Eye Hospital | 36.2 | fuel air lock issue and common line issue error code SPN157 FIM 14P0089 Pres Relief Vlv Falut- Open | closed | Mr. NandhaGopal
35 | South | 211543381 | 30-12-2024 18:37 | 82.5 | 5H.8901.../2420439 | Electrical Problems | Closed | Style Park | 19.5 | 516166/0 ECU fault indication in control so checked all wire connection, connected I Konnect tool flashed the ECU and eliminated the error code. | closed | Mr. Anil Kumar H G
36 | South | 211543239 | 30-12-2024 18:04 | 125.4 | 4H.8041.../2420654 | Starting/Stopping Issue | Closed | Sai Soham Infra. | 100 | visit the site observe the DG error is SPN 520528 FMI 31 And SPN 1761 AND FMI 14 then top-up the adblue and the tool was not connected then check the Can ohms value is 0 and then check the wiring found ok, and then remove the connector and check the pin was bend and then reconnect the took and clear the error code and then start the DG running is good. (Photo attached) | closed | Mr. Anil Kumar H G | Panel name required
37 | South | 211543197 | 30-12-2024 17:58 | 15 | GP3.8501.../2420538 | Genset Trip | Closed | Hotel Kottaram | 19 | Attended the site and examined the engine with the presence of customer representative, confirmed that DG not starting due to fuse failure 2A(1). then replaced the fuse (Photo attached) | closed | Mr. Sanjaimon S
38 | South | 211543040 | 30-12-2024 17:29 | 320 | F6.8802.../2420123 | Alarm problem Call by : Customer Name : Manikanth Contact : 8142584335 | Closed | Maangalya Shopping Mall. | 29 | Emergency switch wire loose (H1 wire) | closed | Mr. MD Saleem
39 | South | 211553879 | 2025-01-01 13:18 | 40 | 3H.8951.../2420575 | Leakage Issue | Task Start | United Intigration | 84.57 | Coolant leakage from oil cooler. oil cooler o ring damaged replace the o ring and fitted properly (photo & video attached) | closed | Mr. Anil Kumar H G
40 | South | 211562804 | 2025-03-01 07:30 | 0 | 5H.5353.C1../2300001 | ERROR CODE ISSUE | Task Start | SCHWING STETTER (INDIA) PVT LTD | NA | Cancelled | Cancelled | Mr. NandhaGopal
41 | South | 211561963 | 2025-02-01 18:23 | 58.5 | T4.8941.../2421623 | DG Not Switching On - Protect Lamp ON & Crank Sensor Signal Faulty Error | Open | Bharti Airtel ANG | 24 | 637/2 ERROR CODE. ENGINE NOT STARTING DUE TO CRANK SENSOR FAULT SIGNAL ERROR, CHECK THE CONNECTOR, REMOVED & FITTED THE WIRING CONNECTOR. TIGHTENED PROPERLY. CONNECTED THE I KONNECT TOOLS & CLEAR THE ERROR CODE | closed | Mr. NandhaGopal
42 | South | 211561953 | 2025-02-01 18:15 | 58.5 | T4.8941.../2420551 | Starting Issue Email By KGD Name:-T. Durga Prasad, | Task Start | Azes Enterprises. | 15 | auto starting problem then found the outside amf panel problem. | closed | Mr. MD Saleem
43 | South | 211561211 | 2025-02-01 16:20 | 5.5 | CC1.1013.../2400361 | Starting Problem Call by : Customer Name : shanmukh Contact : 7013927659 | Closed | JAYARAM MITTAI | 1 | attend the site start the engine observed battery is discharged check the wiring charger connection is disconnected reconnect the wiring battery is boosting mode. explain the customer | closed | Mr. MD Saleem
44 | South | 211560877 | 2025-02-01 15:36 | 20 | GP3.8601.../2420361 | Starting/Stopping Issue | Closed | M. V. K. Infra Equipments. | 38.19 | single pole MCB output wire (2) loose wire | closed | Mr. MD Saleem
45 | South | 211560041 | 2025-02-01 12:41 | 125.4 | 4H.8042.C4../2420923 | Supply Problem Call by : Customer Name :Nadarajen Contact :8056292738 | Cancelled | Aristo Pharmaceuticals Pvt. Ltd. | NA | Cancelled | Cancelled | Mr. Nandha Gopal
46 | South | 211559901 | 2025-02-01 12:08 | 20 | GP3.8601.../2421028 | Red Lamp On Alarm Issue Call By Customer Name :- Abhirup Chatterjee Mobile No :-9110151322 | Closed | Thomas Chacko. | 36.57 | LOP sensor fault codes and redlamp on display LOP sensor switch wire G3 is disconnected and re-fitted the wire to sensor lug | closed | Mr. Anil Kumar H G
47 | South | 211569018 | 2025-04-01 13:37 | 25 | GP3.8702.../2421156 | Alarm problem Call by : Customer Name :Ragothaman Contact :9791007769 | Open | S. S. Logistics. | 8 | 2791/18, 2791/6 Error code. Checked the EGR connection found ok. Then flash the dummy file | closed | Mr. NandhaGopal
48 | South | 211565165 | 2025-03-01 16:46 | 160 | 6H.8475.../2420364 | V belt cut | Closed | Bhima Jewellery Rajapalayam | 379 | V-belt broken also found eye-bolt broken, so replace the v-belt and eyebolt, photo not taken failed part send to HO. | closed | Mr. Nandha Gopal | Service history
49 | South | 211564153 | 2025-03-01 13:15 | 58.5 | T4.8941.../2421088 | Error code issue Call by : Customer Name :Saravanan Contact :9578889429 | Closed | S.B.O.A.SCHOOL(CBSE), MADURAI | 25 | Engine not started, check and found main relay faulty replace the same | closed | Mr. NandhaGopal
50 | South | 211563360 | 2025-03-01 10:44 | 58.5 | T4.8941.../2423081 | Starting/Stopping Issue | Task Start | Acecret Adhesions India Private Limited | 146 | engine not starting due to low battery voltage so customer charged the battery and refitted also found that 2B/4 wire is loose | closed | Mr. Anil Kumar H G
51 | South | 211563296 | 2025-03-01 10:33 | 125.4 | 4H.8041.../2420970 | Oil Leakage Issue Call By Â Service Dealer Name :- Dadasir Mobile No :- 6360576099 | Task Start | Malwa Infracon Pvt. Ltd. | 236 | Oil leakage from flywheel side (photos Attached) | closed | Mr. Anil Kumar H G | Check points at the time of rework
52 | South | 211563170 | 2025-03-01 10:25 | 160 | 6H.8475.../2420046 | Starting Issue Email by GOEM Name - Sivagami S, | Task Start | Maharishi Vidya Mandir. | 20.47 | 1761/16 ,516166/0 Adblue level low, educate the customer to maintain the adblue level | closed | Mr. NandhaGopal
53 | South | 211562937 | 2025-03-01 10:06 | 125.4 | 4H.8042.C4../2420875 | Starting/Stopping Issue | Closed | Venturemark Consultants LLP | 358 | check the engine found 3031/14 error code on display then clear the error code and flash the ECU and start the engine working found normal | closed | Mr. Sanjaimon S
54 | South | 211569041 | 2025-04-01 16:06 | 40 | 3H.8902.../2421885 | CC | Closed | ANANTHA JOTHI JAVULI STORE | CC | Circuit open alarm, check and found that wire wrong fitted (ferule no. 25 fitted in pin no. 18), corrected the wire. | closed | Mr. NandhaGopal | Issue of sun beam
1 | NORTH | 211573487 | 2025-06-01 13:13 | 320 | F6.8802.../2420073 | Door Lock, Coolant Leakage & Coolant Lid Call By Customer Name :- Rishi Pal Mobile No :- 7838955880 | Task Start | A.G. Pipes Pvt. LTD. | 180 | coolant leakage from Engine Radiator hose pipe themostate to Radiator hose pipe clamp proper tight and Engine Canopy door lock hinges alignment out Engine Canopy door lock hinges change required Recovey bottle coolant tank cap missing | Closed | Kapil Solanki
2 | NORTH | 211573485 | 2025-06-01 13:12 | 30 | 3H.8902.../2420013 | Red Lamp Alarm Issue Email by Customer Name - Manuj Jain | Closed | Arihant Machinery Store | 27 | Emergency switch button was pressed realease the same issue resolve | Closed | Kapil Solanki
3 | NORTH | 211573303 | 2025-06-01 12:41 | 500 | DV8.8501.C4../2420058 | Canopy Stop Alarm Call By Customer Name :- Rohit Kumar Mobile No :-9920868795 | Task Start | Regal Emporia Infratech Pvt. Ltd. | 74 | check the interface relay box- (30 ampere fuse brant) and bypass the fuse and proper fitted and check the dg manual start on running condition is ok (30 AMP fuse to the change) | Closed | Kapil Solanki
4 | NORTH | 211573275 | 2025-06-01 12:38 | 125.4 | 4H.8041.../2420869 | Electrical Problems | Task Start | Jasco Handicrafts Pvt. Ltd. | 15.37 | Customer raise the complaint for Automation | Closed | Kapil Solanki
5 | NORTH | 211573066 | 2025-06-01 12:05 | 30 | 3H.8902.../2320159 | Starting/Stopping Issue | Closed | Ankur Kaushik | 228 | Customer side panel issue | Closed | Kapil Solanki
6 | NORTH | 211572458 | 2025-06-01 10:39 | 20 | GP3.1021.../2420471 | lfl alarm generat | Open | Reliance Jio Infocomm Limited | 62 | fuel level sensor checked problem 9 no wire tight in controller | Closed | Sudhir Awasthi
7 | NORTH | 211572429 | 2025-06-01 10:31 | 125.4 | 4H.8041.../2420951 | High At Blew Temperature Alarm Call By Customer Name :- Vinod Kumar Mobile No :- 9560436800 | Completed | Navnit Blister Packs Private Limited | 72 | SPN/FMI 4095/1, 1761/16, 520528/31, 3031/14 reset the alarm | Closed | Kapil Solanki
8 | NORTH | 211572427 | 2025-06-01 10:30 | 125.4 | 4H.8041.../2320134 | Error code Issue Call By Customer Name :- Kashif Ahmad Mobile No :-8445820675 | Closed | M/S SWASTIK PESTICIDES LIMITED | 1425.2 | SPN/FMI 51/0 engine throttle valve connector wire remove clean and refitted trial 20 to 30 min. no issue found | Closed | Sudhir Awasthi
9 | NORTH | 211572340 | 2025-06-01 09:58 | 15 | GP3.8501.../2320035 | Starting/Stopping Issue | Closed | N.K Generator Service | 77 | Controller ON/OFF selector switch wire was loose tightness the same issue resolve | Closed | Kapil Solanki
10 | NORTH | 211572333 | 2025-06-01 09:53 | 20 | GP3.8601.../2420284 | Genset Trip | Closed | Universal Metal Industries | 60 | DG trip due to overload, Suggest to customer kindly Dg run the under load | Closed | Kapil Solanki
11 | NORTH | 211572293 | 2025-06-01 09:34 | 500 | DV8.8501.C4../2320030 | Coolant leakage issue Call By Customer Name - Virendra Kumar Mobile No -7633873576 | Closed | Sobha Ltd. | 2254 | Coolant Overflow from recovery bottle, No leakage found any side in Engine | Closed | Kapil Solanki | KRM data
12 | NORTH | 211571472 | 2025-05-01 15:51 | 125.4 | 4H.8041.../2420635 | About urea level | Task Start | Suja Metals | 48 | SPN/FMI 51/0 , 516166/0 Today visit with I-konnect tool | Closed | Sudhir Awasthi
13 | NORTH | 211571464 | 2025-05-01 15:14 | 160 | 6H.8475.../2420206 | Cranking issue Call By Customer Name :- Devendr .. Mobile No :- 9897437406 | Closed |  | 81 | Low Def level alarm, but found 56% & starting time white smoke after flash the file issue resolve | Closed | Sudhir Awasthi | Service history/ KRM Check
14 | NORTH | 211571435 | 2025-05-01 14:25 | 82.5 | 5H.8901.../2420444 | Power Supply Issue Call By Customer Name :- Astoni . . Mobile No :- 6392632270 | Open | Nagar Palika Parishad Hardoi. |  | Cancelled-Problem solve without visit | Cancelled | Sudhir Awasthi
15 | NORTH | 211571396 | 2025-05-01 13:37 | 82.5 | 5H.8901.../2320021 | Starting issue Call By Customer Name :-Aprana Mobile No :-9811028157 | Closed | CRMK Select | 209 | found DG set tripping After some time oil pressure flt Alarm show spn 100 FMI 3 then reset the alarm after trial on load 30min. Found no issue | OPEN | Kapil Solanki | Under obs KRM data check
16 | NORTH | 211571391 | 2025-05-01 13:00 | 57 | T4.8941.../2320093 | Sarting Issue Call By Customer Name :- Rishav Gupta Mobile No :- 9810539132 | Task Start | ROHIN STEEL INDUSTRIES | 137 | Water seprator air leakage open the filter then found o ring mold & filter loose tightness the same- Service due B check | Closed | Kapil Solanki
17 | NORTH | 211571380 | 2025-05-01 12:33 | 625 | DV0.8501.C4../2420015 | Urea tank issue Call By Customer Name :- Ajay Kumar Sharma Mobile No :- 7869012055 | Cancelled | Irish Infrastructure Pvt. Ltd. |  | Under Cancellation- | Cancelled | Kapil Solanki
18 | NORTH | 211571367 | 2025-05-01 12:20 | 58.5 | T4.8941.../2420673 | Radiator issue Call by customer Name: Ashish Kumar Number: 9810638372 | Cancelled | MSA DEVELOPERS PRIVATE LIMITED |  | Under Cancellation- | Cancelled | Kapil Solanki
19 | NORTH | 211571310 | 2025-05-01 11:43 | 125.4 | 4H.8041.../2420985 | Coolant Leakage Issue Call By Customer Name :- Manoj Kumar Mobile No :- 9871464889 | Task Close | SILICONE TECH. | 56 | Found water droplets from CAC & throttle valve jammed alarm Open the throttle valve found moisture in ITV after clean the ITV and again refitted | Closed | Kapil Solanki | under obs
20 | NORTH | 211571321 | 2025-05-01 11:05 | 82.5 | 5H.8901.../2420144 | Amber lamp alarm Issue Call By Customer Name :-Chandan Mobile No :-9728022147 | Closed | Germinal Technologies Pvt. Ltd. | 138 | Def level low, top up the def issue resolve | Closed | Kapil Solanki
21 | NORTH | 211571270 | 2025-05-01 10:26 | 25 | GP3.8702.../2420626 | Oil Leakage Issue Call By Customer Name :- Ajay Vishwakarma Mobile No :- 8736915911 | Cancelled | Pushpa Associates |  | Under Cancellation- Problem solve in PM visit | Cancelled | Sudhir Awasthi
22 | NORTH | 211571266 | 2025-05-01 10:09 | 750 | DV2.8501.C4../2420112 | Load issue Call by customer Name: Kumar Number: 9911513913 | Task Start | Capital Developers | 3 | Voltage sensing wire disconnected from alternator, Connected the same issue resolve | Closed | Kapil Solanki
23 | NORTH | 211571278 | 2025-05-01 08:53 | 20 | GP3.8601.../2420492 | Amber Lamp Alarm Issue Call By Customer Name :- Gaurav Kumar Mobile No :- 9971176886 | Task Start | Kamal Machinery Stores. | 1000 | Reset the alarm Egr related fault code | Closed | Sudhir Awasthi
24 | NORTH | 211570840 | 2025-04-01 18:52 | 58.5 | T4.8941.../2421411 | Abnormal Sound Issue Call By Customer Name - Vishal Number - 9897468454 | Closed | The Biscuit Centre | 88 | Ecu stand bolt loose, tightness the same issue resolve | Closed | Sudhir Awasthi
25 | NORTH | 211570729 | 2025-04-01 18:07 | 500 | DV8.8501.C4../2320065 | Starting/Stopping Issue | Closed | KW SECURITY AND SERVICES PRIVATE LIMITED | 308 | found alarm show SPN 92 FMI 2 and water separator filter open and fuel drain water mix in fuel and fuel tank check in water mix and water separator filter fitment and alarm clear and engine start testing check- Customer not allow for cleaning | OPEN | Kapil Solanki
26 | NORTH | 211570633 | 2025-04-01 17:39 | 125.4 | 4H.8041.../2420227 | Def level low | Closed | Dynamic Anodizer Aluminium Anodizing | 104 | Low def level topup the def, suggest to customer kindly always topup the def above 50% | Closed | Kapil Solanki
27 | NORTH | 211570473 | 2025-04-01 17:11 | 750 | DV2.8501.C4../2420149 | ECU Alarm Issue. Call By Customer. Name :-Atul ... Mobile No :-9661903409 | Closed | Infratech Solutions | 14 | Low def level, Educate customer always till above 50% def | Closed | Kapil Solanki
28 | NORTH | 211570469 | 2025-04-01 17:08 | 500 | DV8.8501.C4../2420056 | ECU Alarm Issue. Call By Customer. Name :-Atul ... Mobile No :-9661903409 | Closed | Infratech Solution | 23 | Low def level, Educate customer always till above 50% def | Closed | Kapil Solanki
29 | NORTH | 211570458 | 2025-04-01 17:07 | 125.4 | 4H.8041.../2420881 | Starting/Stopping Issue | Closed | Army Public School. | 59 | Low def level topup the def, clear the fault code issue resolve | Closed | Sudhir Awasthi
30 | NORTH | 211570190 | 2025-04-01 16:24 | 250 | F6.8841.../2420256 | Starting/Stopping Issue | Closed | Jaideep Rohatgi | 73 | Low def level, advised to the customer please maintain 50% above def level | Closed | Kapil Solanki
31 | NORTH | 211570148 | 2025-04-01 16:12 | 25 | GP3.8702.../2420626 | Genset Trip | Closed | Pushpa Associates | 286 | SPN/FMI 516166/0, 653/5, Injector 3 no. connector remove & clean after fitted again, Lub oil leakage from turbo oil drain pipe | Closed | Sudhir Awasthi
32 | NORTH | 211569956 | 2025-04-01 15:41 | 30 | 3H.8902.../2320040 | Starting/Stopping Issue | Closed | Kumar Generator House | 17.22 | Low electrolite level topup the electrolite charge the battery issue resolve | Closed | Kapil Solanki
33 | NORTH | 211569752 | 2025-04-01 15:19 | 160 | 6H.8475.../2420247 | Abnormal sound issue Call By Customer Name - Sukhdev Yadav Number - 8755175043 | Closed | V. Retail Ltd. | 64 | V-belt loose tightness the same issue resolve | Closed | Sudhir Awasthi
34 | NORTH | 211569735 | 2025-04-01 15:11 | 625 | DV0.8501.C4../2420017 | Starting/Stopping Issue | Closed | SUNGLOW WORKS LLP | 8 | fuse 30 ampr faulty and new change required temporary fuse short | Closed | Kapil Solanki
1 | East | 211573714 | 2025-06-01 13:59 | 30 | 3H.8902.../2420561 | Starting issue Call by customer Name: MAUSUMI DAS Number:7008552475 | Open | ABIS Exports India Private Limited. . | 2.26 | Today SE will visit Site | OPEN | Ujjwal Das
2 | East | 211573143 | 2025-06-01 12:19 | 15 | GP3.8501.../2420195 | Genset Trip | Task Start | BIRAJA CONSTRUCTION | 631 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das
3 | East | 211572886 | 2025-06-01 11:43 | 58.5 | T4.8941.../2421670 | Starting/Stopping Issue | Task Start | Kaluwala Construction Pvt. Ltd. | 1369 | DG was not starting showing under voltage alarm on checking found AVR fuse burnt so replaced the fuse restored the issue | CLOSED | Subhrajit Roy
4 | East | 211571504 | 2025-05-01 17:37 | 15 | GP3.8501.../2421358 | Starting Issue Email By KGD Name:-sunrise power | Task Start | CHANDAN KUMAR SAHNI | 32 | Customer,s complaint was DG shutdown showing under voltage alarm, so SE checked for DG on trail found 218-220 V so adjusted voltage 228-230 by AVR | CLOSED | Prabhakar Kumar
5 | East | 211571386 | 2025-05-01 12:50 | 35 | 3H.8902.../2420344 | Battery Charger Call by customer Neam =Manoj kumar . No=9973048731 | Closed | Safe Decor | 21 | Wrong battery charging connection was provided due which it discharged (+ve was provide on MCB 8F1 up output point, so when MCB is off battery does not charge) so interchange the MCB input and output point | CLOSED | Prabhakar Kumar
6 | East | 211571279 | 2025-05-01 08:55 | 25 | GP3.8702.../2421034 | Starting Issue Call By Customer Name :-Proshenjit Saha Mobile No :-7001964817 | Task Start | PROSANJIT SAHA | 77 | Low adblue level,SE will visit to educate the customer and filling up the adblue . | CLOSED | Prosanjit saha
7 | East | 211564435 | 2025-03-01 14:27 | 125.4 | 4H.8041.../2420715 | Starting Issue Call by Customer Name : Vikram .. No : 9079902118 | Task Start | GANPATI BHARAT PVT LTD | 268 | update pending | OPEN | Subhrajit Roy
8 | East |  |  | 20 | GP3.8604../2420083 | lube oil dilution | Task Start | RELIANCE JIO INFOCOMM LIMITED | 2 | As per complaint SE checked the lube oil by dipstick and drain it found coolant mixed with lube oil Under observation, found head torque ok 40-45 Nm and found oil cooler ok. | OPEN | Prabhakar Kumar
1 | NORTH | 211578383 | 2025-07-01 13:30 | 500 | DV8.8501.C4../2320060 | Trip_Genset_Low_Voltage | Task Start | LNM. Auto Industries Private Ltd.. | 610 | Battery charger 1 wire break so, not proper 230v come | Closed | Kapil Solanki
2 | NORTH | 211578223 | 2025-07-01 13:03 | 82.5 | 5H.8901.../2420022 | MIL lamp on | Task Start | C. L. ENTERPRISES | 116 | SPN/FMI 1761/16, 4375/4 Low def level, topup the def, Clear the fault code issue resolve | Closed | Ved Prakash Gupta
3 | NORTH | 211578272 | 2025-07-01 13:02 | 0 | 4H.8042.C4../2420987 | urea leakage | Task Start | IEC ELECTRIC POWER LIMITED |  | update pending | Open | Ved Prakash Gupta
4 | NORTH | 211578246 | 2025-07-01 13:01 | 58.5 | T4.8941.../2423222 | Tripping Issue Call By Customer Name :- Viram Mobile No :-9599163060 | Task Start | V.S ELECTRICALS & POWER SOLUTIONS | 272 | SPN/FMI 633/3 IMV remove the connector refitted again issue resolve | Closed | Kapil Solanki | ECU fault check
5 | NORTH | 211578141 | 2025-07-01 12:48 | 15 | GP3.8501.../2420007 | RELAY CARD FAULTY | Task Start | BHARTI AIRTEL LIMITED | 15 | Relay change due to burning issue | Closed | Kapil Solanki
6 | NORTH | 211578022 | 2025-07-01 12:23 | 160 | 6H.8475.../2420042 | Low Urea Issue Call By Customer Name :- Mohit Thakur Mobile No :-9250923316 | Task Start | Within | 37 | Low def level, Customer not known the how to open the Cap of DEF tank | Closed | Kapil Solanki
7 | NORTH | 211578012 | 2025-07-01 12:18 | 40 | 3H.8951.../2420338 | Power Supply Issue Call By Customer Name :- Ramakant Tiwari Mobile No :- 9873422640 | Closed | Bhojpuri Avadhi Sammaj | 18 | Control panel side MCB off condition, Opreator New | Closed | Kapil Solanki
8 | NORTH | 211578000 | 2025-07-01 12:15 | 250 | F6.8841.../2420359 | Ecm Alarm Issue Call By Customer Name :- JAI ARORA Mobile No :- 9999400425 | Task Start | ADHARSHILA POWER CORPORATION. | 57 | Low def level, topup the def, Clear the fault code | Closed | Kapil Solanki
9 | NORTH | 211577911 | 2025-07-01 11:58 | 320 | F6.8802.../2420060 | Emergency switch button faulty | Task Start | Rudra Construction | 279 | checked canopy emergency stop switch found not work properly so bypass done | Closed | Ved Prakash Gupta
10 | NORTH | 211577861 | 2025-07-01 11:54 | 125.4 | 4H.8041.../2420470 | Adblu level low | Completed | IJM. Motors Pvt. Ltd. | 92 | SPN/FMI-1761/16 ;Low AdBlue Level Alarm;Top-up the same & resolve the issue | Closed | Ved Prakash Gupta
11 | NORTH | 211577713 | 2025-07-01 11:19 | 30 | 3H.8902.../2320174 | Starting Issue Call By Customer Name :-Dr. Raghav . Mobile No :- 8968863127 | Closed | Mr. Raghav | 1.32 | DG not start- tightness the all wiring connection in panel, DG start ok issue resolve | Closed | Ved Prakash Gupta
12 | NORTH | 211577682 | 2025-07-01 11:16 | 500 | DV8.8501.C4../2420082 | Loading Issue And Automation Issue Call By Customer Name :- Narendra Varma Mobile No :-7891882818 | Task Start | RIYASAT INFRA DEVELOPERS PRIVATE LIMITED | 47 | Air lock in fuel line tightness the pump then remove the air issue resolve | Closed | Gourav Sharma
13 | NORTH | 211577630 | 2025-07-01 11:11 | 125.4 | 4H.8041.../2320065 | Oil leakage issue. Call By Customer Name - Devendar Sharma Mobile No -8950256020 | Task Start | Srihans Technologies Exports Pvt. Ltd. | 175 | Oil leakage from rocker cover O RING, O RING change then issue resolve | Closed | Kapil Solanki
14 | NORTH | 211577629 | 2025-07-01 11:11 | 62.5 | T4.8941.../2420028 | Starting/Stopping Issue | Task Start | Chadha Generators Private Limited | 917 | Controller display is not ON check the supply 1&2 point found 12v after replace the controller then, issue resolve | Closed | Ved Prakash Gupta | Service history
15 | NORTH | 211577555 | 2025-07-01 10:58 | 125.4 | 4H.8042.C4../2420858 | Starting Issue. Call By Customer. Name:- Anil Kumar Mobile No.:- 9891661870 | Task Start | Z-TECH INDIA LTD |  | Cancelled-Pm visit solve | Cancelled | Sudhir Awasthi
16 | NORTH | 211577506 | 2025-07-01 10:56 | 15 | GP3.8501.../2421657 | Automation Issue And OIl Leakage Issue Call By Customer Name- Surendra Singh Mo.No.- 8755138090 | Closed | Mr Surendra Singh | 10 | Customer side mains phase issue, change the phase issue resolve | Closed | Sudhir Awasthi
17 | NORTH | 211577542 | 2025-07-01 10:54 | 125.4 | 4H.8041.../2420905 | Starting/Stopping Issue | Completed | JEENA CRITICARE LOGISTICS PVT.LTD | 111 | Electric feed pump change because feed pump is not working properly | Closed | Kapil Solanki
18 | NORTH | 211577518 | 2025-07-01 10:49 | 15 | GP3.8501.../2420365 | RELAY CARD REPLACE | Task Start | BHARTI AIRTEL LIMITED | 3 | Relay change due to burning issue | Closed | Kapil Solanki
19 | NORTH | 211577425 | 2025-07-01 10:38 | 58.5 | T4.8941.../2421719 | Diesel Sensor issue Call By Customer Name :- Pravin Kumar Mobile No :- 9971188227 | Closed | WOW EQUIPMENT & INFRA PVT LTD | 138 | Fuel circuit open, checkl the sensor found wire was loose tightness the same issue resolve | Closed | Sudhir Awasthi
20 | NORTH | 211577283 | 2025-07-01 10:05 | 30 | 3H.8902.../2420621 | Bellow to be Change | Closed | MAPSAN ENGINEERING PRIVATE LIMITED | 606 | Bellow change because damage the bellow and alighnment not to be proper, so stress on the bellow | Closed | Kapil Solanki
21 | NORTH | 211577257 | 2025-07-01 09:52 | 400 | DV8.8542.C4../2320010 | Trip_Genset_Low_Voltage | Task Start | BPCL. Haryana | 222 | SPN/FMI 523584/15, 516166/0 & low def level in TANK 2 and R,B,Y connector wire loose tightness the same issue resolve | Closed | Ved Prakash Gupta
22 | NORTH | 211577245 | 2025-07-01 09:50 | 500 | DV8.8501.C4../2320075 | Starting Issue & Error issue call By Customer. name:-Amrish Kumar. Mobile No.:- 9319831265 | Task Start | C.E. INFO SYSTEMS LIMITED | 60 | Low fuel level, EDO place for coolant pipe | Closed | Kapil Solanki
23 | NORTH | 211577204 | 2025-07-01 09:23 | 250 | F6.8841.../2420017 | Urea Alarm And Black Smoke Issue Call By Customer Name :- Rajesh Singh Mobile No :-9459240988 | Task Start | Greenberry Hotels And Residency India Private Limited | 46 | Low def level topup the def issue resolve | Closed | Ved Prakash Gupta
24 | NORTH | 211577140 | 2025-07-01 07:26 | 500 | DV8.8501.C4../2320078 | Trip_Genset_Low_Voltage | Closed | C.E. INFO SYSTEMS LIMITED | 69 | Under speed, Under frequency, Under voltage flash the file issue resolve | Closed | Kapil Solanki
25 | NORTH | 211576206 | 2025-06-01 19:59 | 40 | 3H.8951.../2420072 | Low speed | Task Start | Pulse Heart Hospital | 56 | Low fuel level alarm check the fuel, fuel is not available then topup the fuel & educate customer about | Closed | Ved Prakash Gupta
26 | NORTH | 211576164 | 2025-06-01 18:59 | 625 | DV0.8501.C4../2320026 | Fuse need to change | Task Start | Perigee Infratech Private Limited |  | Cancelled-Complaint on wrong ESN | Cancelled | Kapil Solanki
27 | NORTH | 211576112 | 2025-06-01 18:14 | 20 | GP3.8601.../2420827 | Black Smoke Issue & Preventive Maintenance Call By Customer Name :- Shubham Binwal Mobile No :- 7701979887 | Task Start | JB HOTEL AND RESORT | 28 | Cancelled-problem solve in tele discususion | Cancelled | Sudhir Awasthi
28 | NORTH | 211574937 | 2025-06-01 17:07 | 30 | 3H.8902.../2420974 | DG not working | Task Start | ICICI Bank Limited | 121 | SR open by mistake | Cancelled | Sudhir Awasthi
29 | NORTH | 211574122 | 2025-06-01 15:36 | 40 | 3H.9901.../2300003 | Starting/Stopping Issue | Closed | Kirloskar regional training center | 9 | Battery discharge, after remove the battery charge the battery for 1 day after found battery is ok condition refitted again issue resolve | Closed | Kapil Solanki
30 | NORTH | 211574112 | 2025-06-01 15:32 | 82.5 | 5H.8901.../2420121 | Coolant issue Call By Customer Name :- Davinder Singh Mobile No :- 7031001314 | Closed | Samar Bakers | 111 | Coolant Leakage due to Radiator hose clamp found loose so tightened the same & battery electrolite found slightly low so top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
31 | NORTH | 211574087 | 2025-06-01 15:30 | 0 | GP3.8301.../2420496 | Engine not cranking | Completed | Jakson & Company | LR- | Engine is not cranking, Change the self but same issue found, rotate with manually Engine not to be move | Closed | Gourav Sharma
32 | NORTH | 211574050 | 2025-06-01 15:26 | 125.4 | 4H.8042.C4../2420640 | Voltage Issue Call By Customer Name- Shivam singh Mo.No.- 8802206107 | Closed | Arihant Dies & Moulds Pvt. Ltd. | 2 | found some motors are shown phase reverse so change the r and y phase from customer end then check to start dg ok, advice and guide to the customer about operation and maintenance procedure of dg set. | Closed | Kapil Solanki
33 | NORTH | 211574024 | 2025-06-01 15:15 | 57 | T4.8941.../2320100 | Leakage Issue | Closed | Rishabdeo Crearions Pvt. Ltd. | 182 | found the TC oil drain hose defective,change with new proper fitted and hose clamp proper tight issue resolve | Closed | Kapil Solanki
34 | NORTH | 211574023 | 2025-06-01 15:14 | 82.5 | 5H.8901.../2320077 | Suply module filter change | Closed | SURYA PRESS MET PVT LTD | 181 | During service time filter was wrong collect so Change the supply module filter inlet | Closed | Kapil Solanki
35 | NORTH | 211573993 | 2025-06-01 15:09 | 82.5 | 5H.9301.../2300003 | Starting/Stopping Issue | Closed | Kirloskar regional training center | 12 | New battery fitment start the DG but fuel not storage | Closed | Kapil Solanki
36 | NORTH | 211573972 | 2025-06-01 15:02 | 0 | 3H.8902.../2421200 | fuel hand primer defectives | Task Close | Jakson & Company | LR- | found fuel hand primer not working check pump open the fuel filter change Valve, valve jam on closed position clean Valve and refitted hand primer working ok | Closed | Gourav Sharma
37 | NORTH | 211573900 | 2025-06-01 14:52 | 500 | DV8.8501.C4../2420048 | Abnormal sound Issue Call By Customer Name :- Raj Kumar Mobile No :- 9467425910 | Closed | Shahi Dyeing Pvt. Ltd. | 514 | Exhaust to Turbo charger joint gasket defective Refitted with new gasket, issue resolve | Closed | Kapil Solanki | Failed part
1 | East | 211578922 | 2025-07-01 15:22 | 15 | GP3.8501.../2420815 | Coolant Consumption issue Call By Customer Name :- Shivam Mobile No :- 7781881875 | Task Start | M/S RANJAN JEWELLERS | 54 | SE visited siteand found coolant leakage at thermostat outlet hose as well as there was leakage at radiator outlet hose due to the loose clamp so tighten the clamp issue resolved. | CLOSED | Prabhakar Kumar
2 | East | 211578906 | 2025-07-01 15:18 | 20 | GP3.8601.../2421268 | Leakage Issue | Task Start | D B BRICK FIELD |  | Update pending at ASE end | OPEN | Subhrajit Roy
3 | East | 211578772 | 2025-07-01 15:01 | 20 | GP3.8601.../2420072 | Trip_Genset_Low_Voltage | Open | Kedia Hardware. | 278 | visit pending | OPEN | Prabhakar Kumar
4 | East | 211577974 | 2025-07-01 12:10 | 15 | GP3.8501.../2420164 | Starting Issue Call By Customer Name :- Sourabh .. Mobile No :-6206523252 | Task Start | P. N. S. Enterprises | 138 | Customer side issue- unbalance load at certain time R -17 A, Y- 3 A, B- 5 A, suggested customer to distribute the load equally on all phases. | OPEN | Prabhakar Kumar
5 | East | 211577936 | 2025-07-01 12:04 | 5.5 | CC1.1013.../2400382 | Starting/Stopping Issue | Task Start | Anindya Gazmer | 8 | Update pending | CLOSED | Prosanjit saha
6 | East | 211574502 | 2025-06-01 16:28 | 25 | GP3.8702.../2420427 | INSTANCE ID:-100776270 SITE ID:-OR3124 CALL BY CUSTOMERA:- DG ISSUE :- DG AUTOAMATION FAULTY NAME :- Sagar Sahoo NUMBER :-6370297458 | Open | ATC Telecom Infrastructure Private Limited |  | SR cancelled because customer required CSP | CANCELLED | Ujjwal Das
7 | East | 211574484 | 2025-06-01 16:22 | 5.5 | CC1.1013.../2400100 | R-phase Under Voltage Issue Email by KGD Name - Sagar Chopra | Open | Border Road Organisation Arunachal Pradesh |  | Update pending at ASE end | OPEN | Subhrajit Roy
8 | East | 211573714 | 2025-06-01 13:59 | 30 | 3H.8902.../2420561 | Starting issue Call by customer Name: MAUSUMI DAS Number:7008552475 | Open | ABIS Exports India Private Limited. . | 2.17 | Low voltage issue. MCB to fuse voltage sensing Red wire was faulty, then replaced. Issue resolved | CLOSED | Ujjwal Das
9 | East | 211564435 | 2025-03-01 14:27 | 125.4 | 4H.8041.../2420715 | Starting Issue Call by Customer Name : Vikram .. No : 9079902118 | Task Start | GANPATI BHARAT PVT LTD | 268 | Update pending at ASE end | OPEN | Subhrajit Roy
10 | East |  |  | 20 | GP3.8604../2420083 | lube oil dilution | Task Start | RELIANCE JIO INFOCOMM LIMITED | 2 | Checked oil cooler found ok, after removing sump found no metal or dust or any other particle in the sump also on filling the water in radiator no leakage inside the crankcase, head and head gasket also found in good condition, under observation | OPEN | Prabhakar Kumar
1 | West | 211578947 | 2025-07-01 15:23 | 15 | GP3.8501.../2420943 | Display &Starting problem Call by : Customer Name : Sunil Bhoyar Contact : 9822023388 | Task Start | HARSHITA CONSTRUCTION | 52 | The controller was not turning on. So checked and found that the controller power supply fuse had blown. | CLOSED | Jagdeep saini
2 | West | 211578923 | 2025-07-01 15:22 | 40 | 3H.8951.../2420844 | Starting Issue Call By Customer Name :- Ram Mobile No :-9820787941 | Task Start | HAWARE LEGACCY | 2.55 | SPN/FMI- 636/2(Crank sensor), Engine start after hand priming. Under observation | OPEN | Jagdeep saini
3 | West | 211578752 | 2025-07-01 14:54 | 40 | 3H.8951.../2420999 | Starting Issue Call By Customer Name :- Nikhil Pawar Mobile No :- 7448052033 | Task Start | K. Power Generator | 1 | Battery connection was loose. | CLOSED | Vijay Patil
4 | West | 211577819 | 2025-07-01 11:37 | 160 | 6H.8475.../2420066 | Ad Blue Pump Fault Issue And Device Battery Voltage Issue Call By GOEM Name :- Dhruv Mistry Mobile No :-9099905622 | Open | Kavisha Group Developers | 108.29 | SPN/FMI- 2802/4, 15RB1 relay 2A1 wire was loose. So tightened the same. | CLOSED | Amit Shandilya | KRM check
5 | West | 211576069 | 2025-06-01 18:04 | 25 | GP3.8702.../2421072 | DG not working | Closed | ICICI Bank Limited | 1.1 | Controller ON/Off issue. So tightened the Switch & Controller wire and issue resolved. | CLOSED | Vijay Patil
6 | West | 211574637 | 2025-06-01 16:34 | 30 | 3H.8902.../2421308 | Over heating issue Call By Customer Name- Swarup Sarkar Mo.No.- 9635372946 | Closed | Larsen & Toubro Limited, Construction | 781 | The expansion bellow was broken so a new one was installed. | CLOSED | Jagdeep saini
7 | West | 211574222 | 2025-06-01 15:56 | 320 | F6.8802.../2420235 | Umber Lamp Alarm Issue Call by Customer Name : Mohan .. No : 8976804595 | Closed | Meta Arch Design Built | NA | Low adblue level. | CLOSED | Jagdeep saini
8 | West | 211564895 | 2025-03-01 | 625 | DV0.8501.C4../2420032 | CC SR | Task Start | Transworld Logistics Pvt. Ltd. | NA | 21 error code was showing in the controller. Checked and found ECU & DCU connector were open. | OPEN | Amit Shandilya
9 | West | 211553428 | 2025-01-01 | 30 | 3H.8902...2421152 | CC SR | Task Start | I P Laghu Udyog | CC | Coolant leakage from cylinder head in initial stage. | OPEN | Jagdeep saini
1 | South | 211562047 | 2025-02-01 19:25 | 125.4 | 4H.8042.C4../2420631 | Adouble sound problem Call by : Customer Name : Srrekanath Contact : 9908679955 | Task Start | Sangam Milk Producer Company Ltd...... | 20 | Adblue level low. Clear the DTC | closed | Mr. NandhaGopal
2 | South | 211560899 | 2025-02-01 15:40 | 57 | T4.8941.../2320285 | Coolant Call By Customer Name :- Mutthu . Mobile No :-7019716971 | Task Start | NAVACHETANA P U SCIENCE COLLEGE | 148 | Coolant leakage from radiator hose clamp. Tighten the hose clamp. | closed | Mr. Anil Kumar H G
3 | South | 211559132 | 2025-02-01 10:44 | 0 | T4.8941.../2422328 | FUEL LEAKAGE | Closed | SUNBEAM GENERATORS PVT LTD | LR | inspected the dg noticed the fuel return hose damage, change the new fuel return hose fixing properly, after start the dg check the fuel leak ok | closed | Mr. NandhaGopal
4 | South | 211559129 | 2025-02-01 10:42 | 58.5 | T4.8941.../2420485 | Red Light Alarm issue Call By Customer Name :- Praveen Mobile No :- 6362275481 | Open | M/s. N. S. Electricals. | 40.36 | Start found emergency stop button was on . released emergency stop button. started the engine found ok . checked the other general checkup was done finally started the engine found ok | closed | Mr. Anil Kumar H G
5 | South | 211559036 | 2025-02-01 10:34 | 250 | F6.8841.../2420090 | Battery Issue Call By Customer Name :-Ganesh Sir Mobile No :-7299074458 | Closed | JONES FOUNDATIONS PRIVATE LIMITED | 23 | INSPECT THE ENGINE FOUND KG745 UNIT SHOW IN ECU MALFUNCTION ALARM, IKONNECT TOOL CONNECT CLEAR THE DTC FILE, STARTED AND TESTED THE ENGINE ON LOAD FOUND DG SET RUNNING PERFORMANCE IS SATISFACTORY. 3031/14 | closed | Mr. NandhaGopal
6 | South | 211559028 | 2025-02-01 10:29 | 25 | GP3.8702.../2320006 | Smoking Problem Call by : Customer Name : Deepa Mam Contact :6282801545 | Task Start | Ms. Deepa Nair | 181 | Started the DG manually and it ran normally with no issues or smoke. Switched to auto mode with a 15.6 Amp load, and it ran fine. When the load went above 40 Amps, heavy white smoke came from the exhaust.Stopped the DG, checked the fuel tank, diesel quality, and fuel lines—everything was fine. Replaced the fuel filters, filled them with fresh diesel, cleaned the fuel filter sensor, and refitted it properly.Restarted the DG in auto mode and gradually increased the load to 70.2 Amps. No smoke was observed, and a 90-minute test run showed satisfactory performance. Advised the customer to keep checking for smoke at full load. | closed | Mr. Sanjaimon S | KRM check for load
7 | South | 211558989 | 2025-02-01 10:16 | 0 | T4.8941.../2421988 | FUEL LEAKGE FROM RETURN HOSE | Task Start | SUNBEAM GENERATORS PVT LTD | LR | inspection the dg noticed the fuel leak for lekaoff hose conneting end broken, change the fuel return hose leage issu solve | Task Start | Mr. NandhaGopal
8 | South | 211558525 | 2025-02-01 09:19 | 125.4 | 4H.8041.../2420373 | Oil leakage issue Call by KGD Name: Jamuna Number:9036094197 | Closed | SAMBRAMA PARTY HALL | 10.1 | As per above customer complaint fuel leakage, After visited the site checked the thoroughly fuel system and remove alternator side lowers and primary we found fuel leakage from bottom diesel tank, And unable to remove the diesel tank (removal inspection door)due to improper install the dg set.And also not space for removal the dg sliding diesel tank.. So informed to customer pls provide proper bedding and proper space for for diesel tank removal , So further we will give the actual failure report. | closed | Mr. Anil Kumar H G
9 | South | 211558507 | 2025-02-01 09:05 | 82.5 | 5H.8901.../2420286 | Under speed issue & Starting Problem Call by : Customer Name : Prabakaran Contact : 9629253849 | Task Start | Kirana Kart Technologies Pvt. Ltd. | 18 | 51/0, 51/5 Error showing. ITV jammed internal failure so replace the ITV. Now working ok. | closed | Mr. NandhaGopal
10 | South | 211558452 | 2025-02-01 08:19 | 20 | GP3.8601.../2420047 | AMF Panel Problem Call by : Customer Name :Papayan Contact :8760022704 | Closed | Sumathi Sekar | 66 | Engine under speed signal alarm so checked mpu disconnected and cleaned than connection checked in normal.trail run the dg auto/manual tested. | closed | Mr. NandhaGopal
11 | South | 211558501 | 2025-02-01 08:00 | 200 | 6H.8435.../2420096 | Starting Issue Call By Customer Name:- Ramu .. Mobile No:-6301005575 | Closed | Bojjaiah Convention | 37 | low adblue level.fill the adblue. Clear the error code with help of ikcoonet tool.then start the dg found okay | closed | Mr. NandhaGopal
12 | South | 211569024 | 2025-04-01 13:39 | 58.5 | T4.8941.../2421552 | Starting Problem Call by : Dealer Name :Karthik Contact :7708057324 | Open | SINGAPORE TEXTILES | 52 | Checked EGR line problem.so Remove the EGR cover in cleaning.Refitting the EGR cover. | closed | Mr. NandhaGopal | Load check
13 | South | 211568510 | 2025-04-01 12:24 | 20 | GP3.8601.../2420126 | Leakage Issue | Open | Manula Ramasahaym Reddy. |  | Visit pending | Open | Mr. MD Saleem
14 | South | 211568390 | 2025-04-01 11:59 | 58.5 | T4.8941.../2421802 | Starting Issue Call By Customer Name :- Vinaygan . Mobile No :-6385235499 | Open | DEVTA GENSETS [P] LTD | 930 | visit the site checked the generator found no any error code appear on the controller and checked the cable wiring harness found on/off relay fuse blown replace the fuse and clear the spn97/5,5838/2,520528/31 error code in DM2 and start the generator run with load found normal. | closed | Mr. NandhaGopal
15 | South | 211568343 | 2025-04-01 11:48 | 500 | DV8.9312.../2420003 | ALLARAM ISSUE | Task Start | Lakshmi Infra Projects LLP. | 1 | attend the site for commissioning then found engine not starting due to ECU not responding then checked the panel wiring and ECU wiring found ok then checked the interface card R1 R2 relay not working. | closed | Mr. MD Saleem | Failed part
16 | South | 211568287 | 2025-04-01 11:33 | 250 | F6.8841.../2420275 | Starting/Stopping Issue | Completed | RELIANCE PROJECTS & PROPERTY MANAGEMENT SERVICES LIMITED | 201 | Engine not starting due to D.E.F tank adblue level low so top up adblue to the D.E.F tank,now engine all parameters are good dg running properly | closed | Mr. Anil Kumar H G
17 | South | 211568051 | 2025-04-01 10:53 | 125.4 | 4H.8041.../2420748 | Oil Leakage Issue Call By Customer Name :- Jagdishan Sir Mobile No :-9841645254 | Task Start | V.SATHYAMOORTHY & CO | 644 | After checked the oil leakage for oil sump train bejo bolt moulding side miner crack so informed the customer side.tem solution for apply for m.seal checked the engine oil level checking ok.after thr start the engine running performance found ok. | Task Start | Mr. NandhaGopal
18 | South | 211567982 | 2025-04-01 10:38 | 58.5 | T4.8941.../2423059 | Starting Problem Call by : Dealer Name :Priya Contact :8870478403 | Task Start | S.Sundarraj | 5.5 | check the dg egr valve over current konnect tool connect clear the error code ECU flash problem solved check the all parameters found to start the dg note the performance found ok | closed | Mr. NandhaGopal
19 | South | 211567953 | 2025-04-01 10:33 | 2.8 | AP1.7003.../2400116 | Starting issue | Task Start | MOHAMED FAIZAL | 2 | visit the site and observed that engine petrol fuel leakage so check the fuel hoses clip leakage check the found ok. | closed | Mr. NandhaGopal
20 | South | 211567946 | 2025-04-01 10:33 | 500 | F6.8843.C4../2420004 & 2420004 | Starting Issue Call By Customer Name :- Gurubalam Mobile No :-8925961795 | Task Start | Nibav Lifts Private Limited | 93 | visited the customer site and noticed that the EB supply fuse open. Removed fuse and replaced new. started the set and tested without load found OK. | closed | Mr. NandhaGopal
21 | South | 211567671 | 2025-04-01 09:26 | 20 | GP3.8601.../2420393 | Starting Issue Call By Customer Name :- Mohammad .. Mobile No :-8001192666 | Open | Mr. Manish. |  | Visit pending | Open | Mr. NandhaGopal
22 | South | 211566055 | 2025-03-01 18:23 | 58.5 | T4.8941.../2421741 | Electrical Problems | Task Start | St Peter and Paul Church. | 16.18 | Checked and observed engine stopping due to overload Issue the issue is already informed to customer.Now customer rectify the Issue engine load problem is resolved now load in three phases is balanced but another issue informed to customer engine hot air recirculating into fresh air so engine temp is too high engine is stopping.There is no proper hot air ventilation in the dg room inform to the customer to resolve it customer said he will correct shortly. | closed | Mr. NandhaGopal
23 | South | 211565981 | 2025-03-01 18:00 | 20 | GP3.8601.../2421621 | Alarm sound problem Call by : Customer Name : Bhaskar reddy Contact : 8179582443 | Open | A Raviteja Reddy | 51 | Remove the maintenance alarm.put the battery found no distil water. fill the distil water in battery.after one hour start the dg found okay. | closed | Mr. NandhaGopal
24 | South | 211565308 | 2025-03-01 17:18 | 30 | 3H.8902.../2420235 | Starting/Stopping Issue | Task Start | Lakshmi Srinivasa Tyres | 3 | Battery was discharge so open the battery and give to charging then charge complete again connect the battery now running good battery voltage was 13.5V DC | closed | Mr. MD Saleem
25 | South | 211565087 | 2025-03-01 16:22 | 58.5 | T4.8941.../2421646 | Diesel Leakage Problem Call by : Customer Name :Mohamad Rafi Contact :9526454004 | Closed | PALM TREE SHOPPING PRIVATE LIMITED | 190 | Attented the site checked dg set with the presence of customer representative, checked fuel float sensor working found faulty,Then replaced fuel float sensor and connection connected properly, checked fuel level depend on tank capacity found controller fuel level percentage and tank guage indication is same rectified the problem, | closed | Mr. Sanjaimon S
26 | South | 211565081 | 2025-03-01 16:22 | 82.5 | 5H.8901.../2420045 | Starting Problem Call by : Customer Name : Mahesh Contact : 8977578782 | Task Start | Renee Emergency & Critical Care Centre. | 28 | visited the site observed spn 3031 fmi 14 adblue high temperature connect the tool flashing ok controller parameters change started the engine running condition ok | closed | Mr. MD Saleem
27 | South | 211564837 | 2025-03-01 15:32 | 15 | GP3.8501.../2421316 | STARTING PROBLEM | Completed | Saravanan Saravanan | 1 | SPN 240 AND FMI 7 Problem code found.the FIP inspection released the control rack. ECU program flash the old version and update the new version. after started the engine properly started. after take given load found ok. check the all necessary parameters all are found ok. | closed | Mr. Nandha Gopal | Under observatioon
28 | South | 211564765 | 2025-03-01 15:17 | 160 | 6H.8475.../2420238 | Coolant and Oil Mixture in radiator Call By KGD Name :-Jayanti Mobile No :- 9531815555 | Task Start | The Nest Bulders | 15 | checked the radiator hoses and connection found radiator to water pump coolant hose leakage condition removed the clamp an cleaned the leakage coolant refitted the hose clamp and top-up the coolant . | closed | Mr. NandhaGopal | GEOM issue
29 | South | 211564592 | 2025-03-01 14:53 | 20 | GP3.8601.../2420581 | Starting Issue. Call By Customer. Name:- Balaji .. Mobile No.:- 9841417558 | Completed | S. Meenakshi Sundaram Associates. | 14 | FOUND ENGINE NOT STARTING DUE TO EMERGENCY SWITCH ACTIVATED INDICATION SHOWS IN CONTROL UNIT DUE TO SWITCH AND WIRING (FERULE NO 11) LOOSE CONDITION.CORRECTED THE SAME PROPERLY.CHECKED ALL OTHER SYSTEMS FOUND OK.STARTED AND TESTED THE ENGINE WITH LOAD IN AUTO MODE.FOUND ENGINE RUNNING PERFORMANCE SATISFACTORY.NO ALARM ISSUE. | closed | Mr. NandhaGopal
30 | South | 211564557 | 2025-03-01 14:48 | 20 | GP3.8601.../2420066 | Starting/Stopping Issue | Closed | Cake Fabrica | 50 | 244/8 Attended the site and checked the DG with the presence of the customer representative. Checked and found Lop open fault alarm. Checked the LOP switch wiring connections G3 &D3. Loosened the lop switch and cleaned it. Then refitted and tighten the wiring connections. Then started the DG. Complaint rectified. Checked several times.No LOP alarm found. DG started and stops normally. DG running found normal. | closed | Mr. Sanjaimon S
31 | South | 211564157 | 2025-03-01 13:16 | 160 | 6H.8475.../2420208 | Tripping problem Call by : Customer Name : Ramu Contact : 6300717007 | Closed | Navtej Infrastructure Pvt Ltd | 330.11 | we have vist the site observed v belt slight loose so tighten the same& started engine on load trail found ok no problem no leakage coolint level ok v belt ok air filter ok battery watar level ok | closed | Mr. MD Saleem
32 | South | 211563845 | 2025-03-01 12:09 | 125.4 | 4H.8042.C4../2420871 | Emergency stop | Task Start | RAJSHEKAR MULTISPECIALITY HOSPITAL PRIVATE LTD | 1.19 | checked the dg visually, checked controller found emergency alarm, checked condition off emergency push found it&apos;s in disconnected condition, refitted push botton removed sensing cable postive wire reseted the alarm, | closed | Mr. Anil Kumar H G
33 | South | 211563426 | 2025-03-01 10:58 | 0 | F6.8842.C4../2420008 | FUEL FILTER ISSUE | Closed | SUNBEAM GENERATORS PVT LTD | LR | fuel filter assembly failed and replaced the new fuel filter assembly | closed | Mr. NandhaGopal
34 | South | 211563411 | 2025-03-01 10:51 | 0 | 3H.8951.../2421779 | FUEL LEAKAGE | Closed | SUNBEAM GENERATORS PVT LTD | LR | fuel leak pipe hose damage for Replaced the new leak off pipe hose fitted carried done. | closed | Mr. NandhaGopal
35 | South | 211572419 | 2025-06-01 10:22 | 30 | 3H.8902.../2421321 | KRM issue | Task Start | Bhaskar associates |  | KRM issue- running hours not correct showing | Task Start | Mr. Sanjaimon S
36 | South | 211571498 | 2025-05-01 17:18 | 20 | GP3.8601.../2421629 | Red Lamp Alarm Problem Call by : Customer Name : Sasetharen Contact :9600312545 | Task Start | Rudhrasenan Agencies | 45 | oil pressure switch wire pin open re tight the wire problem solved | closed | Mr. NandhaGopal
37 | South | 211571492 | 2025-05-01 17:10 | 125.4 | 4H.8042.C4../2420279 | Low speed problem Call by : Customer Name : Dineshreddy Contact : 8639307580 | Open | Shri Sai Teja Industries | 56 | visit the site check the engine oil level found ok check the battery found ok check the coolant H Mark found ok check v belt found ok check fuel pipe pipe found ok Air lock problem found ok started engine found ok | closed | Mr. Anil Kumar H G
38 | South | 211571450 | 2025-05-01 16:38 | 58.5 | T4.8941.../2421041 | Starting/Stopping Issue | Task Start | Shaik Adam Basha. |  | Visit pending | Task Start | Mr. NandhaGopal
39 | South | 211571467 | 2025-05-01 15:38 | 40 | 3H.8951.../2420786 | Starting issue Call by customer Name: Namo narayan . Number: 7014570746 | Task Start | Directorate General Of Lighthouses And Lightships | 3 | visited the site inspected the engine, check the problem engine lamp on and error code 2802/4 and 97/5 check the fuel level and quality and sensor, sensor wire cable loose ,so reconnect properly, than check the wiring connection re tight the wiring connection, check the engine oil level, check the battery distilled water, check the coolant level, starting the engine test found OK | closed | Mr. NandhaGopal
40 | South | 211571302 | 2025-05-01 11:33 | 160 | 6H.8475.../2420129 | Coolant Consumption Issue Call By Customer Name :- Ramalinga Mobile No :- 9341808090 | Open | S R N Mehta School | 64 | visit the site carry out the duty check the engine found coolant leakage from radiator hose pipe because of loss clamp so refitted the hose clamp and taken a trail on load leakage arrested running condition is normal | closed | Mr. Anil Kumar H G
41 | South | 211571301 | 2025-05-01 11:31 | 20 | GP3.8601.../2421418 | Alarm problem Call by : Customer Name :Sreejith Contact :7902279999 | Cancelled | SREEJITH PULLAIKODI |  | Cancelled | Cancelled | Mr. Sanjaimon S
42 | South | 211570806 | 2025-04-01 18:49 | 160 | 6H.8475.../2420111 | Leakage Issue | Task Start | KVR AUTOMALL PRIVATE LIMITED | 667 | 175/4, 110/16 . found high coolant temperature, check belt and coolant level, Radiator hose, Radiator fan, Radiator fins, found coolant leakage from top outer side of Radiator. | closed | Mr. Sanjaimon S
43 | South | 211569860 | 2025-04-01 15:31 | 250 | F6.8841.../2420413 | Starting Issue Call By Customer Name- Gaurav Sir Mo.No.- 8884440328 | Task Start | KRISHNA LAMICOAT PVT LTD | 6.53 | as per the complaint engine not starting on auto mode visited the site found that auto starting has been disabled in the engine controller unit so we have program and switched to enable mode and started the engine observed on auto and manual mode found working is satisfactory. | closed | Mr. Anil Kumar H G
44 | South | 211569332 | 2025-04-01 14:26 | 15 | GP3.8501.../2420544 | Starting issue Call by customer Name: Harish Number:6364038815 | Closed | Dak Infra Projects | 32 | visited the site carried out the daily check check up and control panel relay board 2E wire is loose connection and tight the wire after started the engine running found normal ok | closed | Mr. Anil Kumar H G
45 | South | 211573562 | 2025-06-01 13:24 | 58.5 | T4.8941.../2421388 | Automatically switching off Call by : Customer Name :Purthvi Contact :8197168273 | Open | Sri Vishnu Grand Veg | 63 | Engine not starting due battery charging low and battery charger so give the battery for chargi | closed | Mr. Anil Kumar H G
46 | South | 211573561 | 2025-06-01 13:24 | 250 | F6.8841.../2420398 | not taking load | Task Start | BIORHYTHM AGRO RESEARCH PVT LTD | LR | engine not starting because diesel life pump not working,as per godson(ASE) instructions site again visited and removed the protect filter assembly and send to Bosh for repairing. | Task Start | Mr. Sanjaimon S
47 | South | 211573438 | 2025-06-01 13:03 | 40 | 3H.8951.../2421293 | Smoke issue Call by : Customer Name : Adaikulam raj Contact :8300127799 | Completed | Ramjay Agencies | 51 | checked exhaust leakage problem due to expansion below cut, due to alignment problem,so the expansion below changed and alignment corrected,as per koel AO instructions found ok, checked all bolt and nut retighten found ok, start the engine and checked exhaust leakage nil, checked load testing found ok. | closed | Mr. NandhaGopal
48 | South | 211573274 | 2025-06-01 12:38 | 10 | GP3.8301.../2420015 | Under speed problem Call by : Customer Name : Sukumar Babu Contact : 9391035753 | Task Start | Mr. Sukumar |  | Visit pending | Task Start | Mr. MD Saleem
49 | South | 211573207 | 2025-06-01 12:35 | 125.4 | 4H.8042.C4../2420108 | Starting Issue Call By Customer Name :- 8722443077 Mobile No :-Nagarjun | Task Start | PAI INTERNATIONAL ELECTRONICS LIMITED ... | 58 | check the v belt loss retit panal board wring problem retit engine start profomas okay | closed | Mr. Anil Kumar H G
50 | South | 211573036 | 2025-06-01 11:56 | 15 | GP3.8501.../2421832 | fuel senser | Task Start | SRI BALAPPA HULIGEMMA PETROLEUM | 3 | attend the site checked the all DG condition found ok and checked the all DG parameters found ok found the DC Supply issue so retight the all connectors and checked the all wiring connections and resolve the issue | closed | Mr. Anil Kumar H G
51 | South | 211572988 | 2025-06-01 11:54 | 58.5 | T4.8941.../2422362 | Starting issue Call by KGD Name: Jamuna Number:9036094197 | Task Start | MANJUNATH | 13 | visited the site dg working fine but abnormal sound issue. generator running condition exhaust pipe outlet doc to silencer pipe mounting clamp touched to pipe. | closed | Mr. Anil Kumar H G
52 | South | 211572982 | 2025-06-01 11:49 | 30 | 3H.8902.../2421317 | Starting Problem Call by : Customer Name :Palanimurugan Contact :9342044381 | Task Start | Xan Matric Higher Secondary School | 5.58 | reach the site to check the engine oil level after start the engine. in dg safety board not on . to check the battery voltage 1.5 v show in multi meter.to check battery charger not work customer not give neutral in battery charger. connect the neutral battery charger good working. inform to the customer to start the dg after 2 hours battery will charging | closed | Mr. NandhaGopal
53 | South | 211572622 | 2025-06-01 11:07 | 20 | GP3.8601.../2421615 | Red lam on | Task Start | DASARI GEETHA | 3 | found alarm red lamp on emergency stop activated due to emergency stop wiring is loose so retight then start dg found running is ok then put on load dg set load is ok | closed | Mr. MD Saleem
54 | South | 211578960 | 2025-07-01 15:23 | 15 | GP3.8501.../2421853 | COMMISSIONING REQUIRED BY GOM | Task Start | Sathya Agencies Pvt. Ltd. .. | LR | checked engine oil level ok.checked earth connection ok.fitted battery connection ok.checked all wire condition ok | closed | Mr. Nandha Gopal
55 | South | 211578418 | 2025-07-01 13:31 | 82.5 | 5H.8901.../2420205 | Red Lamp On Alarm Call By Customer Name :- chandru Mobile No :-9611365658 | Task Start | MAX FURN | 145 | As per the customer complaint red lamp on alarm after visited the site found that there is a Adblue level low showing from the engine controller and top up the DEF to the tank and connected the I connect tool and cleared the error code finally started the engine observed on running without load condition found working is satisfactory. | closed | Mr. Anil Kumar H G
56 | South | 211578350 | 2025-07-01 13:26 | 40 | 3H.8951.../2420821 | Starting Problem Call by : GOEM Name : Paramasivan Contact : 6380799520 | Open | Sree Mookambika Institute Of Medical Science |  | Visit pending | Task Start | Mr. NandhaGopal
57 | South | 211578034 | 2025-07-01 12:26 | 25 | GP3.8702.../2421281 | DG NOT STARTING | Task Start | Mini Max | 2 | Attended the site .Checked complaint. A general inspection is carried out. While starting dg 5 error codes are there . 3 codes in DM1 and 2 codes in DM2.All are related to the EGR valve. Hence checked EGr valve connections,clips , Continuity checked . Then the tool connected and alarms are cleared. Started the dg and tested . Again error code 2791/18. so session is created with 25kva.EGR_dummy app code in the Ikonnect tool. Ecu is flashed with the tool. Then alarm cleared .started dg. Dg tested several times and now no e | closed | Mr. Sanjaimon S
58 | South | 211577930 | 2025-07-01 12:01 | 58.5 | T4.8941.../2421240 | Commissioning | Task Start | Asian Cancer Hospital |  | SR need to be cancelled |  | Mr. MD Saleem
59 | South | 211577914 | 2025-07-01 11:58 | 10 | GP3.8301.../2420009 | Voltage Fluctuation issue Call By Customer Name :- Kamal Deep Mobile No :- 8904124429 | Task Start | KAMAL DEEP | 71 | Flickering issue, use TAVR27 but issue not resolved | Task Start | Mr. Anil Kumar H G
60 | South | 211577823 | 2025-07-01 11:38 | 125.4 | 4H.8041.../2420828 | Starting Issue Call By Customer Name :- Mahaeoob Pasha Mobile No :-9550565822 | Task Start | Kalyan Jewellers India Limited. |  | update pending | Task Start | Mr. NandhaGopal
61 | South | 211577716 | 2025-07-01 11:23 | 400 | DV8.8542.C4../2320008 | Tripping Issue Call By Customer Name ;- Harish .. No :- 7019123224 | Closed | ULTRA TECH CEMENT LIMITED UNIT RAJASHREE CEMENT WORKS | 81.53 | Visit the site, found no issue | closed | Mr. Anil Kumar H G
62 | South | 211577687 | 2025-07-01 11:18 | 125.4 | 4H.8041.../2420588 | Genset Trip | Closed | Anamalaiss Retails Private Limited. | 44 | check the oil level and conditions due to replace conditions Adblue level is very low than engine is tripping oil service and Adblue top up very quickly | closed | Mr. NandhaGopal
63 | South | 211577678 | 2025-07-01 11:13 | 35 | 3H.8902.../2421868 | Voltage Problem Call by : Dealer Name : Govindan Contact : 9790033065 | Task Start | Sri Dhanalakshmi Thirumana Maaligai | 7 | Voltage fluctuation, also flickering issue as the customer load is not properly, try to replace the AVR but issue is there(customer not satisfy) | closed | Mr. NandhaGopal
64 | South | 211577631 | 2025-07-01 11:07 | 750 | DV2.8501.C4../2320016 | Flickering | Task Start | Recaero India (P) Ltd., | 86 | as per kirloskar instructions DV2.Dummy file flashing to ECU and checked after flashing ecu ,start the dg running ok, all parameters working fine. | closed | Mr. Anil Kumar H G
65 | South | 211577342 | 2025-07-01 10:16 | 20 | GP3.8601.../2420177 | Starting Issue Call By Customer Name :-Sukesh Shetty No :- 9019719108 | Closed | VASUNDHARA AUTOMATION & ENGINEERING SERVICES PVT LTD | 8 | battery completely discharged reason due to customer not starting dg more than 1 week, also .battery charger connection needs to be done | closed | Mr. Anil Kumar H G
66 | South | 211577281 | 2025-07-01 10:01 | 30 | 3H.8902.../2422244 | Not start | Closed | A. M. MOTORS | 3 | SPN-2791/FMI-18 SPN-5838/FMI-1 , flash the dummy file | closed | Mr. Sanjaimon S
67 | South | 211576040 | 2025-06-01 17:56 | 5.5 | CC1.1013.../2400664 | Starting Issue Email By KGD Name:-Poonam Shedage | Open | Accurate Powertech India Private Limited . |  | Cancelled | Cancelled | Mr. Anil Kumar H G
68 | South | 211576038 | 2025-06-01 17:56 | 5.5 | CC1.1013.../2400662 | Starting Issue Email By KGD Name:-Poonam Shedage | Open | Accurate Powertech India Private Limited . |  | Cancelled | Cancelled | Mr. Anil Kumar H G
69 | South | 211576010 | 2025-06-01 17:53 | 5.5 | CC1.1013.../2400676 | Starting Issue Email By KGD Name:-Poonam Shedage | Open | Accurate Powertech India Private Limited . |  | Cancelled | Cancelled | Mr. Anil Kumar H G
70 | South | 211575997 | 2025-06-01 17:47 | 500 | DV8.8501.C4../2420008 | Trip_Genset_Low_Voltage | Closed | ST. Marthas Hospital | 7.29 | found fuel leakage from fuel filter. found it was loose . tight the fuel filter and started the engine found ok | closed | Mr. Anil Kumar H G
71 | South | 211575167 | 2025-06-01 17:35 | 320 | F6.8802.../2420139 | Starting/Stopping Issue | Task Start | Sri Durga Industries | 34 | Adblue concentration variation while running | Task start | Mr. Anil Kumar H G
1 | NORTH | 211583424 | 2025-08-01 13:41 | 40 | 3H.8951.../2420602 | Starting issue Call by customer Name: Purshottam Number:9314064102 | Open | L. N. A. Infraprojects Pvt. Ltd. |  | Cancelled-Problem solve in Pm visit | Cancelled | Gourav Sharma
2 | NORTH | 211583422 | 2025-08-01 13:40 | 40 | 3H.8951.../2420356 | Starting Issue & Preventive Maintenance Call By Customer Name - Gogaram ji Number - 9602062139 | Open | Sudharam Assoceates |  | Cancelled-Problem solve in tele dicussion | Cancelled | Gourav Sharma
3 | NORTH | 211583339 | 2025-08-01 13:23 | 25 | GP3.8702.../2420272 | Inspection/Maintenance | Task Start | VEER BALAJI FUEL CENTRE | 36 | Low coolant level, topup the coolant | Closed | Sudhir Awasthi
4 | NORTH | 211582905 | 2025-08-01 12:11 | 125.4 | 4H.8041.../2420355 | Red Light Alarm Call By Customer Name- Madan singh Mo.No.- 7065173754 | Task Start | Nirman E. Store LLP. . | 16 | Found Emergency button in pressed condition, realease the same issue resolve | Closed | Kapil Solanki
5 | NORTH | 211582805 | 2025-08-01 11:50 | 58.5 | 6H.9840.../2420005 | Automation issue Call By Customer Name :- Ravindra Rathod Mobile No.:- 9811211463 | Task Start | Rathoure Metal Smelting | 20 | DG not start due to gas pressure not build up so, set the gas pressure through regulator then start the DG but PRV is not proper working so, need to be replace | Closed | Kapil Solanki
6 | NORTH | 211582689 | 2025-08-01 11:27 | 320 | F6.8802.../2320031 | Inspection/Maintenance | Completed | Sanspareils Greenlands Pvt. Ltd. | 472 | DEF filter change | Closed | Sudhir Awasthi
7 | NORTH | 211582609 | 2025-08-01 11:11 | 320 | F6.8802.../2420147 | Starting Issue Call By Customer Name :-Pavan No :- 9667637254 | Closed | Techno Ref Solution Company | 29 | Low def level topup the Def clear the fault code issue resolve | Closed | Kapil Solanki
8 | NORTH | 211582588 | 2025-08-01 11:08 | 750 | DV2.8501.C4../2420029 | RELAY CARD FAULTY | Task Start | ABNC PROPERTY MANAGEMENT PRIVATE LIMITED | 36 | Found R2 relay faulty, replace the same | Closed | Kapil Solanki | ECU faults check
9 | NORTH | 211580886 | 2025-07-01 18:18 | 160 | 6H.8475.../2420024 | Abnormal sound | Task Start | Tool Room Engineers LLP | 208 | Abnormal sound change the injector found no abnormal sound, so load trial next day | OPEN | Kapil Solanki
10 | NORTH | 211580548 | 2025-07-01 17:18 | 25 | GP3.8702.../2420404 | Starting/Stopping Issue | Closed | Public Works Department Uttar Pradesh | 29 | Airl lock in fuel line, remove the air issue resolve | Closed | Sudhir Awasthi
11 | NORTH | 211580364 | 2025-07-01 16:48 | 57 | T4.8941.../2320126 | Starting/Stopping Issue | Closed | XPERT POWERGEN PRIVATE LIMITED | 2243 | Battery voltage low, Battery charger not done because it is a rental DG , Connect the charger connection issue resolve | Closed | Kapil Solanki
12 | NORTH | 211580239 | 2025-07-01 16:21 | 625 | DV0.8501.C4../2420017 | Fues issue | Closed | SUNGLOW WORKS LLP | 8 | check found and fuse fault and 40 amp fuse change | Closed | Kapil Solanki
13 | NORTH | 211578851 | 2025-07-01 15:02 | 750 | DV2.8501.C4../2420126 | Electrical Problems | Task Start | IST ALARM SYSTEM ASSOCIATES PRIVATE LIMITED | 13 | SPN/FMI 633/3 Rail Pressure- Functional Voltage above Normal, Check IMV both continuity & BANK1- Voltage 5v, Bank2-6v then check water in fuel sensor found ok, Now found Lifting pump Bank 1 faulty replace the same issue resolve | Closed | Kapil Solanki
14 | NORTH | 211578745 | 2025-07-01 14:51 | 125.4 | 4H.8041.../2420030 | Starting/Stopping Issue | Closed | Kamal Wire | 83 | Def level Alarm, Clear the code issue resolve | Closed | Gourav Sharma
15 | NORTH | 211578627 | 2025-07-01 14:38 | 58.5 | 6H.9840.../2420003 | Load Issue Email By - Customer Name - Santoshi | Closed | Ranawat Inc | 14 | Controller show the under speed alarm, Check & found R-phase fues defective so,replace the same issue resolve | Closed | Kapil Solanki
16 | NORTH | 211578613 | 2025-07-01 14:24 | 20 | GP3.8601.../2420483 | BAttery Issue Call By Customer Name :- Sanjay Raj Mobile No :-9828406318 | Task Start | Surabhi Food Industries. | 123 | Battery discharge Battery charger connection done Now battery charging ok | Closed | Gourav Sharma
17 | NORTH | 211583413 | 2025-08-01 13:37 | 500 | DV8.8501.C4../2420030 | Starting/Stopping Issue | Task Start | Manav Mangal Society | 89 | SPN/FMI-97/2 Water in Fuel,No water traces in Fuel;Remove the code & run the DG ;Issue resolved | Closed | Ved Prakash Gupta
18 | NORTH | 211582947 | 2025-08-01 12:18 | 58.5 | T4.8941.../2422129 | Leakage Issue | Task Start | LA GRAND HOTEL | 9 | Coolant Leakage found from hose(Radiator Bottom Side) , Tightened the clamp & resolve the Issue | Closed | Ved Prakash Gupta
19 | NORTH | 211582604 | 2025-08-01 11:07 | 20 | GP3.8601.../2420932 | Automation Issue Call By Customer Name- Vikas Goel Mo.No.- 9996032784 | Task Start | PARWATI GARDEN | 29.23 | DG Starting issue in Auto mode due to mains setting enable so corrected the same in controller & resolve the issue | Closed | Ved Prakash Gupta
20 | NORTH | 211582413 | 2025-08-01 10:24 | 15 | GP3.8501.../2421070 | Starting issue And preventive Maintenance Call by customer Name: SHARIQ RASHID . Number:9149410921 | Task Start | Shan Filling Station | 148 | Maintenance due Alarm occurred in Controller so reset the same & resolve the Issue | Closed | Ved Prakash Gupta
21 | NORTH | 211582389 | 2025-08-01 10:24 | 15 | GP3.8501.../2421383 | Coolant Leakage Issue Call By Customer Name ;- Ranjeet Singh No :- 8899635604 | Task Start | BHARAT GENERAL STORE | 10.03 | Coolant leakage due to coolant pipefound broken so change the same(Provided by customer) & resolve the Issue | Closed | Ved Prakash Gupta
22 | NORTH | 211580677 | 2025-07-01 17:35 | 15 | GP3.8501.../2421571 | Starting/Stopping Issue | Task Start | ARYA PAINT & HARDWARE STORE | 3.35 | Under Cancellation-Work not comes under Warranty | Cancelled | Ved Prakash Gupta
23 | NORTH | 211580585 | 2025-07-01 17:25 | 82.5 | 5H.8901.../2320006 | Starting Issue Call By Customer Name :- Ashu Sir Mobile No :-9992144500 | Closed | M. K. Textiles | 7.3 | Auto starting Issue due to 11 no. wire found loose in Disribution Block so connected the same & resolve the Issue | Closed | Ved Prakash Gupta
24 | NORTH | 211579930 | 2025-07-01 15:44 | 750 | DV2.8501.C4../2320024 | FLASHING ISSUE | Task Start | BHARAT RASAYAN LTD | 314 | New Dummy File has Flashed in DG due to continous Water Self Test Alarm occurred | Closed | Ved Prakash Gupta
25 | NORTH | 211578948 | 2025-07-01 15:23 | 40 | 3H.8951.../2421130 | Voltage Fluctuation | Closed | Mr. Sushant Nayyar | 6 | DG Tripping due to unbalance Load(33,22,20)amp ,after uniformly Load devided by electrician,Issue resolved | Closed | Ved Prakash Gupta
26 | NORTH | 211578547 | 2025-07-01 14:07 | 25 | GP3.8702.../2420946 | Excessive Smoke | Task Start | BHARAT CROP PROTECTION PVT LTD | 5.51 | Tripping issue due to overload;same educated to customer to keep load within KOEL Parameter | Closed | Ved Prakash Gupta
27 | NORTH | 211573304 | 2025-06-01 12:42 | 58.5 | T4.8941.../2422430 | Preventive Maintenance Call By Customer Name :- Satish Mobile No :- 9996170538 | Task Start | E-Derma Pharma | 14.33 | Starting Issue due to connection found loose(2 No. wire on MCB) so connected the same & resolve the Issue | Closed | Ved Prakash Gupta
28 | NORTH | 211572542 | 2025-06-01 10:53 | 82.5 | 5H.8901.../2320028 | Alarm issue | Task Start | Bharti Enterprises | 100.56 | R-Phase under voltage Alarm occurred due to R-Phase fuse found faulty so replaced the same & resolve the Issue | Closed | Ved Prakash Gupta
29 | NORTH | 211571519 | 2025-05-01 18:04 | 25 | GP3.8702.../2421119 | Under speed Alarm Call By Customer Name :-Pankaj Mobile No :- 9805887886 | Open | Lenexis Foodworks Pvt. Ltd. | 16.28 | Under Cancellation-Rectified on Telephonic Discussion | Cancelled | Ved Prakash Gupta
30 | NORTH | 211571406 | 2025-05-01 14:04 | 30 | 3H.8902.../2420427 | Protect lamp on Alarm issue call By customer name :Jitendr .. no :9485275720 | Open | Assam Rifles | 207.73 | Under Cancellation-Rectified on Telephonic Discussion | Cancelled | Ved Prakash Gupta
31 | NORTH | 211571259 | 2025-05-01 09:59 | 15 | GP3.8501.../2420659 | Starting Issue Call By Customer Name :- Raichand Rai Mobile No :- 9002207788 | Open | M. H. Joinery Machines | 15.63 | Under Cancellation-Rectified on Telephonic Discussion | Cancelled | Ved Prakash Gupta
32 | NORTH | 211571282 | 2025-05-01 09:26 | 62.5 | T4.8941.../2320097 | Starting Issue Call By Customer Name:-Surendra No:-7988586645 | Task Start | Bhajana Home Dacor Private Limited | 352.21 | Battery found faulty(Gravity found low of cell 4-Nill),Replace the same & resolve the issue | Closed | Ved Prakash Gupta
33 | NORTH | 211570727 | 2025-04-01 18:02 | 125.4 | 4H.8041.../2320034 | Starting/Stopping Issue | Cancelled | Abhitex International | 291.28 | Under Cancellation-Rectified on Telephonic Discussion | Cancelled | Ved Prakash Gupta
34 | NORTH | 211570579 | 2025-04-01 17:26 | 320 | F6.8802.../2420010 | ECU Alarm issue Call By Customer Name - Chetan Sharma Number - 9646507019 | Closed | SURGITECH INNOVATION P LTD | 85 | DG voltage falucation so check the Maine alternator and found that Avr card voltage not stable. So adjust the AVR card voltage adjustment | Closed | Ved Prakash Gupta | Details pending
35 | NORTH | 211570334 | 2025-04-01 16:46 | 15 | GP3.8501.../2421058 | Red Lamp On Alarm Call By Customer Name :- Manna Batacharya Mobile No :- 8787855231 | Cancelled | KIBOKO ELECTRICALS | 12.56 | Under Cancellation-Wrongly Open | Cancelled | Ved Prakash Gupta
36 | NORTH | 211570192 | 2025-04-01 16:17 | 320 | F6.8802.../2420029 | ECU Amber Alarm Call By Customer Name :-Rajat . Mobile No :-8146798381 | Closed | Citi Developers | 53 | SPN/FMI-1761/16 Low AdBlue Level ; Physically found low(26%) so Top-up the same & educate customer to keep AdBlue level 50% Min | Closed | Ved Prakash Gupta
37 | NORTH | 211569734 | 2025-04-01 15:09 | 400 | DV8.8542.C4../2320010 | Voltage Â Issue Call By Customer Name :-Suresh Kumar Mobile No :-9991592430 | Cancelled | BPCL. Haryana | 224.21 | Under Cancellation-Appointment Issue | Cancelled | Ved Prakash Gupta
38 | NORTH | 211569568 | 2025-04-01 14:52 | 15 | GP3.8501.../2420089 | Electrical Problems | Closed | P. S. Photography Pargat Singh. | 319 | Engine auto start issue , Check Auto wire the 22(E) point not working so use the 10(H ) point and change the ems setting now start the dg set on auto mode ok | Closed | Ved Prakash Gupta
1 | East | 211583454 | 2025-08-01 13:43 | 20 | GP3.8601.../2420888 | Starting/Stopping Issue | Task Start | Bhartia Infra Projects Ltd | 51 | DG was not starting due feed pump was not operating, then checked voltage at feed pump found no voltage then on inspection found controller 4 no(start from controller) wire found loose after tightening issue resolved. | CLOSED | Subhrajit Roy
2 | East | 211580884 | 2025-07-01 18:16 | 30 | 3H.8902.../2420561 | Trip_Genset_High_Voltage | Open | ABIS Exports India Private Limited. . | 14.29 | Update pending | OPEN | Ujjwal Das
3 | East | 211580839 | 2025-07-01 18:09 | 58.5 | T4.8941.../2420505 | Starting Issue Call By Customer Name- Chinnai TripatI Mo.No.- 9937118247 | Closed | M/S. VATIKA | 76 | SE found DG not start due to fuel level low and air lock in fuel line after top up the fuel level and release the air in fuel line then start the DG running ok & educated to customer maintain fuel in fuel tank minimum 50 percent ,this problem not happen in future. | CLOSED | Ujjwal Das
4 | East | 211578906 | 2025-07-01 15:18 | 20 | GP3.8601.../2421268 | Leakage Issue | Closed | D B BRICK FIELD | 63 | There was diesel seepage at the fuel filter, then tighten the filter issue solved, | CLOSED | Subhrajit Roy
5 | East | 211578772 | 2025-07-01 15:01 | 20 | GP3.8601.../2420072 | Trip_Genset_Low_Voltage | Open | Kedia Hardware. | 278 | False SR created by mistake, SR has been cancelled | CANCELLED | Prabhakar Kumar
6 | East | 211577729 | 2025-07-01 11:27 | 58.5 | T4.8941.../2422213 | Diesel leakage issue. Call By Customer. Name:- Kalpana .. Mobile No.:- 9031034238 | Closed | HERITAGE LANDMARKS AUTOWORLDS PVT LTD | 36 | As per complaint SE found no such leakage of diesel, and customer doubt was fuel sensor faulty but its was normal, Door lock was also not locking properly so adjusted its hook restored and customer satisfied. | CLOSED | Prabhakar Kumar
7 | East | 211564435 | 2025-03-01 14:27 | 125.4 | 4H.8041.../2420715 | Starting Issue Call by Customer Name : Vikram .. No : 9079902118 | Completed | GANPATI BHARAT PVT LTD | 268 | Update pending at ASE end | OPEN | Subhrajit Roy
8 | East |  |  | 20 | GP3.8604../2420083 | lube oil dilution | Task Start | RELIANCE JIO INFOCOMM LIMITED | 2 | Checked oil cooler found ok, after removing sump found no metal or dust or any other particle in the sump also on filling the water in radiator no leakage inside the crankcase, head and head gasket also found in good condition, under observation | OPEN | Prabhakar Kumar
1 | West | 211578578 | 2025-07-01 14:12 | 15 | GP3.8501.../2420546 | Starting/Stopping Issue | Open | CUPID Limited | 448 | Sweep Stuck DTC-240/7. So move the rack manualy and started the Genset. | CLOSED
2 | West | 211577476 | 2025-07-01 10:38 | 30 | 3H.8902.../2421492 | Starting/Stopping Issue | Open | Axis Bank Ltd | 2 | SPN/FMI- 157/14, Cleared the DTC& remove the air from fuel line | CLOSED
3 | West | 211573979 | 2025-06-01 15:05 | 500 | DV8.8501.C4../2420138 | Genset Trip | Task Start | Kolte-Patil Integrated Townships Limited | 13 | Low battery voltage. So engineer checked and found IND connector of charging alternator was open. | CLOSED
4 | West | 211541913 | 30-12-2024 | 750KVA | DV2.8501.C4 / 2420174 | CC SR | Task Start | GULBRANDSEN INDUSTRIES LLP, Dahej | CC | Oil Leakage from12 Number cyl. push rod tube. | OPEN
5 | West | 211573715 | 2025-06-01 13:58 | 320 | F6.8802.../2420260 | Starting Issue Call By Â Service Dealer Name :- Kishor .. Mobile No :- 8815336489 | Task Start | WHISTLING WOOD | 9.54 | SPN/FMI-516166/0( Hot Shutdown), So educated the customer. | CLOSED
1 | South | 211582974 | 2025-08-01 12:26 | 320 | F6.8802.../2420142 | Tripping issue Call By Customer Name :- MR chandn Mobile No :- 8789482769 | Open | Bangalore Generator | 74 | 1761/16, 3031/14, 5461/0, 520528/31 checked and found DEF level is 0% | Task Start | Mr. Anil Kumar H G
2 | South | 211582925 | 2025-08-01 12:23 | 125.4 | 4H.8042.C4../2420275 | Starting Issue Call By Customer Name :- Atish Kumar Mobile No :- 8317489126 | Task Start | Gudipati Sumalatha | 5 | 3224/2 error code replace the relay board. | closed | Mr. Anil Kumar H G
3 | South | 211582806 | 2025-08-01 11:50 | 320 | F6.8802.../2420270 | Electrical Problem | Task Start | Dr. M. Mani Elango M. S. | 768 | checked found engine auto starting problem due to deep sea controller side mains failure detection is not enabled so deep sea 745 controller programs checked in laptop and open the deep sea controller program, read the program, then open the mains option,then checked mains failure detection is now enabled then load test in auto mode dg running good condition in auto mode | closed | Mr. NandhaGopal
4 | South | 211582591 | 2025-08-01 11:01 | 125.4 | 4H.8041.../2420202 | Alarm problem Call by : Customer Name : Vinoth Kanan Contact : 9585073663 | Task Start | Monarch Biotech Private Limited. | 145 | 1761/16 , 516166/0 adblue level low . Clear the DTC | closed | Mr. NandhaGopal
5 | South | 211581831 | 2025-08-01 09:16 | 82.5 | 5H.8901.../2320019 | Starting/Stopping Issue | Completed | STOVE KRAFT LIMITED | 52.5 | 1761/16 adblue low top up and clear DTC. | closed | Mr. Anil Kumar H G
6 | South | 211580719 | 2025-07-01 17:44 | 160 | 6H.8475.../2420370 | Abnormal Sound Call by : KGD Name : Paramasivan Contact : 6380799520 | Task Start | GS LIFT | NA | Visit pending | Task Start | Mr. NandhaGopal
7 | South | 211580683 | 2025-07-01 17:38 | 58.5 | T4.8941.../2423044 | Other-Engine tripping EGR error | Closed | Sai Balaji Hospital | 2.13 | 2791/18. checked the wiring connection tightness no issues no wiring connection ECU flash & update process started the engine on load performance of the dg set found ok | closed | Mr. NandhaGopal
8 | South | 211580274 | 2025-07-01 16:28 | 40 | 3H.8951.../2420114 | Hunting problem Call by :Customer Name : Manohar Contact : 7569172525 | Closed | Dr. Reddys Foundation | 320 | DG ON / OFF switch not working replace the same. | closed | Mr. MD Saleem
9 | South | 211578013 | 2025-07-01 12:19 | 0 | 5H.5351.../2520008 | ERROR CODE | Task Start | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing ( 7026/8 metering unit error ). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
10 | South | 211577989 | 2025-07-01 12:16 | 0 | 5H.5351.../2520001 | ERROR CODE | Task Start | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing the (171/4 environmental temperature sensor error ). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
11 | South | 211577982 | 2025-07-01 12:14 | 0 | 5H.5351.../2420014 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing (100/1 oil pressure sensor error). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
12 | South | 211577977 | 2025-07-01 12:12 | 0 | 5H.5351.../2520016 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing (171/3 environmental temperature sensor error). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
13 | South | 211577971 | 2025-07-01 12:10 | 0 | 5H.5351.../2520018 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing (2791/1 EGR valve sensor error). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
14 | South | 211577946 | 2025-07-01 12:07 | 0 | 5H.5351.../2520015 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing (637/5 crank shaft sensor error). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
15 | South | 211577933 | 2025-07-01 12:01 | 0 | 5H.5351.../2520012 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | as per the customer complaint error code issue from the engine. after check the error code is showing (110/10 coolant temperature sensor error). clear the error code and started the engine observed on running condition working found ok | closed | Mr. Anil Kumar H G
1 | East | 211591492 | 2025-09-01 14:54 | 125.4 | 4H.8041.../2420547 | Starting issue Call by customer Name - Pintu Kumar Mobile No - 9523107477 | Task Start | Nishant Kumar. | 50 | Found Emergency switch on, Operator was not avialable on site so customer had open the SR | CLOSED | Prabhakar Kumar
2 | East | 211591228 | 2025-09-01 13:58 | 10 | GP3.8301.../2420336 | under frequency Alarm Issue Call By Customer Name :- Samaresh Kumar Singh Mobile No :-9608839908 | Task Start | Sanjay Sahani | 5.5 | Update pending | CLOSED | Prabhakar Kumar
3 | East | 211591099 | 2025-09-01 13:28 | 125.4 | 4H.8041.../2420938 | Alarm issue Call By Customer Name :-Shobit Kumar Number :-7549039250 | Task Start | Shantidoot Infra Services Pvt. LTd. |  | Visit pending | OPEN | Prabhakar Kumar
4 | East | 211591031 | 2025-09-01 13:11 | 25 | GP3.8702.../2420623 | Loading problem | Task Start | M/s. Singha Filling Station |  | Visit pending | OPEN | Prosanjit saha
5 | East | 211590297 | 2025-09-01 11:25 | 125.4 | 4H.8041.../2420385 | Starting/Stopping Issue | Task Start | Baazar Style Retail Private Limited |  | Visit pending | OPEN | Prosanjit saha
6 | East | 211589962 | 2025-09-01 11:04 | 5.5 | CC1.1013.../2400381 | Starting Issue Call By KGD Name :-Alisha Mobile No :- 9647904206 | Open | Mr. Monaj singh |  | Update pending | OPEN | Prosanjit saha
7 | East | 211587976 | 2025-08-01 17:40 | 82.5 | 5H.8901.../2420499 | Amber Lamp On Alarm Call By Customer Name :- Koushal Kishor Singh Mobile No.:- 6909604331 | Open | Tojo Karga (IPS) |  | visit pending | OPEN | Subhrajit Roy
8 | East | 211587366 | 2025-08-01 16:15 | 15 | GP3.8501.../2420918 | Red Lamp ON Alarm Issue Call By Customer Name - Manoj Kumar Number - 8709819701 | Closed | BITTU KUMAR JEE | 43 | SE found alarm "Emergency ON" then he cleaned panel side emergency connector and refitted properly. Issue resolved. | CLOSED | Prabhakar Kumar
9 | East | 211585870 | 2025-08-01 15:28 | 58.5 | T4.8941.../2420535 | Starting issue Call By Customer Name :- Mobile No :-9988368785 | Closed | Adi Sports India Pvt. Ltd. | 43 | DG was crancking but not starting due to air lock issue, then SE release air and crank DG started | CLOSED | Prabhakar Kumar
1 | North | 211591231 | 2025-09-01 13:59 | 125.4 | 4H.8041.../2420146 | Starting Issue Call By Customer Name :- Vikaram Singh No :- 9557420142 | Task Start | Prerna Threads Private Limited | 114 | Battery discharge, found charger output ok but battery not charge then send the battery for testing | Open | Kapil Solanki
2 | North | 211591073 | 2025-09-01 13:21 | 58.5 | T4.8941.../2422907 | Trip_Genset_Low_Voltage | Cancelled | UNIVERSAL TECHNOLOGY AND SERVICES |  | Cancelled-Double SR open | Cancelled | Kapil Solanki
3 | North | 211590953 | 2025-09-01 13:01 | 125.4 | 4H.8041.../2420375 | Electrical Problems | Task Start | Neolite Z. K. W. Lighting pvt. Ltd. | 45 | Low Electrolite level & DEF level so, topup required | Open | Kapil Solanki
4 | North | 211590765 | 2025-09-01 12:35 | 125.4 | 4H.8041.../2420429 | Starting issue Called by customer Name : Nawab Contact no : 7669897076 | Task Start | NCR Concrete Private Limited | 317 | Today SE visit | Open | Kapil Solanki
5 | North | 211590709 | 2025-09-01 12:31 | 82.5 | 5H.8901.../2420531 | Amber Lamp ON Alarm Issue Call By Customer Name - Ravi Kumar Number - 9812766500 | Task Start | Kewal Singh | 49 | Under Speed Alarm occurred due to over-load(76 KW);after reduce the load,DG was running fine | Closed | Ved Prakash Gupta
6 | North | 211590621 | 2025-09-01 12:18 | 82.5 | 5H.8901.../2320105 | Starting Issue . Call By Customer. Name :- Shalin Mobile No :-9456706942 | Task Start | ST. Francisi Hospital | 87 | Customer not allow for working on DG | Open | Sudhir Awasthi
7 | North | 211590567 | 2025-09-01 12:14 | 125.4 | 4H.8041.../2420206 | Starting/Stopping Issue | Task Start | SHAMAN VIHAR APARTMENT | 13 | Low def level, found only 26% topup the def 100% issue resolve | Closed | Kapil Solanki
8 | North | 211590523 | 2025-09-01 12:08 | 57 | T4.8941.../2320147 | Leakage Issue | Task Start | Arihant Machinery Store | 210 | update pending | Open | Kapil Solanki
9 | North | 211590427 | 2025-09-01 11:59 | 125.4 | 4H.8041.../2320114 | Starting/Stopping Issue | Closed | NEW GAGAN GENERATOR.. | 1055 | Found water in fuel rusting in tank- required tank cleaning | Open | Kapil Solanki
10 | North | 211590426 | 2025-09-01 11:56 | 250 | F6.8841.../2420091 | Genset Trip | Task Start | Dr.Rakesh Khare | 18 | Low Voltage alarm found and set from AVR Found 385v after set 415v | Closed | Sudhir Awasthi
11 | North | 211590416 | 2025-09-01 11:52 | 30 | 3H.8902.../2420917 | Starting/Stopping Issue | Task Start | DESAI | 2 | Under speed alarm Check the fuel line found ok, the reset the alarm, start the dg found running ok | Closed | Kapil Solanki
12 | North | 211590261 | 2025-09-01 11:20 | 125.4 | 4H.8041.../2420923 | Ad Blue Issue Call By Customer Name :- Dr. Sourabh Prabahkar Mobile No :-8549000070 | Task Start | Prabhakar Hospital | 79 | SPN/FMI-516166/0 & 1761/16 Related to hot shutdown & AdBlue Level Low,Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
13 | North | 211590205 | 2025-09-01 11:14 | 125.4 | 4H.8042.C4../2420686 | Adblue level not proper sow | Task Start | Sunheri Industries | 22.18 | SPN/FMI-1761/16 & 3031/14 , Tool not connected ; Flash the ECU,issue resolved | Closed | Ved Prakash Gupta
14 | North | 211589953 | 2025-09-01 11:00 | 500 | DV8.8501.C4../2420090 | Fuel leakage | Task Start | Ping Engineers India Pvt. Ltd. | 59 | Fuel Leakage found on leak-off pipe so wrapped the same with Tape & resolve the Issue | Closed | Ved Prakash Gupta
15 | North | 211589631 | 2025-09-01 09:28 | 250 | F6.8841.../2320039 | Automation Issue Call By Customer Name :-Rahul Mobile No :- 8454097416 | Closed | Kendriya Vihar II Apartments Owners Association | 132 | SPN/FMI 3031/14, 1761/16 reset the alarm topup the def | Closed | Kapil Solanki
16 | North | 211589623 | 2025-09-01 09:21 | 250 | DV8.9840.../2420009 | Starting Issue Call By Customer Name :-Anuj Kumar Mobile No :-8527090334 | Task Start | METAFLEX DOORS INDIA PRIVATE LIMITED. | 6 | GAS ENGINE- Initial Pressre_5.1kpa after set through ZPR 4.3kpa, found jerk load on DG, and check after found throttle valve connector damage so today replace | Closed | Kapil Solanki
17 | North | 211589598 | 2025-09-01 09:18 | 57 | T4.8941.../2420137 | Starting/Stopping Issue | Closed | Arihant Machinery Store | 135 | Battery discharge, Low electrolite level, Service due -update pending | Open | Kapil Solanki
18 | North | 211588102 | 2025-08-01 17:54 | 125.4 | 4H.8041.../2420019 | VOC-ENGINE OVERHEATING DUE TO CHOKING OF RADIATOR Customer Name -Chander Shekhar Customer Number -9141142915 Mode- SR Generated through CDI calling. | Closed | Rahee Infratech Ltd. | 3733 | SPN/FMI 4095/1, 4339/2 DM & SM not working | Open | Kapil Solanki
19 | North | 211587935 | 2025-08-01 17:36 | 125.4 | 4H.8041.../2320110 | BATTERY CHANGE | Task Start | Oceanica Infratech LLP. | 156 | Battery replace, due to battery defective | Closed | Kapil Solanki
20 | North | 211587857 | 2025-08-01 17:18 | 40 | 3H.8951.../2420246 | Starting/Stopping Issue | Closed | PUNJABI DHABA | 1.5 | update pending | Open | Gourav Sharma
21 | North | 211587828 | 2025-08-01 17:15 | 125.4 | 4H.8041.../2320086 | White Smoke issue Call By Customer Name :- ShivJi Mobile No :-9821993148 | Task Start | Total Construction | 2439 | Low def level, clear the fault code issue resolve | Closed | Kapil Solanki
22 | North | 211587700 | 2025-08-01 16:55 | 250 | F6.8841.../2420135 | Error Code Issue Call By Service Dealer Name - Shalu Number - 7973080439 | Closed | Garg Builders and Promoters LLP | 180 | SPN/FMI-516166/0 & 3031/14 Related to hot shutdown & High AdBlue Level,Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
23 | North | 211587288 | 2025-08-01 15:59 | 160 | 6H.8475.../2420260 | Voltage Fluctuation | Task Start | MEGAMIND ENGG.PROJECT | 12 | Customer not give the load, but SR close in the system | Closed | Kapil Solanki
24 | North | 211587224 | 2025-08-01 15:47 | 0 | 4H.8042.C4../2420345 | HUNTING PROBLEM | Task Start | Jakson & Company |  | Today SE visit | Open | Gourav Sharma
25 | North | 211585900 | 2025-08-01 15:32 | 125.4 | 4H.8041.../2421002 | VOC-FEEDPUMP STICKY alarm problem starting problem is facing. Customer Name -Manjeet Customer Number -8053438593 Mode- SR Generated through CDI calling. | Task Start | S R S Engg Co | 49.5 | SPN/FMI-522120/19,522122/19,3391/14,3224/2 ; Cleared the code & flash the ECU,after that run the DG for 30 minutes on Load,Also DG running on overload,same educated to customer,Issue resolved | Closed | Ved Prakash Gupta | Under obs
26 | North | 211585898 | 2025-08-01 15:31 | 125.4 | 4H.8042.C4../2420057 | current frequency issue Call By Customer Name :- Virendra . Mobile No :- 8779904318 | Closed | SHUBHAM RMC SERVICES PRIVATE LIMITED | 825 | Customer side issue- Inverter not working | Closed | Sudhir Awasthi
27 | North | 211585701 | 2025-08-01 15:25 | 20 | GP3.8601.../2420208 | Maintenance Due Alarm Call By Customer Name :- Parvesh . Mobile No :- 9814020720 | Cancelled | Winstic Insurance Brokers India Pvt. Ltd. | 35.91 | Under Cancellation-Complaint rectified on call | Cancelled | Ved Prakash Gupta
28 | North | 211585702 | 2025-08-01 15:22 | 500 | DV8.8501.C4../2320073 | VOC-ECU - MALFUNCTIONING/FLASHING/TAMPERINGMALFUNCTIONING/FLASHING/TAMPERING Customer Name -Brijesh Customer Number -7619976285 Mode- SR Generated through CDI calling. | Task Start | A C POLYCOATERS PRIVATE LIMITED | 142 | After Stop the DG;Fail to Stop Alarm occurred on controller;Controller found faulty;will replace the same | Open | Ved Prakash Gupta
29 | North | 211585348 | 2025-08-01 15:14 | 20 | GP3.8601.../2420427 | Starting/Stopping Issue | Closed | JaiKrishan Filling Station. | 143 | SPN 2802/4, 2791/14 Found battery voltage with charger found 13.6v checked control wiring and found relay board wire 2E5/2E loose tightness the same issue resolve | Closed | Gourav Sharma
30 | North | 211583746 | 2025-08-01 14:54 | 1000 | DV8.8502.C4../2420001. & 2420002. | Loading issue Called by customer Name : Magan Number: 7500568862 | Task Start | TULIP IVORY RWA | 116 | Low fuel level alarm, found on controller 10% open the connector then again refitted show the fuel level 60% at actual | Closed | Kapil Solanki
31 | North | 211583656 | 2025-08-01 14:31 | 40 | 3H.8951.../2420770 | Red lam Shut down Alarm issue Call By Customer Name- Sanjit .. Mo.No.- 7786839601 | Task Start | BN. Engineering Co. | 2 | Emergency alarm, Under speed alarm reset the alarm, trial on load found after no issue | Closed | Kapil Solanki | Fault check
32 | North | 211583590 | 2025-08-01 14:17 | 500 | DV8.8501.C4../2420043 | Error code issue | Closed | Nikvin Healthcare India Pvt. Ltd. | 66 | SPN/FMI-1761/16 Low AdBlue Level & Battery terminal found rusty & faulty;Top-up & clean respectively & advised to customer to replace the terminals immediatly | Closed | Ved Prakash Gupta
33 | North | 211583588 | 2025-08-01 14:16 | 82.5 | 5H.8901.../2320084 | Starting Issue And Emergency Stop Alarm Call By Customer Name- Sahil Rana Mo.No.- 7300651325 | Closed | AMBITION RETAILS ALLIANCE LLP | 3171 | Emergency switch faulty Element defective now bypass the emergency,- Today replace | Open | Kapil Solanki
34 | North | 211583582 | 2025-08-01 14:12 | 125.4 | 4H.8041.../2420806 | Starting/Stopping Issue | Closed | Vivek Enterprises. | 3 | Starting issue due to Battery Voltage Low(11.4),Battery Charger was connected with mains but not getting voltage so get mains supply from different point,after charging,High AdBlue level alarm (3031/14) shown on controller,Flash the ECU,issue resolved | Closed | Ved Prakash Gupta
1 | West | 211570067 | 2025-04-01 16:01 | 40 | 3H.8951.../2320042 | Krm unit not working properly | Closed | Shree Ram Heights Co. Op. Housing Society Ltd. | 17.58 | KRM is not providing the proper data but network issue in this area.
2 | West | 211569569 | 2025-04-01 14:54 | 500 | DV8.8501.C4../2420136 | Leakage Issue | Closed | ESSEN LANDMARK | 25 | leakage from pre fuel filter so changed the filter body.
3 | West | 211568852 | 2025-04-01 13:16 | 15 | GP3.8501.../2420226 | Electrical Problems | Closed | Dynamic Corporation | 2.59 | Load was not shifting so replaced the contactor and issue resolved.
4 | West | 211568671 | 2025-04-01 12:48 | 40 | 3H.8951.../2421106 | Leakage Issue | Closed | Satisfaction. | 182 | Oil leakage from breather pipe so tightened the same .
5 | West | 211568455 | 2025-04-01 12:11 | 500 | DV8.8501.C4../2420138 | Tripping issue Call By Customer Name :- Suhas . Mobile No :-8550995874 | Closed | Kolte-Patil Integrated Townships Limited | 14 | 520168,4- Device Library - Batt Low - Bank 2 - Voltage Below Normal,517168,4- Dev system voltage-Voltage Below Normal Tightened the battery & charging alternator connections. Refited the ECU & DCU Connectors. Cleared the DTC.
6 | West | 211568417 | 2025-04-01 11:59 | 250 | F6.8841.../2420120 | Starting/Stopping Issue | Closed | Future Rock Technologies | 926 | SPN/FMI-4095/2(NOx limits exceeded due to Interrupted Diesel Exhaust Fluid Dosing-Erratic, Intermittent, or Incorrect),4389/2(SCR Monitoring - Dosing Module - Bank 2 - Erratic, Intermittent, or Incorrect) The engineer visited the spot and checked the DEF and found that there were oil particles in the DEF tank, so the DEF tank was cleaned. The engineer recommended the use of Kirloskar DEF.
7 | West | 211568183 | 2025-04-01 11:03 | 625 | DV0.8501.C4../2420129 | bagli relay faulty | Closed | Malpani Parks Indore Private Limited | 4 | Customer complaint: Genset is sometimes not cranking. So engineer visited on site and tightened the all points and connector of interfacebox and problem has been resolved.
8 | West | 211421394 |  | 15 | GP3.8006.PB../2320126 | Starting issue | Open | Nashik Auto Ancillaries | 200 | Sweep Stuck alarm DTC 240/7 SE changed the ECU & Engine wiring because connector & Pin found broken & bend. Replaced the Fuel pump but issue was same. Interchanged the controller with another dg controller.
1 | East | 211595170 | 2025-10-01 14:00 | 15 | GP3.8501.../2420678 | Starting Issue Call By Customer Name :- Sanjiv Kumar Mobile No :-9152001011 | Task Start | Hindustan Pencil Pvt. Ltd. | 76 | There was no issue in DG, customer side atutomation issue due to loose connection of mains sensing supply to controller. | CLOSED | Prabhakar Kumar
2 | East | 211594839 | 2025-10-01 12:41 | 20 | GP3.8604.../2420157 | STARTING ISSUE | Open | Reliance Jio Infocomm Limited | 2 | After restoring the engine and flashing contaminated lube oil properly then operated DG for the 15-20 min then checked by dipstick found coolant mixed with lube oil. Customer is so frustrated, want engine replacement. | OPEN | Prabhakar Kumar
3 | East | 211593974 | 2025-10-01 10:01 | 30 | 3H.8902.../2420892 | Starting Issue Call By Customer Name :- Rawat Ji Mobile No :-8637507378 | Task Start | LINKCON ENGINEERING PRIVATE LIMITED |  | Update pending at ASE end | OPEN | Ujjwal Das
4 | East | 211593907 | 2025-10-01 09:51 | 15 | GP3.8501.../2420615 | Load Issue Call By Customer Name ;- Bittu Soni Mob No ;- 8794016784 | Cancelled | M/S Marcofed Heningkunhlwa | 121 | SR Cancelled- load side issue no issue in DG | CANCELLED | Ujjwal Das
5 | East | 211592796 | 2025-09-01 18:05 | 160 | 6H.8475.../2420166 | Starting/Stopping Issue | Closed | M/s. Fifeo Energy Station | 188 | There was low adblue level so fault code SPN-4365 FMI-2, SPN 520527 FMI-18 found in ikonnect so top up the adblue and clesred fault code. | CLOSED | Ujjwal Das
6 | East | 211592791 | 2025-09-01 18:03 | 30 | 3H.8902.../2420815 | Alternator Fan Issue Email by OEM Name - Abhay Mishra | Open | Dinesh Chandra R. Agrawal Infra Con Pvt. Ltd. | 111 | Update pending at ASE end | OPEN | Ujjwal Das
7 | East | 211591099 | 2025-09-01 13:28 | 125.4 | 4H.8041.../2420938 | Alarm issue Call By Customer Name :-Shobit Kumar Number :-7549039250 | Task Start | Shantidoot Infra Services Pvt. LTd. | 240 | SR cancelled- low adblue regarding alarm resolved on telephonic communication issue resolved | CANCELLED | Prabhakar Kumar
8 | East | 211587976 | 2025-08-01 17:40 | 82.5 | 5H.8901.../2420499 | Amber Lamp On Alarm Call By Customer Name :- Koushal Kishor Singh Mobile No.:- 6909604331 | Open | Tojo Karga (IPS) | 27 | Update pending at ASE end | OPEN | Ujjwal Das
9 | East | 211564435 | 2025-03-01 14:27 | 125.4 | 4H.8041.../2420715 | Starting Issue Call by Customer Name : Vikram .. No : 9079902118 | Completed | GANPATI BHARAT PVT LTD | 268 | DG send in GOEM and its PRV counts are increasing frequently so decided to change common rail but also same problem, under inspection | OPEN | Ujjwal Das | Service History
10 | East | 211594002 | 2025-10-01 10:09 | 20 | GP3.8601.../2420685 | Red lamp on Alarm Call By Customer Name - Akhilesh Prasad Number - 9778074795 | Task Start | VEERMAN ENTERPRISES | 28 | Customer required service no issue in DG | CLOSED | Ujjwal Das
11 | East | 211593936 | 2025-10-01 09:57 | 250 | F6.8841.../2420114 | Starting/Stopping Issue | Task Start | S. A. Trading | 567 | Update pending | OPEN | Prosanjit saha
12 | East | 211591920 | 2025-09-01 15:45 | 250 | F6.8841.../2420169 | Error code | Task Start | MAHIMANANDA MISHRA | 44 | SPN:516166/0 code alarm popuped on display after clearing DTC and flashing ECU issue resolved also educated customer not to hot shutdown DG. | CLOSED | Ujjwal Das
13 | East | 211591031 | 2025-09-01 13:11 | 25 | GP3.8702.../2420623 | Loading problem | Cancelled | M/s. Singha Filling Station | 22 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Prosanjit saha
14 | East | 211590297 | 2025-09-01 11:25 | 125.4 | 4H.8041.../2420385 | Starting/Stopping Issue | Closed | Baazar Style Retail Private Limited | 46 | SPN:516166/0 code alarm popuped on display after clearing DTC and flashing ECU issue resolved also educated customer not to hot shutdown DG. | CLOSED | Prosanjit saha
1 | North | 211595164 | 2025-10-01 13:57 | 62.5 | T4.8941.../2420261 | voltage fluctuation Call by service dealer name - preeti no - 8427103008 | Completed | Amson Transformers | 577 | Voltage Fluctuation issue ;Power Factor minimize(0.3) when 3 hp & 5 hp 3 phase Motor applied as load ; as per RRT suggestion ; Load will analysis with IEC Team | Open | Ved Prakash Gupta | KRM load check
2 | North | 211595149 | 2025-10-01 13:57 | 82.5 | 5H.8901.../2320005 | Error code | Task Start | Noxon Blowers Pvt. Ltd. | 148 | SPN/FMI-6595/0;DNOX system monitoring;Check the AdBlue Line & Filter condition,found ok,DEF Injection found ok ; remove the code & resolve the Issue | Closed | Ved Prakash Gupta
3 | North | 211595059 | 2025-10-01 13:33 | 750 | DV2.8501.C4../2420043 | Tripping issue Call By Customer Name :- Hanumat Singh Mobile No :- 9690424866 | Task Start | BVG. India Ltd. | 40 | SPN/FMI 633/3 Check fuel line find ok the check the lifting pump found loose tightness the same issue resolve | Closed | Kapil Solanki
4 | North | 211595011 | 2025-10-01 13:20 | 30 | 3H.8902.../2420277 | Starting Issue Call By Customer Name :- Kapil Giri Mobile No :- 9410219607 | Task Start | Usha Fuel Centre. | 84 | found 2C wire MCB not passing dc volt check 2C wire of MCB is not tightness with MCB point and check dg set start & issue resolve | Closed | Kapil Solanki
5 | North | 211595004 | 2025-10-01 13:18 | 125.4 | 4H.8041.../2320035 | Load Issue Call By Customer Name ;- Chirag Mob no ;- | Task Start | VINKAY TEXTILES [P] LTD | 291 | Customer panel load cable thimble burnt after replace the thimble & topup the Def then start the DG running fine well | Closed | Kapil Solanki
6 | North | 211594967 | 2025-10-01 13:08 | 750 | DV2.8501.C4../2320005 | Electrical Problems | Task Start | BHARAT RASAYAN LTD | 413 | Canopy Emergency Stop activated;Bypass the NC & resolve the issue | Closed | Ved Prakash Gupta
7 | North | 211594825 | 2025-10-01 12:34 | 40 | 3H.8951.../2421252 | Starting/Stopping Issue | Task Start | HOTEL SHAN AT ULEY |  | Under Cancellation | Cancelled | Ved Prakash Gupta
8 | North | 211594790 | 2025-10-01 12:27 | 125.4 | 4H.8041.../2420142 | Electrical Problems | Task Start | Uttarakhand Jal Vidyut Nigam Limited U. J. V. N. | 3 | Battery voltage low, battery charger connection not given from the mains supply | Closed | Sudhir Awasthi
9 | North | 211594146 | 2025-10-01 10:53 | 500 | DV8.8501.C4../2420058 | Canopy Stop Alarm. Call By Customer . Name :- Rohit Kumar Mobile No :-9920868795 | Task Start | Regal Emporia Infratech Pvt. Ltd. | 76 | checked and Replaced Emergency switch and fuse 30 Amps, start the Engine checked All parameter proper working. | Closed | Kapil Solanki
10 | North | 211594139 | 2025-10-01 10:52 | 500 | DV8.8501.C4../2420022 | Trip_Genset_Low_Voltage | Task Start | BVG. India Ltd. | 104 | Wrong report- DG running ok | Closed | Kapil Solanki
11 | North | 211594079 | 2025-10-01 10:37 | 750 | DV2.8501.C4../2320024 | Voltage Fluctuation | Task Start | BHARAT RASAYAN LTD | 321 | Genset Under Volatage due to in sync pannel to AVR AL1 wire found loose so tightened the same & rsolve the Issue | Closed | Ved Prakash Gupta
12 | North | 211594071 | 2025-10-01 10:33 | 82.5 | 5H.8901.../2420072 | Starting Issue Call By Customer Name :-Sanjay Mobile No :-8527629951 | Task Start | St. Karens High School |  | Under Cancellation | Cancellation | Kapil Solanki
13 | North | 211594013 | 2025-10-01 10:16 | 125.4 | 4H.8041.../2320059 | Electrical Problems | Closed | Sudh Investments Private Limited | 278 | To take KG640C R02 Controller observations | Closed | Kapil Solanki
14 | North | 211593967 | 2025-10-01 09:59 | 15 | GP3.8501.../2421769 | Starting/Stopping Issue | Task Start | VD. Power Solution | 34 | Battery terminal clean and then check DG set panel MCB load cable lossing problem, tightness the cable issue resolve trial on load (16amp) running properly. | Closed | Sudhir Awasthi
15 | North | 211593927 | 2025-10-01 09:52 | 125.4 | 4H.8041.../2420690 | Voltage Fluctuiation Call By Customer Name :- Deepanshu Gupta Mobile No :- 9818380707 | Task Start | Jaishree Infra | 176 | 2no. Of motors 50HP start engine working on loud testing R phase 67 y phase 87 and B phase 91 loud testing | Closed | Kapil Solanki | KRM data
16 | North | 211593923 | 2025-10-01 09:52 | 58.5 | T4.8941.../2422913 | Starting Issue Call By Customer Name :-ROHIT JI Mobile No :-9953148727 | Task Start | R.S ENTERPRISES | 3.2 | Starting Issue due to 4 No. wire found loose on controller so tightened the same & resolve the issue | Closed | Ved Prakash Gupta | GOEM issue
17 | North | 211593892 | 2025-10-01 09:42 | 15 | GP3.8501.../2421369 | Starting Issue. Call By Customer. Name:- D.B SINGH .. Mobile No.:- 8376048045 | Task Start | D B SINGH | 4.49 | Starting Issue with under speed alarm;check the fuel line ;no such issue found so reset the same & resolve the issue | Closed | Ved Prakash Gupta
18 | North | 211593867 | 2025-10-01 09:29 | 82.5 | 5H.8901.../2420011 | Starting Issue Call By Customer Name :-Pawan Gupta No :- 9918982839 | Task Start | Bhavani Enterprises | 108 | SPN/FMI 100/1, Low oil pressure, Low def level & Coolant level topup the def issue resolve flash the file | Closed | Sudhir Awasthi | KRM check
19 | North | 211592978 | 2025-09-01 19:46 | 20 | GP3.8601.../2421121 | Automation issue Called by customer Name : Shabir Number: 8430299043 | Task Start | THE MUSLIM EDUCATION WELFARE SOCIETY | 3 | Customer side panel issue- Negative command not come proper | Closed | Sudhir Awasthi
20 | North | 211592657 | 2025-09-01 17:37 | 57 | T4.8941.../2320217 | We not receive notifications for KRM | Closed | Sonu Tools | 236 | update pending | Open | Kapil Solanki
21 | North | 211592529 | 2025-09-01 17:16 | 200 | 6H.8435.../2320027 | Preventive Maintenance Call By Customer Name :- Rajeash Khana ... Mobile No :- 9891411486 | Closed | RAJESH KHANNA | 50 | Maintenance due alarm change the date issue resolve | Closed | Kapil Solanki
22 | North | 211592465 | 2025-09-01 17:03 | 30 | 3H.8902.../2421423 | AMF Panel not working,Main contractor issue Frist service due-501777 | Task Start | ICICI Bank Limited | 58.3 | DG mains contactor nutral point foulty, now need to be replace the mains contactor | Closed | Sudhir Awasthi
23 | North | 211592409 | 2025-09-01 16:49 | 20 | GP3.8604.../2420198 | INSTANCE ID:-100742275 SITE ID:- I-UE-GKPR-ENB-9091 CALL BY CUSTOMER// DG ISSUE:- DG STARTING PROBLEM NAME:- SHAILESH NUMBER:- 8299698446 | Task Start | Reliance Jio Infocomm Limited | 151 | ECU flash for the under voltage alarm | Open | Sudhir Awasthi
24 | North | 211592290 | 2025-09-01 16:30 | 25 | GP3.8702.../2420158 | Leakage Issue | Completed | Precision Building Contractor | 93 | Oil Leakage found due to oil filter found faulty so replace the same & resolve the issue | Closed | Ved Prakash Gupta
25 | North | 211592131 | 2025-09-01 16:01 | 5.5 | CC1.1013.../2400002 | Display issue Call By Customer Name :- Sandip Kumar Mobile No :- 9078505468 | Task Start | RANK SOLUTIONS SERVICES | 3 | Starting Issue due to 20A 2nd wire fuse found faulty so replace the same & Load Trial given,Issue resolved | Closed | Ved Prakash Gupta
26 | North | 211591787 | 2025-09-01 15:25 | 320 | F6.8802.../2320051 | Starting Issue Email By Customer Name:-Jeet Singh | Closed | Sri Dwarkadheesh Polymers Pvt. Ltd. | 99 | Start the Dg set and tested on load upto 127KW/50% load found set is running ok but after 127 kw customer start 150 HP motor of compressor engine over current | Closed | Gourav Sharma
27 | North | 211591800 | 2025-09-01 15:24 | 82.5 | 5H.8901.../2320092 | Inspection/Maintenance | Closed | KALYAN JEWELLERS INDIA LTD | 9 | found maintenance alarm showing after that Reset | Closed | Kapil Solanki
28 | North | 211591797 | 2025-09-01 15:23 | 30 | 3H.8902.../2421409 | Automation issue | Closed | Head Master Corporate Office C/o. Gillz Beauty & Wellness Pvt. Ltd. | 10 | Automation installed but from different pannel;Mains to Auto connection re-installed from different Point with Customer's Technician | Closed | Ved Prakash Gupta
29 | North | 211591790 | 2025-09-01 15:21 | 15 | GP3.8501.../2421389 | Cooling Fan issue | Open | Dynamics Solutions |  | Visit Pending | Open | Ved Prakash Gupta
30 | North | 211591729 | 2025-09-01 15:09 | 30 | 3H.8902.../2420568 | Voltage Fluctuation | Closed | Shuddowala Jail | 77 | mains voltage 1phase going up and down down, 270 volt to 280 volt now VMR setting over volt 300 done. | Closed | Sudhir Awasthi
31 | North | 211591391 | 2025-09-01 14:45 | 20 | GP3.8601.../2420928 | Electrical Problems | Task Start | SOLDIER ENGINEERS & CONTRACTORS | 52 | Main Contactor found burnt & Mains CT Transformer Neutral wire found burnt so advised customer to correct the Mains supply & replace the mains contactor on paid basis | Closed | Ved Prakash Gupta
32 | North | 211591357 | 2025-09-01 14:34 | 82.5 | 5H.8901.../2420719 | Diesel Leakage Issue Call By Customer Name :- Lalji Shingala Mobile No :-9722804342 | Closed | Vishal enterprise | 177 | Fuel Leakage due to Fuel filter assembly found broken so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
33 | North | 211591265 | 2025-09-01 14:19 | 30 | 3H.8902.../2420576 | Leakage Issue | Closed | Dudani Hospital & Rehabilitation Centre | 66 | found recovery bottle empty and water leakage from thermostat hose pipe, rectified the water leakage problem, tighten all hose clamps properly | Closed | Gourav Sharma
1 | NORTH | 211602883 | 13-01-2025 13:29 | 125 | F6.9840.../2420020 | Auto stop issue Call By Customer Name :- Nitesh Sharma Mobile No :-9311225211 | Open | B Continental Hotel |  | Visit pending | OPEN | Kapil Solanki
2 | NORTH | 211602791 | 13-01-2025 13:15 | 500 | F6.8843.C4../2420002 & 2420002 | Error code issue | Task Start | Brij Healthcare & Research Centre. | 127 | Maintenance alarm & Gen. Voltage asymmetry error code show, reset the alarm Educate the customer for unbalance load | Closed | Sudhir Awasthi
3 | NORTH | 211602670 | 13-01-2025 12:47 | 125.4 | 4H.8041.../2420168 | Canopy issue Call By Customer Name :-Raj Kumar Mobile No :-9149682470 | Open | M/s Source Dot Com Private Limited |  | Visit pending | OPEN | Kapil Solanki
4 | NORTH | 211602649 | 13-01-2025 12:45 | 125.4 | 4H.8041.../2421023 | Starting/Stopping Issue | Task Start | SAATWIC PARTNERS | 70 | Low adblue level topup the def issue resolve | Closed | Sudhir Awasthi
5 | NORTH | 211602647 | 13-01-2025 12:45 | 125.4 | 4H.8041.../2320031 | Paint quality is not good, rust observed at base of Dg with in 1 year. | Open | Edgetech Air System Pvt. Ltd. |  | Under Cancellation-Customer raised complaint as Paint issue on canopy | Cancelled | Ved Prakash Gupta
6 | NORTH | 211602405 | 13-01-2025 11:50 | 57 | T4.8941.../2420185 | Starting Issue Call By Customer Name :- Atmaram Mobile No :-9810571470 | Task Start | Jay Garud Gas Station | 37.11 | Battery voltage low, Battery charger connection ok, but customer side panel MCB off condition | Closed | Kapil Solanki
7 | NORTH | 211602277 | 13-01-2025 11:23 | 25 | GP3.8702.../2420404 | Low Fuel Issue Call By Customer Name :- Rajiv Mobile No :-9997083696 | Task Start | Public Works Department Uttar Pradesh | 36 | Air lock in fuel line, remove the air issue resolve | Closed | Sudhir Awasthi
8 | NORTH | 211602268 | 13-01-2025 11:20 | 125.4 | 4H.8041.../2420259 | Starting issue Call By Customer Name :- 9636320216 Mobile No :- Om Choudhary Barmer | Task Start | Cygnet Servises | 1821 | Update pending | OPEN | Gourav Sharma
9 | NORTH | 211602163 | 13-01-2025 10:59 | 500 | DV8.8501.C4../2420047 | Electrical Problems | Task Start | Shubh Industry | 210 | Canopy lamp not working due to Switch wire (2g) found loose so connected the same & issue resolved | Closed | Ved Prakash Gupta
10 | NORTH | 211602107 | 13-01-2025 10:52 | 125.4 | 4H.8041.../2320101 | Amber Lamp On Alarm and Starting issue Call By Customer Name :- Sanjay Gupta Mobile No :- 9711360601 | Task Start | ALTOS ENGINEERS PVT LTD. | 354 | SPN/FMI 1761/16, 3031/28 Low DEF level topup the DEF issue resolve | Closed | Kapil Solanki
11 | NORTH | 211602049 | 13-01-2025 10:26 | 160 | 6H.8475.../2320025 | Starting problem | Task Start | STRIKER INDUSTRIES PRIVATE LIMITED | 85.11 | B-Phase Under Voltage Alarm occurred due to fuse found faulty so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
12 | NORTH | 211602047 | 13-01-2025 10:25 | 750 | DV2.8501.C4../2420031 | ECU Alarm issue Call By Customer Name :- Sanddep Kumar Mobile No :- 8527171957 | Task Start | Jay Fe Cylinders Ltd. | 16 | Low def level topup the def issue resolve | Closed | Kapil Solanki
13 | NORTH | 211602035 | 13-01-2025 10:21 | 125.4 | 4H.8041.../2320103 | Starting issue | Task Start | SHRI BALAJI POLYMERS | 174 | Starting issue due to 2A supply fuse found faulty in Pannel so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
14 | NORTH | 211602025 | 13-01-2025 10:17 | 125.4 | 4H.8041.../2320063 | Alarm isshu | Task Start | ALSTEN ENTERPRISES | 193.58 | Under speed Alarm occurred found 2A6 fuse faulty in Pannel so replace the same &resolve the Issue | Closed | Ved Prakash Gupta
15 | NORTH | 211601997 | 13-01-2025 10:14 | 30 | 3H.8902.../2420248 | Genset Trip | Task Start | Parduman Singh Educational Social and Enviourmental Development Trust | 61 | SPN/FMI 100/1 Low oil pressure Connector remove & again refitted, Unbalance load R14, Y28, B12 Educate the customer for balancing the load | Closed | Sudhir Awasthi | KRM check
16 | NORTH | 211601982 | 13-01-2025 10:07 | 125.4 | 4H.8041.../2320006 | Coolant leakage | Task Start | Shri Balaji Enterprises | 173 | Coolant Leakage found on radiator top side due to clamp fond loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta
17 | NORTH | 211601966 | 13-01-2025 09:59 | 125.4 | 4H.8041.../2420096 | Low Speed Alarm and Starting issue Call By Customer Name :- Manoj Kumar Mobile No :- 8800573997 | Closed | Macro Plast Private Ltd | 116 | found DG set not starting fuel motor not working Due to fuel motor DC supply fuse is burnt After that change the new fuse issue resolve | Closed | Kapil Solanki
18 | NORTH | 211601950 | 13-01-2025 09:59 | 25 | GP3.8702.../2420291 | Leakage Issue | Task Start | C. Bikaner Misthan Bhandar. | 98 | Starting issue due to -ve supply wire to Battery found loose on self starter & electrolite level found low slightly ; Tightened & Top-up respectively & resolve the Issue | Closed | Ved Prakash Gupta
19 | NORTH | 211601943 | 13-01-2025 09:54 | 125 | F6.9840.../2420027 | UEGO sensor to be change | Task Start | GRAPECITY INDIA PVT LTD | 32 | Change the UEGO sensor | Closed | Kapil Solanki
20 | NORTH | 211601790 | 13-01-2025 08:42 | 58.5 | T4.8941.../2422111 | Power Supply Issue Call By Customer Name :- Mundra Kumari Mobile No :-8800283254 | Open | Himanshu Yadav. |  | Visit pending | OPEN | Kapil Solanki
21 | NORTH | 211601589 | 2025-12-01 20:54 | 125.4 | 4H.8041.../2420429 | Inspection/Maintenance | Open | NCR Concrete Private Limited |  | Cancelled-Problem solve in PM visit | Cancelled | Kapil Solanki
22 | NORTH | 211601433 | 2025-12-01 18:56 | 15 | GP3.8501.../2421377 | Red Lap Alram Issie Call By Csutomer Name ;- Mob No ;- ' | Open | BHARAT GENERAL STORE |  | Under Cancellation-Complaint rectified on call | Cancelled | Ved Prakash Gupta
23 | NORTH | 211601391 | 2025-12-01 16:35 | 125.4 | 4H.8041.../2320133 | Amber lamp alarm issue Call By Customer Name :- Udyan Number :- 9899294348 | Open | Jai Balaji Industries..... |  | Visit pending | OPEN | Sudhir Awasthi
24 | NORTH | 211601370 | 2025-12-01 15:10 | 25 | GP3.8702.../2320003 | Starting/Stopping Issue | Closed | Pawan Tanay Chem Plast Pvt. Ltd. | 186 | found MR wire of battery charger broken.replace broken wire, checked and tighten all connectors properly | Closed | Gourav Sharma
25 | NORTH | 211601298 | 2025-12-01 14:08 | 125.4 | 4H.8041.../2420171 | Starting Issue. call By Customer. Name:- Udit Tiwari. Mobile No.:- 9711169025 | Closed | Malrik Seam Export | 68 | SPN/FMI 1761/14, Low def level topup the def, Clear the fault code issue resolve | Closed | Kapil Solanki
26 | NORTH | 211601279 | 2025-12-01 13:37 | 45 | 3H.8951.../2421243 | Starting issue Call By Customer Name :- Ram Charn Mobile No :-7982975198 | Open | SETHI BUILDCON |  | Cancelled-SR open by mistake | Cancelled | Kapil Solanki
27 | NORTH |  | 2025-12-01 12:57 | 58.5 | T4.8941.../2421994 | Tripping issue Call By Customer Name :- Omveer Singh Number :- 7011204885 | Task Start | CHAUDHARY GENERATOR SERVICE | 232 | found battery negative terminal loose tightness the same and 2 Amp. fuse loose, spn 100 fmi 3 clear the fault code issue resolve | Closed | Kapil Solanki
28 | NORTH | 211601261 | 2025-12-01 12:39 | 125.4 | 4H.8041.../2420404 | Starting Issue And Load Issue Call By Customer Name :-Jayvir Singh Mobile No :-8193933394 | Task Start | Style Baazar Santragachi | 113 | Battery terminal break replace & tightness the same issue resolve | Closed | Sudhir Awasthi
29 | NORTH | 211601189 | 2025-12-01 11:43 | 40 | 3H.8951.../2320115 | Black Smoke Issue Call By Customer Name - Ajay Malik Number - 7774000009 | Closed | Nirmal Charitable Trust Regd | 88.38 | SPN/FMI-97/5 Water in fuel; No water traces in fuel line or tank;Load connected only as single phase & jerk load (25-35 amp) so same advised to customer to keep load connection corrected | Closed | Ved Prakash Gupta
30 | NORTH | 211600813 | 2025-12-01 09:16 | 500 | DV8.8501.C4../2420044 | ECU Alarm Call By Customer Name :- Punit Kumar Mobile No :- 7027920042 | Closed | Sikka Group | 316 | Update pending | OPEN | Kapil Solanki
31 | NORTH | 211600470 | 2025-11-01 17:56 | 320 | F6.8802.../2320023 | Trip_Genset_Low_Voltage | Closed | KSJN Chemicals Private Limited | 362 | found XDBK 1,2,3,&4 distribution connection loose tighten all connectors properly | Closed | Gourav Sharma
32 | NORTH | 211599869 | 2025-11-01 16:31 | 320 | F6.8802.../2420127 | Fan belt damage | Closed | Vikas Polyplast Pvt. Ltd. | 11.43 | Fan belt corner side defective, EDO for replace | OPEN | Gourav Sharma | Mail to QA
33 | NORTH | 211599478 | 2025-11-01 15:18 | 320 | F6.8802.../2320063 | Maintanance due alram | Closed | Vashisth Estates Limited | 584 | Found radiator chocked quation send to the customer | Closed | Kapil Solanki
34 | NORTH | 211599260 | 2025-11-01 14:27 | 125.4 | 4H.8042.C4../2420472 | ADD BLUE | Task Start | Jakson & Company | 0.01 | Adblue sensor faulty replace the same show the adblue level | Closed | Gourav Sharma
35 | NORTH | 211599203 | 2025-11-01 14:13 | 30 | 3H.8902.../2420684 | Electrical Problems | Closed | Darshan Power Solutions | 1268 | Maintenance due alarm reset the alarm issue resolve | Closed | Kapil Solanki
36 | NORTH | 211599188 | 2025-11-01 14:10 | 30 | 3H.8902.../2420679 | Electrical Problems | Closed | Darshan Power Solutions | 1307 | Maintenance due alarm reset the alarm issue resolve | Closed | Kapil Solanki
37 | NORTH | 211599068 | 2025-11-01 13:40 | 40 | 3H.8951.../2320109 | Starting Issue Call By Customer Name :- Satish Kumar Mobile No :- 8803349159 | Task Start | Jammu Kashmir Cricket Association |  | SPN/FMI-637/2 Starting issue due to -ve supply wire to Battery found loose on self starter & electrolite ; & resolve the Issue | Closed | Ved Prakash Gupta
38 | NORTH | 211598859 | 2025-11-01 13:01 | 125.4 | 4H.8041.../2420247 | Starting Issue Call By Customer Name :- Vicky Chaudhary Mobile No :- 9891723444 | Task Start | SHARMA ENTERPRISES | 99 | Self starter defective, coil is burnt give for repairing | OPEN | Kapil Solanki | KRM check
39 | NORTH | 211598871 | 2025-11-01 12:57 | 0 | DV8.8508.C4../2420004 | NO COOLANT PRESSURE | Closed | Jakson & Company | 0.01 | Wiring & controller programming update | Closed | Gourav Sharma
40 | NORTH | 211598819 | 2025-11-01 12:56 | 160 | 6H.8475.../2420147 | 5161.FM10 code issue | Closed | ADITYA LADIA S/O RAJINDER KUMAR LADIA | 90 | SPN/FMI-5461/0 ; Flash the ECU with latest version & run the DG on load,issue resolved | Closed | Ved Prakash Gupta | Under obs
41 | NORTH | 211598834 | 2025-11-01 12:51 | 125.4 | 4H.8041.../2420825 | Oil leakage issue Call By Customer Name - Sanjeev .. Number - 9811608525 | Closed | BANSAL ASSOCIATES | 1280 | found leakage from the turbo charger drain pipe joint gasket need to be replace and also found leakage from the tappet housing required k sealant for leakage stop | OPEN | Kapil Solanki
42 | NORTH | 211598808 | 2025-11-01 12:48 | 125.4 | 4H.8042.C4../2420480 | CAM SENSOR FALTY COMMON RAIL DEFECTIVE | Task Start | Jakson & Company | 0.1 | Common rail & Cam sensor faulty replace the same | Closed | Gourav Sharma
43 | NORTH | 211598833 | 2025-11-01 12:48 | 0 | DV8.8508.C4../2420007 | COOLENT PRESSURE SWITCH | Closed | Jakson & Company | 0.02 | Wiring & controller programming update | Closed | Gourav Sharma
44 | NORTH | 211598781 | 2025-11-01 12:43 | 250 | F6.8841.../2320046 | voltage fluctuation Call By Customer Name :-Ram Pratab Mobile No :- 9625865970 | Closed | Sobha Ltd. | 85 | Customer side panel issue | Closed | Kapil Solanki
45 | NORTH | 211598758 | 2025-11-01 12:35 | 125.4 | 4H.8041.../2420778 | Starting issue Call by customer Name: Prashant Number: 9639100451 | Closed | Shree Ram Industries. | 609 | Supply module not working replace the same issue resolve | Closed | Sudhir Awasthi | Failed part
46 | NORTH | 211598406 | 2025-11-01 11:29 | 20 | GP3.8601.../2420798 | Umber lamp on alarm issue Call by customer Name: Avdesh Yadav Number:7905246982 | Closed | HARI BANDHU TRUST | 8 | Update pending | OPEN | Sudhir Awasthi
47 | NORTH | 211598306 | 2025-11-01 11:07 | 15 | GP3.8501.../2421571 | Remote start and remote stop | Closed | ARYA PAINT & HARDWARE STORE | 3.26 | fitment new VMR, 12VDC PLA 8 pin relay with base and start stop push button, 1 NO & 1 NC Element and box, after connection check dg set start and stop with push button and after mains EB supply dg off. | Closed | Ved Prakash Gupta
48 | NORTH | 211598251 | 2025-11-01 10:59 | 82.5 | 5H.8901.../2320021 | Red Lamp On Alarm Call By Customer Name :- Sachin Kumar Mobile No :-9811028157 | Closed | CRMK Select | 210 | SPN/FMI 100/3 high oil pressure fault refitted oil sensor connector by pass | OPEN | Kapil Solanki
49 | NORTH | 211597897 | 2025-11-01 09:22 | 82.5 | 5H.8901.../2320042 | Error code Issue Call By Customer Name :- Kashif Ahmad Mobile No :-8445820675 | Closed | M/S SWASTIK PESTICIDES LIMITED | 156 | SPN/FMI 6595/0 Urea cap rubber loose fitted the cap | Closed | Sudhir Awasthi
50 | NORTH | 211597055 | 2025-10-01 20:17 | 20 | GP3.8601.../2421061 | Tripping Issue Call By Customer Name - Anand Shankar Number - 9830952272 | Closed | Anand Shankar Mall. | 33 | Mains problem Supply problem | Closed | Gourav Sharma
51 | NORTH | 211596903 | 2025-10-01 18:28 | 58.5 | T4.8941.../2420316 | Starting Issue Call By Customer Name :- Kavender Singh Mobile No :- 9958790301 | Closed | Maaks Industries | 143 | Update pending | OPEN | Kapil Solanki
52 | NORTH | 211596873 | 2025-10-01 18:22 | 40 | 3H.8951.../2420639 | Trip_Genset_High_Voltage | Closed | NAV SHAKTI APARTMENT CGSH LTD. | 4.4 | Found Mains voltage high so DG trip | Closed | Kapil Solanki
53 | NORTH | 211596070 | 2025-10-01 17:05 | 320 | F6.8802.../2320081 | Load Issue Call By Customer Name :- Punit Gupta Mobile No :-8233536121 | Closed | G P AUTO INDUSTRIES | 121 | Under voltage alarm, Ecu flash after that issue resolve | Closed | Gourav Sharma
54 | NORTH | 211595984 | 2025-10-01 16:47 | 40 | 3H.8951.../2420266 | Genset Trip | Closed | Kamla eye foundation pvt ltd | 7.56 | Found overload from customer, so DG trip in auto command, genset is stop, Educate the customer maintain the load | Closed | Kapil Solanki
55 | NORTH | 211595933 | 2025-10-01 16:41 | 20 | GP3.8604.../2420102 | INSTANCE ID:-100740911 SITE ID:- I-RJ-ALWR-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-dg issue NAME-KISHAN NUMBER:-9024467214 | Task Start | Reliance Jio Infocomm Limited |  | Pending | OPEN | Gourav Sharma
56 | NORTH | 211595773 | 2025-10-01 16:10 | 500 | DV8.8501.C4../2420129 | Tripping Issue Call By Customer Name - Sunil Kumar Number - 8427280370 | Closed | S. S. Enterprises | 78 | SPN/FMI 523576/0, 4411/1, 4358/1 clear the error code issue resolve | Closed | Gourav Sharma | ECU fault and DEF lines need to check
57 | NORTH | 211595626 | 2025-10-01 15:45 | 160 | 6H.8475.../2420209 | Error Code Issue Call By Customer Name - Devendra Tyagi Number - 9258016233 | Closed | VINAYAK TRANSCO PRIVATE LIMITED | 8.4 | SPN/FMI 516166/0, 3031/14 reset the alarm | Closed | Kapil Solanki
58 | NORTH | 211595580 | 2025-10-01 15:33 | 125.4 | 4H.8041.../2420222 | Mobil Leakage Issue Call By Customer Name :- Avinash . Mobile No :- 9540023080 | Closed | SHIVALIK ENGG.WORKS | 390 | Found no leakage, Maintenance alarm & def alarm reset the alarm | Closed | Kapil Solanki
59 | NORTH | 211595329 | 2025-10-01 14:48 | 30 | 3H.8902.../2420576 | Hunting Issue Call By Customer Name :-Yaadran Mobile No :-8209871622 | Closed | Dudani Hospital & Rehabilitation Centre | 67 | Customer DG set install on 3rd Floor, crack on 2nd floor, so customer say DG set vibration | Closed | Gourav Sharma
60 | NORTH | 211595297 | 2025-10-01 14:44 | 320 | F6.8802.../2420169 | Alarm Issue Call By Customer Name :- Rajkumar Mobile No :-9871400025 | Task Start | KKM Engineering Solutions Pvt. Ltd. | 7 | SPN/FMI 4363/4 T6 sensor Check continuity found ok | Closed | Kapil Solanki | ECU fault check
61 | NORTH | 211595217 | 2025-10-01 14:29 | 25 | GP3.8702.../2420626 | Oil Leakage Issue Call By Customer Name :- Ajay Vishwakarma Mobile No :- 8736915911 | Closed | Pushpa Associates | 326 | update pending | OPEN | Sudhir Awasthi
62 | NORTH | 211595244 | 2025-10-01 14:25 | 125.4 | 4H.8041.../2420889 | Electrical Problems | Closed | M. S. R. Associates | 59 | SPN/FMI-1761/16 ; Low AdBlue Level ,not available on site ; advised customer to purchase & Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
63 | NORTH | 211595224 | 2025-10-01 14:13 | 40 | 3H.8951.../2420602 | Starting issue Call by customer Name: Purshottam Number:9314064102 | Closed | LNA Infra Projects Pvt. Ltd. | 14.16 | Battery low, Battery charger wire damage, replace with new wire charge the battery issue resolve | Closed | Gourav Sharma
1 | West | 211602886 | 13-01-2025 13:30 | 40 | 3H.8951.../2421179 | Battery Issue Call By Customer Name :- Rahul Tambe Mobile No :-9822606657 | Open | Axis Bank Ltd | 1 | The battery was stolen so it is needed.
2 | West | 211602861 | 13-01-2025 13:27 | 320 | F6.8802.../2420235 | Coolant Leakage Issue Email by GOEM Name - Ranjan Kowale | Task Start | Meta Arch Design Built | 33.2 | Coolant leakage from cylinder head.
3 | West | 211602703 | 13-01-2025 12:55 | 82.5 | 5H.8901.../2420276 | Error code issue Call By Service Dealer Name - Deepak Patil Number - 9158004571 | Task Start | Sangeeta Saree Centre | 60 | SPN/FMI-4384/1,6595/0,1761/16.Filled the DEF.
4 | West | 211602489 | 13-01-2025 12:07 | 250 | F6.8841.../2420415 | DEF LEVEL ISSUE | Task Start | Goel Power Engineers | LR | DEF level was not showing properly. So manually moved the float of DEF sensor up and down but no value of DEF level was changing in controller. So checked the power supply of sensor and found no power supply. Tightened 2B3 wire on 14RB1- RL3 and distribution block XDBK4 and solved the problem.
5 | West | 211601440 | 2025-12-01 17:27 | 125.4 | 4H.8042.C4../2420621 | Amber lamp Alarm Call by customer Name:Dhru ... no:7069995777 ; | Closed | AARIC INTERNATIONAL | 5.46 | SPN/FMI-516166/0(Hot shutdown alarm),Cleared the DTC & educated the customer.
6 | West | 211601373 | 2025-12-01 15:17 | 320 | F6.8802.../2420094 | Low Fuel Level Issue. Call By Customer. Name:- Nagnath Nanvare. Mobile No.:- 9850232412. | Closed | Sanvik Technologies. | 30 | Low coolant level in the reservoir tank so topup the coolant between min to max in reservoir tank.
7 | West | 211598487 | 2025-11-01 11:38 | 400 | DV8.8542.C4../2420011 | Starting Issue Call By Customer Name :- E.S. UNNIKRISHNAN Mobile No :-9979884155 | Closed | Baroda Hi-Tech Alloys Private Limited | 26.7 | The reservoir tank was empty but the radiator was completely full. No any leakage in cooling system. Topup the coolant in reservoir tank.
8 | West | 211597993 | 2025-11-01 10:03 | 82.5 | 5H.8901.../2420420 | Red Lamp Issue Email by KGD Name - HARSHADBHAI | Closed | Navadia Refines | 43 | 516166/0 and low adblue level. Topup the adblue and cleared the DTC.
9 | West | 211597875 | 2025-11-01 08:53 | 0 | GP3.8702.../2421286 | STARTING ISSUE | Task Start | JAKSON & COMPANY | LR | Error Code- Voltage not buildup The soldering of the main rotor and diode wire was damaged so votage was not coming from alternator.
10 | West | 211597873 | 2025-11-01 08:48 | 200 | 6H.8435.../2420222 | STARTING ISSUE | Task Start | Goel Power Engineers | LR | Problem of engine not starting. It was found that fuse 2A1 was burnt. On investigation it was found that the wire was shorted to the body.
11 | West | 211595707 | 2025-10-01 16:00 | 15 | GP3.8501.../2421223 | Starting Issue Call By KGD Name :- Ramish Chavahan Mobile No :- 9016803464 | Closed | SHETHWALA PETROLEUM | 3.31 | Phase reverse alarm Interchanged the R,Y,B wires on the MCB and the problem was solved
12 | West | 211594682 | 2025-10-01 12:07 | 20 | GP3.8601.../2421249 | Loading Issue Call By Customer Name :- Kashyap Vlnd Mobile No :- 9375286235 | Closed | AADHAR WHOLESALE CENTER | 29.24 | There was 150V voltage coming from R,Y and B wires relative to neutral. So the AVR was replaced and the problem was solved.
13 | West | 211593829 | 2025-10-01 08:35 | 500 | DV8.8501.C4../2420118 | ERROR ISSUE | Task Start | JAKSON & COMPANY | LR | No issue found at plant.
14 | West | 211602453 | 13-01-2025 12:01 | 30 | 3H.8902.../2422014 | Amber lamp alarm Issue Call By Customer Name - Rupesh KUMAR Mobile No -7099463471 | Task Start | BIGHNAHANTA CONSTRUCTION PVT. LTD. | 28 | SPN/FMI-2791/18,2791/6,5838/1 & 5838,1 Checked the EGR connector and refited it. Cleared the DTC. It is under observation.
15 | West | 211607769 | 15-01-2025 10:53 | 5.5 | CC1.1013.../2400733 | commissioning | Closed | Davinchi | LR | Engineer visited on site for commissioning the DG. Checked battery charger connections and leakage, no leakage found. Disconnected transit lock from DG.
16 | West | 211574043 | 2025-06-01 15:21 | 5.5 | CC1.1013.../2400543 | Engine Not Starting | Task Start | M. J. Enterprises.... | LR | Visit Pending.
17 | West | 211568861 | 2025-04-01 13:20 | 5.5 | CC1.1013.../2400668 | customer load not pass | Closed | Vighnahar Hospital | 4 | The power supply was in the neutral cable as the neutral cable was not connected to earthing.
18 | West | 211565344 | 2025-03-01 17:28 | 5.5 | CC1.1013.../2400593 | Starting Issue Email By KGD Name:-Poonam Shedage | Closed | Accurate Powertech India Private Limited | 1.14 | DC regulator charger 5.5KVA diesel failure. This communication is in the mail.
1 | East | 211602942 | 13/01/2025 13:53:22 | 400 | DV8.8542.C4../2420023 | Error issue Email By - Customer Name - Neeraj Mishra | Task Start | Mr. Ravindra Patel | 14 | Today SE will visit site | OPEN | Prabhakar Kumar
2 | East | 211602132 | 13/01/2025 10:48:46 | 20 | GP3.8601.../2420187 | Starting Issue Call By KGD Name- Neha Komkom Mo.No.- 9234456624 | Open | Jharkhand Sales Agencies Pvt. Ltd. | 54 | visit pending | OPEN | Prabhakar Kumar
3 | East | 211601584 | 2025-12-01 20:37 | 125.4 | 4H.8041.../2420652 | Protect Alarm Issue Call By KGD Name ;- Sanjay Mob No ;-9234456620 | Task Start | S.K ENTERPRISES | 52 | SE found 1761/17 low adblue level alarm in DM1 so topup the adblue and cleared the DTC issue restored also educated customer how to see urea level and maintain minimum 50% Adblue in tank | CLOSED | Prabhakar Kumar
4 | East | 211601117 | 2025-12-01 08:53 | 30 | 3H.8902.../2422023 | Starting Issue Call By Customer Name :-Satpal Sharma Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS |  | Update pending at ASE end | OPEN | Ujjwal Das
5 | East | 211599602 | 2025-11-01 15:50 | 160 | 6H.8475.../2420432 | Starting/Stopping Issue | Closed | V. Retail Ltd. | 22.5 | SE found 1761/17 low adblue level alarm in DM1 so topup the adblue and cleared the DTC issue restored also educated customer how to see urea level and maintain minimum 50% Adblue in tank | CLOSED | Prabhakar Kumar
6 | East | 211598932 | 2025-11-01 13:12 | 20 | GP3.8601.../2420650 | Starting issue Call by customer Name: Jahirul Islam Number:7002124310 | Closed | STATE BANK OF INDIA | 87 | Electric feed pump issue (more details required from SE) | CLOSED | Ujjwal Das
7 | East | 211598895 | 2025-11-01 13:05 | 58.5 | T4.8941.../2422210 | Starting issue Call by customer Name - Pintu Kumar Mobile No - 9523107477 | Closed | RAJESH KUMAR | 64 | Battery discharge due to customer running hrs is less, due to mains unavailabilty battery charger also fails to charge. After charging battery issue restored and started DG. | CLOSED | Prabhakar Kumar
8 | East | 211598585 | 2025-11-01 11:58 | 250 | F6.8841.../2420085 | Coolant Lekege Issue Call By Customer Name :- Sumant Kumar Mobile No :- 7903667490 | Closed | Ziqitza Health Care Limited. | 65 | SE found coolant leakage at water pump and thermostat byepass hose clamp loose after tighteing issue resolved | CLOSED | Prabhakar Kumar
9 | East | 211598234 | 2025-11-01 11:00 | 500 | DV8.8501.C4../2320004 | Starting Issue Call By Customer Name - Nitesh kumar Mo No -9572166785 | Task Start | Indian Potash Limited | 154 | starter motor defective, more detail required from SE (update prnding) | OPEN | Prabhakar Kumar
10 | East | 211596140 | 2025-10-01 17:13 | 45 | 3H.8951.../2421580 | Voltage issue | Closed | Powerline Industries | 3 | Line rejection- at time of trail found output voltage 424 V at 50 Hz so SE adjusted voltage by AVR to 415 V | CLOSED | Ujjwal Das
11 | East | 211595861 | 2025-10-01 16:27 | 82.5 | 5H.8901.../2420425 | Mobil Tank Issue Call By Customer Name :- Sangram .. Mobile No :-6002465552 | Closed | KALYAN JEWELLERS INDIA LTD | 1219 | SE found SPN 97 FMI 2 SPN 3031 FMI 1 then drained fuel from fuel filter found no water refitted connector after cleaning properly and cleared DTC by Ikonnect issue resolved. | CLOSED | Ujjwal Das
12 | East | 211594839 | 2025-10-01 12:42 | 20 | GP3.8604.../2420157 | STARTING ISSUE | Open | Reliance Jio Infocomm Limited | 0 | Line rejection- SPN 1210 FMI 8 Rack pos open alarm checked for continuity from ECU connector to FIP actuator connector found countinuity but found no voltage also few time its rack move but there was also no full 3 movement of rack then drops few drops of oil on rack then also same problem then decided to change the wire harness after that checked above point all found ok so due to defective wiring harness issue arise harness under EDO. | OPEN | Prabhakar Kumar
13 | East | 211594515 | 2025-10-01 11:47 | 20 | GP3.8604.../2420083 | OIL LEAKEGE | Task Start | Reliance Jio Infocomm Limited | 2 | After restoring the engine and flashing contaminated lube oil properly then operated DG for the 15-20 min then checked by dipstick found coolant mixed with lube oil. Customer is so frustrated, want engine replacement. | OPEN | Prabhakar Kumar
14 | East | 211593974 | 2025-10-01 10:01 | 30 | 3H.8902.../2420892 | Starting Issue Call By Customer Name :- Rawat Ji Mobile No :-8637507378 | Task Start | LINKCON ENGINEERING PRIVATE LIMITED |  | Update pending at ASE end | OPEN | Ujjwal Das
15 | East | 211592791 | 2025-09-01 18:03 | 30 | 3H.8902.../2420815 | Alternator Fan Issue Email by OEM Name - Abhay Mishra | Open | Dinesh Chandra R. Agrawal Infra Con Pvt. Ltd. | 111 | Postponed Visit - Due to Work load | OPEN | Ujjwal Das
16 | East | 211587976 | 2025-08-01 17:40 | 82.5 | 5H.8901.../2420499 | Amber Lamp On Alarm Call By Customer Name :- Koushal Kishor Singh Mobile No.:- 6909604331 | Open | Tojo Karga (IPS) | 27 | Update pending at ASE end | OPEN | Ujjwal Das
17 | East | 211602621 | 13-01-2025 12:35 | 20 | GP3.8601.../2420761 | Starting Issue Call By Customer Name :- MR. AKSHYA KUMAR Mobile No :-8249048100 | Task Start | M/S CHAND AUTOMOBILE LLP |  | Today SE will visit site | OPEN | Ujjwal Das
18 | East | 211602257 | 13-01-2025 11:23 | 20 | GP3.8601.../2421919 | VOLTAGE PROBLEM | Task Start | ELMECH ENGINEERS |  | Update pending | OPEN | Prosanjit saha
19 | East | 211601905 | 13-01-2025 09:42 | 10 | GP3.8301.../2420057 | Red Lamp On Alarm Issue Call By Customer Name :- Saurabh Rai Mobile No :- 7008755713 | Task Start | SAINIK MINING AND ALLIED SERVICES LIMITED |  | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das
20 | East | 211598784 | 2025-11-01 12:44 | 320 | F6.8802.../2420196 | Electrical Problems | Closed | Rockbay Foods Private Limited | 22 | 1761/16 (Low DEF level) after top up the DEF tank Issue resolved. | CLOSED | Ujjwal Das
21 | East | 211595772 | 2025-10-01 16:10 | 125.4 | 4H.8042.C4../2420118 | Amber Lamp Alam Issue Call By Customer Name :- NALINI . Mobile No :- 9178710101 | Closed | ANURAG INDUSTRY AQUA | 9 | SPN:516166/0 code alarm popuped on display after clearing DTC and flashing ECU issue resolved also educated customer not to hot shutdown DG. | CLOSED | Ujjwal Das
22 | East | 211594510 | 2025-10-01 11:47 | 15 | GP3.8501.../2420195 | Excessive Smoke | Task Start | BIRAJA CONSTRUCTION | 632 | SE attend the site but no abnormal smoke found, Smoke was normal and DG running healthy | CLOSED | Ujjwal Das
1 | NORTH | 211605951 | 14-01-2025 13:53 | 160 | 6H.8475.../2420104 | V belt broken | Task Start | Worldnext Realty LLP. | 606 | Attended site for V-belt replacement ; SPN/FMI-5461/8,516166/0,110/0,3364/8,110/16 ;Flash the ECU & replace the V-belt after discussion with KOEL Team ;Load trial performed for 1 hour ;will check belt condition after 5 days | Closed | Ved Prakash Gupta
2 | NORTH | 211605946 | 14-01-2025 13:48 | 160 | 6H.8475.../2420371 | starting Issue. Call Bu Customer. name:- Somil madan Mobile No.:- 8800709847 | Task Start | VIVEK ANCILLARY (P) LTD. | 29 | Found abnormal sound in Engine check & found Charging alternator bracket bolt was loose tightness the same & topup the def issue resolve | Closed | Kapil Solanki | GOEM issue
3 | NORTH | 211605887 | 14-01-2025 13:25 | 125.4 | 4H.8042.C4../2420013 | Starting Issue Call By Customer Name - Charan Singh Number - 9812754609 | Open | BABA AMARNATH ENTERPRISES |  | Visit pending | Open | Gourav Sharma
4 | NORTH | 211605873 | 14-01-2025 13:23 | 82.5 | 5H.8901.../2420177 | Power Supply Issue Call By Customer Name ;- Mr. Nitin Ji Jain . Mob No ;- 9475444498 | Task Start | THE ARHAM GARDEN AND RESORT | 30 | Battery voltage low, Controller display ON & Charger supply off | Closed | Gourav Sharma
5 | NORTH | 211605851 | 14-01-2025 13:16 | 82.5 | 5H.8901.../2320076 | Genset Trip | Task Start | Sandhu Construction | 2080 | AS per KRM Tracker SR opened ; SPN/FMI-6595/0 & 1761/16 AdBlue tank found Dirty; Last visit done by Authorised Dealer at 1000 hour,Customer denied to check-up from Dealer;warranty will be rejected | Closed | Ved Prakash Gupta
6 | NORTH | 211605756 | 14-01-2025 12:35 | 500 | DV8.8501.C4../2320021 | Tripping Issue. Call by Customer. Name:- Navine Varma Mobile No.:- 8755023232 | Open | SUPRA CRAFT PACKAGING (P) LTD. |  | Visit pending | Open | Gourav Sharma
7 | NORTH | 211605702 | 14-01-2025 12:14 | 57 | T4.8941.../2320085 | Starting Issue Call By Customer Name - Sachin Khare Number - 9999436017 | Task Start | Sunder Mavi Hospital | 752 | Battery voltage low, Battery give for the testing | Closed | Kapil Solanki
8 | NORTH | 211605676 | 14-01-2025 12:04 | 25 | GP3.8702.../2421007 | Power Supply Issue Call By Customer Name - Ram . Number - 9935116882 | Task Start | T. V. Today Network Limited. | 5 | DG not start in auto mode Check & found Customer panel selector swich select on manual mode so, Dg not start in auto mode after change in auto mode start the DG | Closed | Sudhir Awasthi
9 | NORTH | 211605453 | 14-01-2025 10:41 | 40 | 3H.8951.../2320098 | Dg not start in auto | Completed | M/S ARYAN EXPORTERS PVT.LTD. |  | update pending | Open | Kapil Solanki
10 | NORTH | 211605447 | 14-01-2025 10:39 | 160 | 6H.8475.../2320026 | Leakage Issue | Task Start | STRIKER INDUSTRIES PRIVATE LIMITED | 70.2 | Oil Leakage found on supply pipe (Sump to FIP);Change the Washer & Tightened the same properly ; Issue resolved | Closed | Ved Prakash Gupta
11 | NORTH | 211605327 | 14-01-2025 08:33 | 20 | GP3.1021.../2420205 | INSTANCE ID: 100750208 SITE ID: I-UE-SLMB-ENB-9034 CALL BY CUSTOMER\\ DG ISSUE: DG ALARM ISSUE , MAINS COIL FAULTY NAME:Aditya Yadav NUMBER: 8810728360 | Task Start | Reliance Jio Infocomm Limited |  | Under voltage alarm & Mains coil burn change the coil & visit again for under voltage | Open | Sudhir Awasthi
12 | NORTH | 211605324 | 14-01-2025 08:14 | 125.4 | 4H.8041.../2320090 | Starting/Stopping Issue | Task Start | TAURUS READY MIXED CONCRETES | 2550 | Found mud in DEF tank & filter was chocked, Cleaning the tank & def line after required filter change | Open | Kapil Solanki
13 | NORTH | 211604541 | 13-01-2025 18:46 | 15 | GP3.8501.../2420282 | Starting/Stopping Issue | Closed | Dr. Ajay Mohan. | 55 | Emergency Switch is not proper working so, under EDO | Open | Sudhir Awasthi
14 | NORTH | 211604518 | 13-01-2025 18:41 | 45 | 3H.8951.../2420904 | Electrical Problems | Task Start | NEW FAMOUS BAKERY | 66 | MCB 63A burnt replace the same-update pending | Closed | Sudhir Awasthi
15 | NORTH | 211604354 | 13-01-2025 17:42 | 30 | 3H.8902.../2420923 | Starting Issue Email By - KGD Name -Rohit Gawade | Cancelled | Axis Bank Ltd |  | Under Cancellation-Out of Warranty Scope | Cancelled | Ved Prakash Gupta
16 | NORTH | 211604253 | 13-01-2025 17:15 | 82.5 | 5H.8901.../2420589 | Leakage Issue | Task Start | CHANDRIKA FARMS | 571 | All tappet cover bolt loose tightness to be all | Closed | Sudhir Awasthi | Campaign to bee check
17 | NORTH | 211604117 | 13-01-2025 16:57 | 58.5 | T4.8941.../2422073 | Automation Issue Call By Customer Name :-Aaryaman Zealong hospitality Mobile No :- 9876010688 | Cancelled | Zealong INC. |  | Under Cancellation-Customer not approved | Cancelled | Ved Prakash Gupta
18 | NORTH | 211604142 | 13-01-2025 16:54 | 57 | T4.8941.../2420460 | Starting Issue Call By Customer Name - Vinay Khurana Number - 9779780014 | Task Start | Yogi Raj Shri Ram Chiritable Trust | 25 | Fuel filter air lock problem- Today engineer visit with I-konnect tool | Open | Sudhir Awasthi
19 | NORTH | 211603984 | 13-01-2025 16:23 | 125.4 | 4H.8041.../2320184 | Starting Issue Call By Customer Name- H.L singhal Mo.No.- 9953775151 | Closed | ARCHWAY ENTERPRISES LLP | 137 | Wrong reporting by customer | Closed | Kapil Solanki
20 | NORTH | 211603878 | 13-01-2025 16:00 | 750 | DV2.8501.C4../2420021 | Low Frequency and Door Lock issue Call By Customer Name :- Nadeem Mobile No :- 7017899282 | Closed | MODI ARC ELECTRODES CO. | 49 | Low frequency alarm flash the file issue resolve | Closed | Kapil Solanki | KRM check karo
21 | NORTH | 211603862 | 13-01-2025 15:54 | 125.4 | 4H.8041.../2420092 | Starting Issue Call By Customer Name :-Dharm Pal Mobile No :- 9351916712 | Task Start | Raj Engineering Works | 33 | Engine not starting due to fuel is not available, Fuel low | Open | Gourav Sharma
22 | NORTH | 211603509 | 13-01-2025 15:38 | 400 | DV8.8542.C4../2320010 | Starting issue Call by customer Name: Suresh Kumar Number: 9991592430 | Task Start | BPCL. Haryana | 222 | Under Cancellation-Multiple SR open on same asset | Cancelled | Ved Prakash Gupta
23 | NORTH | 211603202 | 13-01-2025 15:06 | 62.5 | T4.8941.../2420188 | Leakage Issue | Closed | Littel Hearts International School | 196 | Coolant Leakage found on Radiator hose pipe (Bottom Side) due to Clamp found loose so Tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
24 | NORTH | 211603175 | 13-01-2025 14:59 | 500 | DV8.8501.C4../2320022 | Starting Issue Call By Customer Name :- Navin . Mobile No :-8882241581 | Closed | NIIT Limited | 103 | Radiator to front side to rain water | Closed | Kapil Solanki
25 | NORTH | 211603169 | 13-01-2025 14:57 | 250 | F6.8841.../2420008 | Starting Issue Call By Customer Name :- Navin ... Mobile No :-8882241581 | Closed | NIIT Limited | 211 | Radiator to front side to rain water | Closed | Kapil Solanki
26 | NORTH | 211603162 | 13-01-2025 14:53 | 20 | GP3.8601.../2420016 | Amber lamp on and maintaince due alarm Call By Customer Name : Naresh . No 9829148400 | Task Start | Shri Vaidic Swasti Pantha Nyas | 57 | Maintenance due alarm reset the alarm issue resolve | Closed | Gourav Sharma
27 | NORTH | 211603132 | 13-01-2025 14:47 | 125.4 | 4H.8042.C4../2420151 | Spn 6595 showing on DM1 | Closed | Gagan Generators. | 1054 | update pending | Open | Kapil Solanki
28 | NORTH | 211603019 | 13-01-2025 14:16 | 62.5 | T4.8941.../2320056 | Ndbc alarm is on | Closed | GAGAN GENERATORS | 870 | Wrong reporting by customer | Closed | Kapil Solanki
29 | NORTH | 211603014 | 13-01-2025 14:12 | 15 | GP3.8501.../2420476 | Starting issue Call By Customer Name :- Tarun Kumar Mobile No :- 9837809976 | Closed | Mohammad Faisal C/o. Diamond Engineering Company | 18 | Check & Found battery terminal loose and fuel filter loose so leakage the fuel tightness to be all issue resolve | Closed | Sudhir Awasthi
30 | NORTH | 211601181 | 2025-12-01 11:18 | 125.4 | 4H.8041.../2420635 | Engine is showing circuit open in diesel tank ,infact diesel is full in genset | Task Start | Suja Metals | 49 | Found Fuel sensor faulty , need to be replace | Open | Sudhir Awasthi
31 | NORTH | 211600549 | 2025-11-01 18:46 | 250 | F6.8841.../2420129 | Inspection/Maintenance | Open | Tng Exploration JV. Pvt. Limited. |  | Cancelled-Problem solve in PM visit | Cancelled | Gourav Sharma
32 | NORTH | 211599336 | 2025-11-01 14:56 | 200 | 6H.8435.../2320028 | Leakage Issue | Closed | Shabnam Enterprises | 17 | Found Overflow the fuel, Fuel tank over topup | Closed | Sudhir Awasthi
33 | NORTH | 211599257 | 2025-11-01 14:27 | 125.4 | 4H.8041.../2420150 | Ueara censer issue Call By Customer Name :- Rameshvar Singh Mobile No :-9810388104 | Closed | Anshuman Jain HUF | 29 | SPN/FMI 516166/0 reset the alarm issue resolve | Closed | Kapil Solanki
1 | West | 211602541 | 13-01-2025 12:20 | 30 | 3H.8902.../2421745 | Mild Lampi ssue and Tripping Issue Call By Customer Name- Sunil lokhande Mo.No.- 8850290508 | Task Start | DILIPO MACHCHHINDRA LOKHANDE | 1.28 | SPN/FMI- 2791/18, Calibrated the ECU. | Closed
2 | West | 211602525 | 13-01-2025 12:17 | 7.5 | D3.8305.../2400085 | Starting/Stopping Issue | Task Start | B. T. Kadlag Construction Pvt Ltd | 136 | Controller R phase sensing wire(GR1) fuse burn. So changed it. | Closed
3 | West | 211602147 | 13-01-2025 10:54 | 125.4 | 4H.8041.../2420898 | Starting issue Call by customer Name: Sandip Number:9822894086 | Completed | DUA CONSTRUCTION | 155.9 | Low Adblue level so filled it. | Closed
4 | West | 211602058 | 13-01-2025 10:31 | 20 | GP3.8601.../2420988 | Dg not start | Task Start | Dermatico | 15 | There is a problem in starting the genset in auto mode. So checked and found that the VMR wire is cut. | Closed
5 | West | 211601789 | 13-01-2025 08:38 | 20 | GP3.1021.../2420262 | INSTANCE ID:-100750592 SITE ID:- I-MH-LOAR-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-EB CONTRACTOR FAULTY NAME-Ambure NUMBER:-9309769264 | Open | Reliance Jio Infocomm Limited | Na | Cancelled | Closed
6 | West | 211601421 | 2025-12-01 17:10 | 58.5 | T4.8941.../2422077 | Genset Trip | Open | Shree Marketing Devkar Poultry Farm | 9.48 | SPN/FMI- 157/14, All wire connections checked and tightened. DTC cleared, case under monitoring. | Closed
7 | West | 211600409 | 2025-11-01 17:46 | 125.4 | 4H.8042.C4../2420598 | Error code 100/3 | Closed | Karan Development Services Pvt. Ltd. | 354 | SPN/FMI- 100/3, Opened the oil pressure sensor connector and checked the wire continuity, which was found to be OK. Checked the power supply of the sensor and found the supply to be 5V. There was an engine wiring pressure sensor connector pin backout. So fixed it and the problem was solved. | Closed |  | KRM Detail
8 | West | 211599917 | 2025-11-01 16:43 | 40 | 3H.8951.../2420844 | Starting Issue Call By Customer Name :- Ram Mobile No :-9820787941 | Closed | HAWARE LEGACCY | 4.18 | Air lock issue (SPN/FMI- 637/2) had been present for the past 8 days. Therefore, a Non-Return Valve (NRV) was installed on the return line | Closed | Need to confirmNRV as per BOM
9 | West | 211599882 | 2025-11-01 16:37 | 750 | DV2.8501.C4../2420178 | ECU alarm issue Call by customer Name: Satyandar Number:9657932174 | Under Monitoring | Sairama Realty. | 6.19 | SPN/FMI-656/3( Engine Fuel 1 Injector Cylinder 6-Voltage Above Normal) Checked the wiring continuity and found it okay. Opened the 10 Number cylinder rocker cover and checked the injector connector wire, which was also found to be okay. Cleared the DTC and the error code did not reappear. This case is under observation | Closed
10 | West | 211598606 | 2025-11-01 12:01 | 20 | GP3.8601.../2420992 | Red lamp alarm issue Call By Customer Name :-Sumit Dapke Mobile No :- 9975254254 | Closed | MUKUND PETROLIUM | 20.31 | 190/8 - Engine speed sensor erratic, 100/3- Lube oil sensor Tightened and refitted the MPU and Oil pressure sensor connector, but the MPU error code persisted. So,opened the MPU and found dust on its surface. After cleaning the dust, the problem was resolved. | Closed
12 | West | 211598503 | 2025-11-01 11:43 | 5.5 | CC1.1013.../2400113 | Starting Issue Call By Customer Name :- Mr. Rishabh Mobile No :-8809753477 | Closed | Rajlaxmi Dev Build India Pvt. Ltd. | 471.5 | The genset was running at 2800 RPM. So, by adjusting the actuator lever settings, the RPM was stabilized at 3000 RPM. | Closed
13 | West | 211598393 | 2025-11-01 11:23 | 200 | 6H.8435.../2420162 | Starting/Stopping Issue | Closed | Secure Matrix Constro Engineering Solution | 39.29 | Genset starting problem. SE found that feed pump was not working, so tightened all the wires of feed pump relay, but problem was still there. | Open
14 | West | 211595782 | 2025-10-01 16:13 | 15 | GP3.8501.../2420868 | Starting Issue Call By Customer Name :- Pankaj .. Mobile No :-9075625162 | Closed | Swantavir Sanik Manikrao Petroleum | 918 | Starting issue due to Low fuel level. | Closed
15 | West | 211595503 | 2025-10-01 15:24 | 125.4 | 4H.8042.C4../2420664 | Hunting Issue Call By Customer Name :- Vishal Yadav Mobile No :-8417848429 | Closed | Tube Tech Copper & Alloys Pvt Ltd | 18.51 | SPN/FMI- 3031/14, Cleared the DTC and calibrated the ECU. | Closed
16 | West | 211595385 | 2025-10-01 15:00 | 58.5 | T4.8941.../2422170 | Starting Issue Call By Customer Name :- Anish Powar Mobile No :- 9773887422 | Closed | Deja Blu | 23 | Genset was tripping due to under speed alarm. So checked the fuel line and crank sensor found OK. NRV direction OK. SPN/FMI- 110/3. So checked the temperature sensor connector and wiring found OK,Cleared the DTC. | Closed | Under observation
17 | West | 211605691 | 14-01-2025 12:09 | 40 | 3H.8951.../2421190 | Automation Issue Call By Customer Name - mr uddesh . Number -8308602950 | Closed | Technocraft Engineering. . | 29 | SPN/FMI-2791/18, Cleared the DTC through the i Konnect. | Closed
18 | West | 211605612 | 14-01-2025 11:41 | 500 | DV8.8501.C4../2420002 | controller issue & alarm issue Email By GOEM Name:-Surekha Auti | Task Start | M/s Silverio Developers Pvt. Ltd | 53.12 | 523597,0- communication fault-COMPROOEM9TO-High - most severe,516223,0- communication fault-COMPROOEM7TO-High - most severe,523582,0- Tampering Inducment Warn-High - most severe,523591,7- Communication Fault - Not Responding Properly,523531,7- Communication Fault - Not Responding Properly,523597,0- communication fault-COMPROOEM9TO-High - most severe,523591,7- Communication Fault - Not Responding Properly Could not arrange i connect tool yesterday so SE will visit today. | Open |  | KRM Data
19 | West | 211605481 | 14-01-2025 10:45 | 40 | 3H.8951.../2420457 | Starting/Stopping Issue | Task Start | Jyoti Buildcon. | 6.59 | Fuel pipe normal leakage. | Closed
1 | South | 211591387 | 2025-09-01 14:45 | 25 | GP3.8702.../2421377 | power supply problem Call by : Customer Name :G JAGADEESHA Contact :9945848161 | Open | G JAGADEESHA | 3 | visited the site checked the load cable connections and found that neutral connector link is not there so replaced the connecter with new one and solved the issue. photo | Closed | Mr. Anil Kumar H G
2 | South | 211591356 | 2025-09-01 14:33 | 58.5 | T4.8941.../2420862 | Oil Leakage Issue Call By Customer Name :- Danu . Mobile No :- 7424824604 | Task Start | KNR CONSTRUCTIONS LIMITED | 2239 | attend the site observed the dg sarted running ok observed the oil leakage check the lube oil filter damage replace the lube oil ok check the lube oil top up ok replace the air filter ok check radiator coolent oil level is a ok dg sarted running conditions ok. Photo | Closed | Mr. MD Saleem
3 | South | 211591352 | 2025-09-01 14:32 | 125.4 | 4H.8042.C4../2420783 | Starting Issue Call By Customer Name :- Ajmal Mobile No :- 7902990519 | Task Start | HARIS RAJA | 268 | DM1-1761/17, DM2 - 51/0shown in display. So SE Checked the DEF level found 81.60% then SE remove the def connector again fitted, also checked the remove the ITV and clean it & refitted,then clear the DTC issue resolved. | Closed | Mr. Sanjaimon S
4 | South | 211591232 | 2025-09-01 13:59 | 160 | 6H.8475.../2420354 | Display showing Amber light on Problem Call by : Customer Name :Plint Contact :9048289295 | Task Start | ASSISI VIDYANIKETAN PUBLIC SCHOOL | 18.52 | During the inspection noticed that ad blue low alarm, Checked ad blue level found 80% above ,checked ad blue level sensor wire connections found loose then tighted the connections and reset the alarm now started and tested ok,no alarm showing the display, engine started and tested with load engine working performance found good | Closed | Mr. Sanjaimon S
5 | South | 211591179 | 2025-09-01 13:45 | 500 | DV8.8501.C4../2420070 | Starting Problem Call by : Customer Name :Surat Sir Contact :9995088199 | Task Start | Nesto Hypermarket | 152 | Engine starting issue found low urea level alarm in bank 1. SE found 65% in tank. SO SE flash the ECU. Engine working found ok. photo | Closed | Mr. Sanjaimon S
6 | South | 211590444 | 2025-09-01 11:59 | 5.5 | CC1.1013.../2400021 | Over Heat Problem Call by : Customer Name :Vincent Contact :9400302821 | Open | VIVIAN TIES | 23 | over Heating,Found ex conical filter clogged,clean filter and start dg check load condition found ok photo. | Closed | Mr. Sanjaimon S
7 | South | 211590438 | 2025-09-01 11:57 | 320 | F6.9051.../2420001 | Preventive Maintenance Call by : Customer Name : Nageshwararao Contact : 9963944802 | Open | Anvita Group | NA | Cancelled | Cancelled | Mr. MD Saleem
8 | South | 211590298 | 2025-09-01 11:25 | 25 | GP3.8702.../2420678 | Starting/Stopping Issue | Task Start | Mr. Ashrit Kishan | 206 | inspected to the engine checked engine oil level and coolant level checked ok engine belt condition checked ok battery condition checked ok. DG not starting due to emergency stop switch press . correct the emergency switch. after complete the work started to the engine checked ok. the load used to welding working in 1ph load | Closed | Mr. NandhaGopal
9 | South | 211590256 | 2025-09-01 11:18 | 25 | GP3.8702.../2420754 | DG Emergency stop alaram reported | Task Start | ATC Telecom Infrastructure Private Limited | 10 | visit the site check the amf panel wiring conesons is found ok but 1c2 and 2c 12v dc supply connected the and control unit emergency stop is active in display and check the control panel wiring is found ok and kg640C control unit input A emergency is emergency active and input B is remote start/stop active and control unit settings is reset the input A and B and A is remote start/stop and B is emergency switch active and check the all external condition is found ok start and run the engine all working parameters condition is satisfied | Closed | Mr. Anil Kumar H G
10 | South | 211590202 | 2025-09-01 11:13 | 82.5 | 5H.8901.../2420029 | Amf Pannel problem Call by : Customer Name : Dr. Murali Contact : 9441314436 | Task Start | BANDAN PHARMACY | 26 | As per the customer complaint we have attended the site checked engine parameters found emergency stop due to released stop button and checked engine parameters found ok educated the customer about emergency stop,fuel level,coolent level battery voltage ,distilled water level ,etc ofter engine started taken load trails performence found ok | Closed | Mr. MD Saleem
11 | South | 211590193 | 2025-09-01 11:10 | 58.5 | T4.8941.../2420389 | Starting/Stopping Issue | Task Start | Munavar Sait | 40.55 | Fuel level showing wrong on display(26%) but the fuel is 40% | Closed | Mr. Anil Kumar H G
12 | South | 211589673 | 2025-09-01 09:49 | 30 | 3H.8902.../2421241 | Low Voltage Issue Call By Customer Name :- PRADEEP K M Mobile No :- 7899025739 | Closed | PRADEEP K M | 34 | SPN 97/FMI 5, clear the DTC | Closed | Mr. Anil Kumar H G
13 | South | 211588255 | 2025-08-01 18:24 | 125.4 | 4H.8042.C4../2420828 | Genset Trip | Closed | SVC Cinemas | 11.39 | 5161660/0 error code. cleared alarm so started engine engine starting and running condition is normal | Closed | Mr. MD Saleem
14 | South | 211587699 | 2025-08-01 16:55 | 15 | GP3.8501.../2420819 | Starting Problem Call by : Dealer Name : Srinivas Contact : 9030035225 | Closed | Primary Agruculture C/o. Operative Society Limited Sircilla. | 12 | 2791/14, 2802/4 Eroor code issue. visited the site observed error code EGR Valve clean. ECU flashing with neera cable and laptop and started the engine running condition load trail performance found ok | Closed | Mr. MD Saleem
15 | South | 211587649 | 2025-08-01 16:47 | 0 | 6H.8475.../2420196 | CAC HOSE FAILURE AND RADIATOR COOLANT LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | LR | inspected the dg noticed the cac hose damage,so change the new cac hose fixing properly, after start the dg given load always working ok | Closed | Mr. NandhaGopal
16 | South | 211587393 | 2025-08-01 16:17 | 0 | T4.8941.../2421504 | FUEL LEAKAGE FROM RETURN HOSE | Task Start | SUNBEAM GENERATORS PVT LTD | LR | inspected the dg noticed the fuel leak for fuel return hose, change the new fuel return hose fixing properly, after start the dg check the leakage found ok | Closed | Mr. NandhaGopal
17 | South | 211587311 | 2025-08-01 15:59 | 40 | 3H.8951.../2421202 | MCB Lamb problem and Abnormal problem Call by : KGD Name :Suneer Contact :9567057200 9562607535 (KGD) | Task Start | Arabian Palace | 8 | 2791/1, 5838/1 error code issue. attended the site checked the connector found ok , then connected ikonnect and error codes cleared. then started DG and running found normal. tested for 1 hour of 15 min duration, no fault codes observed. then tested for 30 min, no fault codes were observed. instructed customer to monitor DG for 2 days. DG working properly. output voltages found normal. ca and battery charger output found normal. | Closed | Mr. Sanjaimon S
18 | South | 211583674 | 2025-08-01 14:36 | 20 | GP3.8601.../2421418 | Starting/Stopping Issue | Closed | SREEJITH PULLAIKODI | 33 | visited the site found emergency switch problem then remove emergency switch clean and refitted | Closed | Mr. Sanjaimon S
19 | South | 211583459 | 2025-08-01 13:45 | 40 | 3H.8951.../2420744 | Power supply issue Called by customer Name : Amith Number: 9611199934 | Closed | Amith R | 19 | As per the customer complaint visit the site dg not starting.check the dg and observe the problem.the problem was emergency stopped.check the emergency push button normal.check the emergency no and nc contactor interpted.remive the wire connection then fixed found ok.check the emergency push button ok. | Closed | Mr. Anil Kumar H G
20 | South | 211583402 | 2025-08-01 13:33 | 82.5 | 5H.8901.../2420171 | Inspection/Maintenance | Closed | Aditya Vemuri. | 5.53 | Attand the site check the oil level is ok air filter and belt is ok battery water level is ok check the coolent leave is low top the coolent After start the engine check the running condition is ok coolent water lekages from the radiotar house pipes tight the house clamps after start the engine check the running condition is ok oil and water leakages no staring and stoping is ok | Closed | Mr. MD Saleem
21 | South | 211583377 | 2025-08-01 13:31 | 160 | 6H.8475.../2420101 | Leakage Issue | Closed | Aditya Vemuri. | 2 | start the engine check the engine oil leakages form the engine filter loos Tight the engine oil filter after start the engine check the running condition is ok oil and water leakages no staring and stopping is ok | Closed | Mr. MD Saleem
22 | South | 211583336 | 2025-08-01 13:21 | 160 | 6H.8475.../2420208 | Fan belt problem Call by : Customer Name : Raju Reddy Contact : 9985044305 | Closed | Navtej Infrastructure Pvt Ltd | 351 | 516166/0 error code issue. Observed belt failed so replace new belt error code clear started the engine running condition load trail performance found ok | Closed | Mr. MD Saleem
23 | South | 211601795 | 13-01-2025 08:55 | 5 | CP1.1003.../2400039 | Sound/Vibration Issue | Open | KUNHAHAMMED | 2 | No issue. SE not found any abnormal sound. Engine runing ok. | Closed | Mr. Sanjaimon S
24 | South | 211601322 | 2025-12-01 14:19 | 320 | F6.8802.../2420270 | Door lock not working properly | Task Start | Dr. M. Mani Elango M. S. | 769 | door is not proper close | Closed | Mr. NandhaGopal
25 | South | 211601291 | 2025-12-01 13:29 | 58.5 | T4.8941.../2421400 | Fuel Sensor Issue Call By Customer Name - Arjun .. Number - 9482879219 | Open | Sri Gavisiddheshwara Samsthan Sri Gavimath | 39 | As per customer complaint fuel level shown 88% only if customer fill the tank still level show 88%. So SE visited the & checked the float for stuck found ok then removed the sensor agian refitted found ok | Closed | Mr. Anil Kumar H G
26 | South | 211601182 | 2025-12-01 11:19 | 58.5 | T4.8941.../2422410 | Starting/Stopping Issue | Closed | M/s. MVR Traders | 25 | Attended the site observed the DG start condition it was auto Start problem due to mains sensing connections not given then connected to the sencing wire and change controller settings | Closed | Mr. MD Saleem
27 | South | 211600424 | 2025-11-01 17:49 | 5.5 | CC1.1013.../2400084 | Starting/Stopping Issue | Closed | EMPOWER | 125.54 | Attended the site and checked the DG with the presence of the customer representative. Found dc supply not coming to controller. Found dc glass fuse in failed condition. No continuity for the fuse. Replaced the fuse and checked. Found now working OK. Started and checked several times. Now DG running found normal. | Closed | Mr. Sanjaimon S
28 | South | 211599784 | 2025-11-01 16:20 | 30 | 3H.8902.../2421008 | Starting/Stopping Issue | Closed | THOMAS. | 20 | attended the site check the problem found battery charger fuse fused condition,replace fuse charge for sometime problem solved, check oil level, coolant level, foundation bolt,start the engine output voltage is ok dg running helthy | Closed | Mr. Sanjaimon S
29 | South | 211599718 | 2025-11-01 16:02 | 40 | 3H.8951.../2420946 | Starting Problem Call by : Customer Name : Patil Contact : 9448110999 | Open | Bhimanagouda Goudappagouda Patil. | NA | Visit pending | Open | Mr. Anil Kumar H G
30 | South | 211599587 | 2025-11-01 15:44 | 25 | GP3.8702.../2420926 | Under speed problem Call by : Customer Name : Akram Contact : 8328260634 | Task Start | Malwa Infracon Pvt. Ltd. | NA | Update pending | Closed | Mr. Anil Kumar H G
31 | South | 211599409 | 2025-11-01 15:04 | 58.5 | T4.8941.../2421359 | Power supplay Issue Call By Customer Name :-Amit Desai Mobile No :-9579983990 | Open | D. H. D. Infracon Pvt. Ltd. | NA | Visit pending | Open | Mr. Anil Kumar H G
32 | South | 211599361 | 2025-11-01 14:54 | 125.4 | 4H.8041.../2420886 | Error code problem Call by : Customer Name :Basha Contact : 7799000211 | Closed | M/S INDIAN AUTO MOBILE SERVICESS | 64 | Ecu malfunction error code.516166/0 error codes .Connect the ikonnect tool remove the error code.then start the dg found okay. | Closed | Mr. NandhaGopal
33 | South | 211599239 | 2025-11-01 14:33 | 15 | GP3.8501.../2421515 | IN proper Installation | Task Start | HOTEL VAIBHAV | LR | This SR need to be Cancelled | Cancelled | Mr. Anil Kumar H G
34 | South | 211599251 | 2025-11-01 14:23 | 25 | GP3.8702.../2421481 | Starting Issue. Call by Customer. Name:- Namrata ... Mobile No.:-9886475015 | Task Start | Vasudeva Developers | 2.5 | Control Panel XDBK 4 wire loose connection | Closed | Mr. Anil Kumar H G
35 | South | 211599034 | 2025-11-01 13:36 | 20 | GP3.8601.../2421622 | Electrical-amber light problem | Closed | M G S Agencies | 32 | Engine not starting reason for engine speed sensor error issue.lop switch wiring loose connection.so engine not starting.crooction the wiring (f.no-D3). problem solving.started the engine voltages found ok.engine condition normal | Closed | Mr. Nandha Gopal
36 | South | 211599016 | 2025-11-01 13:33 | 20 | GP3.8601.../2421556 | Oil leakage issue Called by customer Name : AVISHKAR Number: 9742966649 | Task Start | PUSHPA CHANDRA ENERGY STATION | 45 | Fuel pump hurting adjustment out side 17 no allen Bolt through oil leakage so removed the fuel pump Bolt apply the taplan tep and annabond gem after started with load there is no leakage engine working condition | Closed | Mr. Anil Kumar H G
37 | South | 211598977 | 2025-11-01 13:26 | 250 | F6.8841.../2420147 | Coolant Leakage Call by : Customer Name :Pratheesh Sir Contact :9207478037 | Closed | AR. Handlooms | 1492 | attended the site checked the dg set with the presence of customer representative. checked oil fuel coolent and battery water levels. found leakage from lower side radiator hose. tightened radiator hose and checked all hoses. then checked belt and condition of hoses. then start and run the dg manually and automatically. checked load and all other parameters. dg running condition is good. | Closed | Mr. Sanjaimon S
38 | South | 211598985 | 2025-11-01 13:24 | 58.5 | T4.8941.../2423082 | LOAD CABLE NOT DONE | Closed | S. S. Hospitel | LR | LR open dy dealer for claim since no part has been and CC sr open . | Closed | Mr. Anil Kumar H G
39 | South | 211598677 | 2025-11-01 12:19 | 25 | GP3.8702.../2420804 | Starting Problem Call by : Customer Name :Sreenath Contact : 8977014597 | Closed | Varsity Education Management Private Limited Sri Chaitanya Educational | 10.46 | ATTENDE the site checking engine not starting so checking battery volatge is ok battery water level is ok so checking wiring connection Fuse Failed so replaced new fuse ferule No 2C &2D so Due to losse connection so fightment tight and checking connection is ok so started the engine starting and running condition is good engine all paramater are normal | Closed | Mr. MD Saleem
40 | South | 211598624 | 2025-11-01 12:09 | 30 | 3H.8902.../2421067 | Starting/Stopping Issue | Closed | Mr. Cherukuri Chakradhar Ji. | 26 | visit the site as per following complaint check the engine condition and wiring connections found the metering unit wiring are lose so retit the wiring then start the engine running condition is ok | Closed | Mr. MD Saleem
41 | South | 211598287 | 2025-11-01 11:03 | 58.5 | T4.8941.../2423258 | battery not available | Cancelled | Sugama Convention Hall | NA | Cancelled | Cancelled | Mr. Anil Kumar H G
42 | South | 211598280 | 2025-11-01 11:02 | 58.5 | T4.8941.../2421471 | Inspection/Maintenance | Closed | Shiva Prakash | 5 | 2802/4 error code shown in event log. Also fuel level low so SE remove the airlock and run dg working ok | Closed | Mr. Anil Kumar H G
43 | South | 211598250 | 2025-11-01 10:59 | 30 | 3H.8902.../2420853 | Starting/Stopping Issue | Closed | K. G. D. Unikorn | 9 | visit the site check the engine not starting problem was disel Air lock issue after removed the Air lock after start the engine running condition ok all wiring connection ok all parameters found ok | Closed | Mr. Anil Kumar H G
44 | South | 211595836 | 2025-10-01 16:25 | 15 | GP3.8501.../2320007 | Door Lock Issue Call By Customer Name :- Prabhakar Mobile No :-9176669465 | Closed | S. K. Agency. | 49 | Adjust the door lock | Closed | Mr. NandhaGopal
45 | South | 211595554 | 2025-10-01 15:32 | 5.5 | CC1.1013.../2400016 | Starting Issue Call By Customer Name :- Kalin Kumar Mobile No :- 8757520945 | Open | East Coast Railway Andhra Pradesh | NA | Cancelled | Cancelled | Mr. MD Saleem
46 | South | 211595459 | 2025-10-01 15:20 | 40 | 3H.8951.../2421546 | CC | Task Start | Sathya Agencies Pvt. Ltd. .. | LR | commissioning sr | Closed | Mr. NandhaGopal
47 | South | 211594840 | 2025-10-01 12:33 | 0 | 5H.5106.../2400002 | OIL SERVICE | Closed | Bull Machines Pvt Ltd | 616 | Done oil service | Closed | Mr. NandhaGopal
48 | South | 211594339 | 2025-10-01 11:26 | 58.5 | T4.8941.../2422797 | Display showing incorrect fuel level & Door Lock Problem Call by : Customer Name :Manoj Contact :8089660774 | Task Start | EVEREST GREEN KERALA | 26 | attended the site check engine door locking system problem adjust the locking system door close problem solving engine Star and Stop and emergency stopping working ok belt tensioner ok hose and hose clips ok battery voltage 13 charging voltage 14 engine out put voltage 231 fuels level sensor ok fuel level settings problem settings correct problem solving | Closed | Mr. NandhaGopal
49 | South | 211592832 | 2025-09-01 18:13 | 125.4 | 4H.8042.C4../2420315 | Oil leakage problem Call by : KGD Name : vijay krishna Contact : 8501945299 Dealer contact No: 9347338159 | Closed | m.sri hari tnfra | 51 | sump blot lose tight sump blot clear the problem | Closed | Mr. NandhaGopal
50 | South | 211592089 | 2025-09-01 16:00 | 40 | 3H.8951.../2420982 | Leakage Issue | Closed | D.Lakhsmi Narayana | 30.2 | coolent leakage from hose pipe so retight the clamp is ok | Closed | Mr. MD Saleem
51 | South | 211591930 | 2025-09-01 15:49 | 30 | 3H.8902.../2420342 | Genset Trip | Closed | Sri Sitarama Enterprises | 4 | overload alarm due to costumer using overload so advice to costumer use normal load a | Closed | Mr. MD Saleem
52 | South | 211591870 | 2025-09-01 15:40 | 58.5 | T4.8941.../2420694 | Oil Leakage Issue Call By Customer Name :- Dhamu Sir Mobile No :- 9502164038 | Closed | KNR CONSTRUCTIONS LTD | 1837 | lube oil filter o ring damage replace the new filter | Closed | Mr. MD Saleem
53 | South | 211591860 | 2025-09-01 15:36 | 40 | 3H.8951.../2421298 | Starting Problem Call by : Customer Name : Yasin Contact : 9945971936 | Closed | Kareem Amjadh | 43 | Battery discharge as the battery supply was removed | Closed | Mr. Anil Kumar H G
54 | South | 211590113 | 2025-09-01 11:06 | 0 | 5H.5106.../2420001 | JOINT VISIT | Open | Bull Machines Pvt Ltd | NA | Cancelled | Cancelled | Mr. NandhaGopal
1 | East | 211606834 | 14-01-2025 18:03 | 45 | 3H.8951.../2421369 | Diesel Leakage & Silencer Broken Call By Service Dealer Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. |  | visit pending | OPEN | Prabhakar Kumar
2 | East | 211605799 | 14-01-2025 12:50 | 250 | F6.8841.../2420332 | Leakage Issue | Closed | Bishop Westcot School | 3 | There was coolant leakage at thermostat outlet hose due to clamp loose after tightening issue resolved | CLOSED | Prabhakar Kumar | GOEM issue
3 | East | 211602132 | 13/01/2025 10:48:46 | 20 | GP3.8601.../2420187 | Starting Issue Call By KGD Name- Neha Komkom Mo.No.- 9234456624 | Open | Jharkhand Sales Agencies Pvt. Ltd. | 54 | SR cancelled - problem resolved on telephonic communication | OPEN | Prabhakar Kumar
4 | East | 211602942 | 13/01/2025 13:53:22 | 400 | DV8.8542.C4../2420023 | Error issue Email By - Customer Name - Neeraj Mishra | Task Start | Mr. Ravindra Patel | 14 | Today SE will visit site | OPEN | Prabhakar Kumar
5 | East | 211601117 | 2025-12-01 08:53 | 30 | 3H.8902.../2422023 | Starting Issue Call By Customer Name :-Satpal Sharma Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS |  | Visit pending | OPEN | Ujjwal Das
6 | East | 211598932 | 2025-11-01 13:12 | 20 | GP3.8601.../2420650 | Starting issue Call by customer Name: Jahirul Islam Number:7002124310 | Closed | STATE BANK OF INDIA | 87 | Electric feed pump issue not working check all connection found OK and also given direct supply to the electric pump but not working so need to replace feed pump. | CLOSED | Ujjwal Das
7 | East | 211598234 | 2025-11-01 11:00 | 500 | DV8.8501.C4../2320004 | Starting Issue Call By Customer Name - Nitesh kumar Mo No -9572166785 | Task Start | Indian Potash Limited | 154 | SE found DG not cranking then checked for loose connection found starter +ve wire loose as well as due to short circuit wire burn then tighten it and checked all connection found ok then crank but failled also given direct supply to starter motor but same issue, Starter motor is defective checked in workshop found its burn. | OPEN | Prabhakar Kumar
9 | East | 211587976 | 2025-08-01 17:40 | 82.5 | 5H.8901.../2420499 | Amber Lamp On Alarm Call By Customer Name :- Koushal Kishor Singh Mobile No.:- 6909604331 | Open | Tojo Karga (IPS) | 27 | DEF level low alarm, problem resolved mail send for cancellation | OPEN | Ujjwal Das
10 | East | 211606793 | 14-01-2025 17:35 | 58.5 | T4.8941.../2420371 | Emergency Stop Alarm Issue Call By Customer Name - Behra .. Number -9556800599 | Open | Shree Binayak Textile |  | Today SE will visit site | OPEN | Ujjwal Das
11 | East | 211606055 | 14-01-2025 15:03 | 25 | GP3.8702.../2420009 | Starting/Stopping Issue | Task Start | Axis Bank Ltd |  | Today SE will visit site | OPEN | Prosanjit saha
12 | East | 211604590 | 13-01-2025 19:46 | 30 | 3H.8902.../2420816 | Automation Issue Call By Customer Name - Ashok Kumar Number - 8249408483 | Open | Abis Exports I. Pvt. Limited. . |  | Today SE will visit site | CLOSED | Ujjwal Das
13 | East | 211604569 | 13-01-2025 20:00 | 20 | GP3.8601.../2420556 | Maintenance Due Alarm Call By Customer Name :- Saurabh . Mobile No :-8609120321 | Closed | Sanjay Energy Station. | 10 | Customer required service no issue in DG | CLOSED | Prosanjit saha
14 | East | 211604529 | 13-01-2025 18:21 | 58.5 | T4.8941.../2423095 | EGR VLV H BRIDGE FLT. | Closed | Ramjibanpur Municipality | 3 | Check the engine found 2791/31 ( EGR vlv H Bridge flt code), so flashing the ECU , then start the engine running condition was ok, no error code showing, all parameters was ok. | CLOSED | Prosanjit saha | Under Observation
15 | East | 211602621 | 13-01-2025 12:35 | 20 | GP3.8601.../2420761 | Starting Issue Call By Customer Name :- MR. AKSHYA KUMAR Mobile No :-8249048100 | Closed | M/S CHAND AUTOMOBILE LLP | 6 | SE check the Dg found Dg trip in under speed alarm. After checked the fuel supply line found ok & removed the MPU connection and again properly connected the MPU connection. Then start the Dg running okay ,Problem was resolved. | CLOSED | Ujjwal Das
1 | NORTH | 211608375 | 15-01-2025 13:57 | 125.4 | 4H.8041.../2420018 | issue | Closed | Sharkline Appliances | 224 | DG Auto Starting Issue due to R-Phase fuse found faulty so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
2 | NORTH | 211608353 | 15-01-2025 13:44 | 125.4 | 4H.8041.../2420994 | Inspection/Maintenance | Closed | PINNACLE DENTAL | 31 | Controller show the low def level so, Dg not start after reset the alarm with i-konnect tool then issue resolve | Closed | Kapil Solanki
3 | NORTH | 211608277 | 15-01-2025 13:25 | 58.5 | 3H.8902.../2420531 | Battery Issue Call By Customer Name: NAVEEN GROVER Number: 8882241581 | Task Start | B. N. P. Enterprises | 12 | Visit pending | Open | Kapil Solanki
4 | NORTH | 211608267 | 15-01-2025 13:15 | 30 | 3H.8902.../2420531 | Battery Issue And Preventive maintenance Call By Customer Name :- Jagdish Tewatia Mobile No :-8384002020 | Closed | Rolling Pin Bakes | 33 | Educate the customer please Battery charger always ON & not required service | Closed | Kapil Solanki
5 | NORTH | 211608261 | 15-01-2025 13:12 | 82.5 | 5H.8901.../2420804 | E rror code Issue Call By Customer Name- Naveen Mo.No.- 8221904142 | Closed | PARWATI GARDEN | 49.2 | Controller select on manual mode so, Dg not start in auto | Closed | Ved Prakash Gupta
6 | NORTH | 211608168 | 15-01-2025 12:50 | 82.5 | 5H.8901.../2420347 | Automation issue Call By Customer Name :- Surendra Singh Bhatti Mobile No.:- 9968663656 | Closed | Annat C.G.H.S. Ltd. | 12 |  | Closed | Kapil Solanki
7 | NORTH | 211608102 | 15-01-2025 12:30 | 125.4 | 4H.8041.../2420162 | Starting/Stopping Issue | Closed | K. N. Promoters India Pvt. Ltd. | 176 | SPN/FMI-157/14 ; Found Common Rail pressure sensor wiring loose so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
8 | NORTH | 211608080 | 15-01-2025 12:25 | 160 | 6H.8475.../2320014 | Amber lamp alarm issue Call By Customer Name :- Monu Kumar Mobile No.:- 7500162400 | Task Start | Swarup Steel Industries Ltd. | 1188 | SPN/FMI 1761/2 during C-check Def inlet filter not available in dealership so, replace now then issue resolve | Closed | Sudhir Awasthi
9 | NORTH | 211608021 | 15-01-2025 12:07 | 40 | 3H.8951.../2421100 | Starting/Stopping Issue | Closed | Shree Geetanand Generator. | 4.42 | Crank Rest Alarm on controller;Battery Voltage found ok ; On interface card,NO point for supply to Card not fitted properly(2E) , Corrected same & start the DG,Issue resolved | Closed | Ved Prakash Gupta
10 | NORTH | 211607985 | 15-01-2025 11:58 | 25 | GP3.8702.../2420847 | Voltage Fluctuation | Closed | Ruchi Verma. |  | update pending | Open | Sudhir Awasthi
11 | NORTH | 211607954 | 15-01-2025 11:55 | 58.5 | T4.8941.../2421683 | Automation issue Call By Customer Name :- Sunil Kumar Panday Mobile No :- 9811720884 | Closed | Pooja Embroidery | 39 | Auto wire was loose tightness the same issue resolve | Closed | Kapil Solanki
12 | NORTH | 211607947 | 15-01-2025 11:51 | 125.4 | 4H.8041.../2420430 | Abnormal Sound Issue Call By Customer Name :- Shiva Mobile No :- 8707200471 | Closed | Shyam Multiplex LLP. | 235 | Check & found V-Belt Loose tightness the same & topup the Urea after that clear the fault code issue resolve | Closed | Sudhir Awasthi
13 | NORTH | 211607898 | 15-01-2025 11:45 | 125 | F6.9840.../2420020 | Starting/Stopping Issue | Closed | B Continental Hotel | 5 | update pending | Open | Kapil Solanki
14 | NORTH | 211607882 | 15-01-2025 11:30 | 125.4 | 4H.8042.C4../2420021 | Door Lock Issue Call By Customer Name :- Abdul Sattar Mobile No:-9310737227 | Closed | S H A ASSOCIATES | 35 | Correct door lock with screw driver | Closed | Kapil Solanki
15 | NORTH | 211607880 | 15-01-2025 11:30 | 125.4 | 4H.8041.../2420164 | KRM ISSUE | Closed | Peace Unlimited Hospitalities | 191 | KRM not showing live parameter even after updated from dealer office ; suggested to mail KRM Team for the same | Closed | Ved Prakash Gupta
16 | NORTH | 211607812 | 15-01-2025 11:10 | 125.4 | 4H.8041.../2320019 | B Check service | Open | MNH. Industires |  | Visit pending | Open | Gourav Sharma
17 | NORTH | 211607795 | 15-01-2025 11:07 | 160 | 6H.8475.../2420263 | Inspection/Maintenance | Open | Parmeshwari Silk Mills Ltd. |  | Under Cancellation-Complaint rectified on telephonic discussion | Cancelled | Ved Prakash Gupta
18 | NORTH | 211607774 | 15-01-2025 10:57 | 30 | 3H.8902.../2320024 | Starting Issue Call By Customer Name :- Pankaj Mobile No :-9810566739 | Under Monitoring | Maple Infrastructures Pvt. Ltd. | 32 | Battery discharge, battery connection done from customer end- under observation | Open | Kapil Solanki
19 | NORTH | 211607759 | 15-01-2025 10:51 | 125.4 | 4H.8041.../2320090 | Excessive Smoke | Completed | TAURUS READY MIXED CONCRETES |  | Def filter change | Open | Kapil Solanki
20 | NORTH | 211607737 | 15-01-2025 10:47 | 25 | GP3.8702.../2421292 | Starting Issue Call By Customer Name: Rahul Saini No : 9971188227 | Task Start | WOW EQUIPMENT & INFRA PVT LTD |  | Visit pending | Open | Gourav Sharma
21 | NORTH | 211607747 | 15-01-2025 10:41 | 10 | GP3.8301.../2420138 | Maintenance Due Alarm Issue Call By Customer Name l- PRABHAT SINGH . Mob No :- 9161083904 | Closed | Prabhat Singh |  | update pending | Open | Sudhir Awasthi
22 | NORTH | 211607637 | 15-01-2025 10:32 | 125 | F6.9840.../2420027 | Reverse Phase Issue Call By Customer Name - Ram Sahi No - 9899280112 | Closed | GRAPECITY INDIA PVT LTD | 34 | DG Phase reversed, Disable from controller | Closed | Kapil Solanki
23 | NORTH | 211607660 | 15-01-2025 10:27 | 58.5 | 6H.9840.../2420003 | Starting/Stopping Issue | Closed | Ranawat Inc | 15.44 | Gas Engine- Ecu flash -Update pending | Closed | Kapil Solanki
24 | NORTH | 211607616 | 15-01-2025 10:19 | 15 | GP3.8501.../2421527 | Electrical Problems | Task Start | REYAZ AHMAD NAJAR |  | Visit pending | Open | Ved Prakash Gupta
25 | NORTH | 211607558 | 15-01-2025 10:06 | 25 | GP3.8702.../2420272 | Starting/Stopping Issue | Task Start | VEER BALAJI FUEL CENTRE |  | Today visit Engineer | Open | Sudhir Awasthi
26 | NORTH | 211607481 | 15-01-2025 08:26 | 500 | DV8.8501.C4../2320051 | Trip_Genset_Low_Voltage | Closed | Sunil Healthcare Limited | 53 | Low def level,reset the alarm then check engine found no any issue in DG | Closed | Gourav Sharma
27 | NORTH | 211606896 | 14-01-2025 19:05 | 320 | F6.8802.../2420018 | Trip_Genset_Low_Voltage | Cancelled | KPC FLEXI TUBES PVT LTD |  | Cancelled-Problem solve in telephonic disscution | Cancelled | Kapil Solanki
28 | NORTH | 211606823 | 14-01-2025 17:44 | 15 | GP3.8501.../2420006 | Starting/Stopping Issue | Task Start | BHARTI AIRTEL LIMITED | 6 | Engine not start-Required visit with koel team | Open | Kapil Solanki
29 | NORTH | 211606609 | 14-01-2025 16:25 | 58.5 | T4.8941.../2423116 | Alternator Fan Damage Email By - KGD Name - Darshan Power Solutions | Task Start | DARSHAN POWER SERVICES | 405 | Main alternator fan damage, required to be change | Open | Kapil Solanki
30 | NORTH | 211606124 | 14-01-2025 15:38 | 40 | 3H.8951.../2421185 | Genset Trip | Cancelled | Axis Bank Ltd |  | Under Cancellation-Problem solve without visit | Cancelled | Kapil Solanki
31 | NORTH | 211606106 | 14-01-2025 15:22 | 400 | DV8.8542.C4../2320010 | Trip_Genset_Low_Voltage | Closed | BPCL. Haryana | 225 | Controller not getting voltage (Voltage fluctuation on controller) due to 415 V coupler found loose;so bypass the same & run the DG,issue resolved(Voltage malfunctioned at starting) | Closed | Ved Prakash Gupta
32 | NORTH | 211606075 | 14-01-2025 15:11 | 82.5 | 5H.8901.../2320093 | Low Urea Alarm Call By Customer Name :- Sumit Mobile No :- 9818430800 | Task Start | GENERAL AUTOMOTIVES COMPONENTS | 622 | Low def level, topup required more then reset the alarm | Open | Kapil Solanki
33 | NORTH | 211606016 | 14-01-2025 14:44 | 50 | T4.8941.../2420659 | Starting/Stopping Issue | Closed | Administrative Reforms Department Uttar Pradesh. | 210 | DG not start because Crank sensor wiring loose Clean the connector after start the Dg ok & customer requirement for big charger quatation send to the customer for 10Amp. Charger | Closed | Sudhir Awasthi
34 | NORTH | 211606013 | 14-01-2025 14:41 | 15 | GP3.8501.../2421047 | Self Issue Call By Customer Name :- Mobile No :- 7210616022 | Task Start | B. D. S. Decor & Fabricators. |  | Visit Pending | Open | Ved Prakash Gupta
35 | NORTH | 211605992 | 14-01-2025 14:22 | 125.4 | 4H.8042.C4../2420792 | Amber Lamp On Alarm Issue. Call By Customer. Name:- Sataym.. Mobile No.:- 8800815113 | Closed | RAVI SINGH | 47 | Def level low & service required | Closed | Sudhir Awasthi
36 | NORTH | 211595911 | 2025-10-01 16:37 | 40 | 3H.8951.../2420728 | Leakage Issue | Closed | SUNIL KUMAR KAUSHIK | 63 | Recovery bottle damage, replace the same with 1 Lit. Coolant topup-under EDO | Open | Sudhir Awasthi
1 | South | 211598135 | 2025-11-01 10:36 | 25 | GP3.8702.../2421390 | Alarm Issue Call By Customer Name :- Shibil Mobile No :-9380648422 | Closed | MAYURA BAKERY SWEETS AND JUICES | 61 | SPN: 2791,FMI: 18/SPN: 5838,FMI: 1/ SPN: 2791,FMI: 6, clear the DTC | Closed | Mr. Anil Kumar H G
2 | South | 211598056 | 2025-11-01 10:26 | 58.5 | T4.8941.../2421437 | Voltage Problem & Load Problem Call by : Customer Name :THIRUNAVUKARASU Contact :9940156642 Dealer Contact No:9786116199 | Closed | COTTON HOME | 38 | Customer side load issue, eduactte the customer to adjust the inverter | Closed | Mr. NandhaGopal
3 | South | 211597895 | 2025-11-01 09:18 | 5.5 | CC1.1013.../2400084 | Starting/Stopping Issue | Closed | EMPOWER | 52 | ferule number 8, was cut. The damaged wiring was replaced | Closed | Mr. NandhaGopal | Required Photo
4 | South | 211597050 | 2025-10-01 19:58 | 20 | GP3.8601.../2420858 | Inspection/Maintenance | Open | Hotel Dawaat |  | visit pending | Open | Mr. NandhaGopal
5 | South | 211596300 | 2025-10-01 17:30 | 58.5 | T4.8941.../2421860 | STARTER ISSUE-PAVUN | Closed | Mr. Narendra Kumar Gehlot | LR | DG not starting check the battery voltage found 12.9 volt, check any other abnormalities, all found ok, fitted new battery DG start. | Closed | Mr. Anil Kumar H G | Required analysis report
6 | South | 211595924 | 2025-10-01 16:39 | 30 | 3H.8902.../2421241 | Automation Issue Call By Customer Name :- Mobile No :-9663793637 | Completed | PRADEEP K N | 47 | the engine not start because of code 97/5 issues so clear code and ECU flash after start again 97/5 show so replaced filter sensor assly and start the engine running is ok | Closed | Mr. Anil Kumar H G | Under Observation
7 | South | 211594853 | 2025-10-01 12:37 | 58.5 | T4.8941.../2420390 | AMF Problem Call by : Customer Name :Bharath Contact :9061712030 | Closed | CSB BANK LIMITED | 11 | Automation issue | Closed | Mr. Sanjaimon S
8 | South | 211594078 | 2025-10-01 10:36 | 10 | GP3.8301.../2420080 | Starting issue Call By Service Dealer Name :- Manu Mobile No :- 8589980069 | Task Start | ATHIRA DRINKS | 36 | fuel tank butterfly valve checked, fuel line checked ok, fuel pump voltage checked ok, fuel pump Rack checked ok, panel board wiring titted, Air removed, high pressure pipe, Nozel removed check, Nozel blocked, removed, | Task start | Mr. Sanjaimon S | Required Calibration Report
9 | South | 211593925 | 2025-10-01 09:52 | 125.4 | 4H.8042.C4../2420697 | Abnormal sound & Alarm Problem Call by : Customer Name :Raghu ram Contact : 7993310814 | Closed | Sai Silks Kalamandir Limited | 39 | ad blue level is low filling the addblue educated the customer maintainance the adblue level | Closed | Mr. MD Saleem
10 | South | 211593869 | 2025-10-01 09:29 | 15 | GP3.8501.../2421483 | red lamp alarm Call by : Customer Name :Kanthraj Contact :9591637383 | Task Start | M/s. Venkatadri Fuels | 24 | update pending |  | Mr. Anil Kumar H G
11 | South | 211607528 | 15-01-2025 09:47 | 30 | 3H.8902.../2420738 | low speed problem Call by : Customer Name :.DR.Paws Contact :7760327586 | Task Start | M/s. Dr. Paws. | 40 | Visited the site as per the customer's complaint. Inspected the engine, including the fuel line, fuel filter, engine oil level, battery distilled water, radiator coolant level, V-belt, and air filter. Checked the control unit and alarm system, connected diagnostic tools to check SPN and FMI codes, verified all engine connections, and started the engine. | Closed | Mr. Anil Kumar H G
12 | South | 211606782 | 14-01-2025 17:29 | 15 | GP3.8501.../2420824 | Starting issue Call By Customer Name- Satish No-9448025132 | Task Start | C. R. Fuels. | 348 | 190/4, 244/8, LLOP switch wire loose so tighten the wire& clear the DTC | Closed | Mr. Anil Kumar H G
13 | South | 211606663 | 14-01-2025 16:46 | 20 | GP3.8601.../2421342 | Display Issue & Battery Under Voltage Issue. Call By Customer. Name:- jitu .. Mobile No.:- 8139809294 | Task Start | FATHIMA HYPER MARKET | 7 | Battery voltage (10v) low. EB supply not given to battery charger. SE connected the EB supply. | Closed
14 | South | 211606153 | 14-01-2025 15:51 | 25 | GP3.8702.../2421120 | Display & abnormal sound problem Call by : Customer Name : Mohammad Contact : 7259313410 | Task Start | Arabian Palace | 14 | 2791/18, 2791/6, 5838/1 Egr fault code. So SE flash the dummy file. Working ok | Closed
15 | South | 211605978 | 14-01-2025 14:23 | 20 | GP3.8601.../2420850 | Tripping Problem Call by : Customer Name : Shinu Das Contact : 9048519008 | Task Start | PRAKASH EXPORTS |  | Voltage not showing on controller | Task start |  | Failed Part
16 | South | 211605727 | 14-01-2025 12:21 | 200 | 6H.8435.../2420094 | INSTANCE ID: 100769889 SITE ID: T9TX DG ISSUE: DG STARTING ISSUE NAME: AKSHAY CONTACT NUMBER: 6282748817 | Closed | Reliance Retail Limited | 205.1 | 110/16 error code. Found belt loose tighten the belt. Clear the dtc now working ok | Closed
17 | South | 211605539 | 14-01-2025 11:12 | 125.4 | 4H.8041.../2420970 | Oil Leakage Issue Call By Customer Name :- Sachin Mobile No :- 7879323284 | Open | Malwa Infracon Pvt. Ltd. |  | Visit pending | open | Mr. Anil Kumar H G
18 | South | 211605152 | 14-01-2025 09:39 | 40 | 3H.8951.../2420527 | Tripping Issue Call By Service Dealer Name - Sachin sir Number - 9663836891 | Task Start | Suvidha Namma Super Market. | 106 | Checked the fuel line and battery connections, found them okay. Started the engine, run for 2 minutes under load, but it tripped suddenly without any alarm. Inspected the fuel line and tightened all panel board wiring. Restarted the engine with load; no further tripping observed. Currently under observation. | Closed | Mr. Anil Kumar H G
19 | South | 211604282 | 13-01-2025 17:22 | 250 | F6.8841.../2420044 | Starting/Stopping Issue | Completed | THE URALUNGAL LABOUR CONTRACT CO OPERATIVE SOCIETY |  | update pending | Completed
20 | South | 211603504 | 13-01-2025 15:34 | 250 | F6.8841.../2420210 | Automation Issue Email By - GOEM Name - M.K.GURUMURTHY | Closed | Rinac India Limited | 15 | checked engine battery discharge so engine not start,due to engine controller on and battery charger off mode | Closed | Mr. Anil Kumar H G
21 | South | 211603212 | 13-01-2025 15:13 | 25 | GP3.8702.../2420738 | DG Battery faulty | Under Monitoring | ATC Telecom Infrastructure Private Limited | 25 | checked the battery distilled water level ok, checked the battery volt without battery charger 3 volt only, checked the battery charger output on Battery cables, battery charger supply not coming on battery cables, checked the controller wiring connection, battery charger out put connection on 2C&1c2 connect, after remove the 2C wire ,after connect the wire 2A, checked the battery charger out put voltage 13.95,connect the battery cables on battery, checked the battery voltage on 13.20, battery on charging, informed the customer, customer ok on battery charger via battery charging, tomorrow inform on battery status, | Under monitoring
22 | South | 211603018 | 13-01-2025 14:15 | 125.4 | 4H.8042.C4../2420113 | Oil Leakage Issue Email by Customer Name - ATS ENERGIES PRIVATE LIMITED | Closed | ATS ENERGIES PRIVATE LIMITED | 56 | checked engine oil leakage from FIP oil supply pipe due to improper hose crimping | Closed | Mr. Anil Kumar H G
23 | South | 211602860 | 13-01-2025 13:22 | 0 | T4.8941.../2421866 | fuel leak problem | Task Start | SUNBEAM GENERATORS PVT LTD | LR | fuel filter, hand priming not working, so replace the filter | Closed | Mr. NandhaGopal
24 | South | 211602543 | 13-01-2025 12:20 | 58.5 | T4.8941.../2422396 | AMF Pannel Problem Call by : Customer Name :Satheesh Contact :9746133341 | Open | Cedar Retail Pvt. Ltd. | 1.46 | Not starting in auto mode, check and found atuo sensoning wire loose in AMF panel, tighten the wire | Closed | Mr. Sanjaimon S
25 | South | 211602462 | 13-01-2025 11:58 | 58.5 | T4.8941.../2421646 | Leakage Issue | Task Start | PALM TREE SHOPPING PRIVATE LIMITED | 191 | fuel level sensor wire problem, crimping broken | Closed | Mr. Sanjaimon S
26 | South | 211602419 | 13-01-2025 11:54 | 25 | GP3.8702.../2421253 | Starting Problem Call by : Customer Name :Vijay kumar Contact :9895926125 | Task Start | Axis Bank Ltd | 3.21 | found emergency Stop connection. 1H connection is open in control panel.so remove the connection and rearrange it | Closed | Mr. Anil Kumar H G
27 | South | 211602374 | 13-01-2025 11:45 | 0 | 6H.8435.../2420142 | CAC HOSE PROBLEM | Task Start | SUNBEAM GENERATORS PVT LTD | LR | CAC hose broken, replace the hose | Closed | Mr. NandhaGopal
28 | South | 211602364 | 13-01-2025 11:39 | 0 | T4.8941.../2421966 | FUEL LEAK PROBLEM | Open | SUNBEAM GENERATORS PVT LTD |  | Cancelled | Cancelled | Mr. NandhaGopal
29 | South | 211602012 | 13-01-2025 10:25 | 20 | GP3.8601.../2421250 | Fuel Level Sensor Problem Call by : Customer Name : Sampath kumar Contact : 9894782881 | Task Start | MURUGAN AGENCIY | 14.6 | Fuel level stuck, also not working, so replace the sensor | Closed | Mr. NandhaGopal
30 | South | 211602001 | 13-01-2025 10:16 | 400 | DV8.8542.C4../2420078 | Voltage problem Call by : KGD Name : Gaffer Contact : 7660011834 KGD Number: 8099566271 | Task Start | Tellapur Technocity Private Limited | 23 | customer side panel contactor trip | Closed | Mr. MD Saleem
31 | South | 211601894 | 13-01-2025 09:36 | 25 | GP3.8702.../2421634 | Starting Problem Call by : Customer Name :Senthil Kumar Contact :7025086344 | Task Start | Senthil | 2 | not starting, under speed alarm, increases under speed delay time from 2 sec to 6 sec | Closed | Mr. Anil Kumar H G
32 | South | 211601889 | 13-01-2025 09:33 | 20 | GP3.8601.../2421300 | Starting Problem & Alarm problem Call by : Customer Name :Ajith Sebastian Contact :7708272478 | Closed | Sri Jwalamukhi Homes | 44.2 | emergency switch activated alarm in Control panel controller, wire 11 got loose contact in wiring harness, | Closed | Mr. Anil Kumar H G
1 | East | 211607895 | 15-01-2025 11:43 | 58.5 | T4.8941.../2422049 | Provide PM sr | Open | SECURITY HI TECH GRAPHICS PVT LTD. | 40 | Customer required service no issue in DG | CLOSED | Prosanjit saha
2 | East | 211606793 | 14-01-2025 17:35 | 58.5 | T4.8941.../2420371 | Emergency Stop Alarm Issue Call By Customer Name - Behra .. Number -9556800599 | Open | Shree Binayak Textile | 56 | Found pressed the Emergency stop switch so SE released the emergency stop switch issue resolved | CLOSED | Ujjwal Das
3 | East | 211604590 | 13-01-2025 19:46 | 30 | 3H.8902.../2420816 | Automation Issue Call By Customer Name - Ashok Kumar Number - 8249408483 | Open | Abis Exports I. Pvt. Limited. . | 45 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das
4 | East | 211606834 | 14-01-2025 18:03 | 45 | 3H.8951.../2421369 | Diesel Leakage & Silencer Broken Call By Service Dealer Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. | 64 | visit pending | OPEN | Prabhakar Kumar
5 | East | 211601117 | 2025-12-01 08:53 | 30 | 3H.8902.../2422023 | Starting Issue Call By Customer Name :-Satpal Sharma Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS |  | Visit pending | OPEN | Ujjwal Das
6 | East | 211602942 | 13/01/2025 13:53:22 | 400 | DV8.8542.C4../2420023 | Error issue Email By - Customer Name - Neeraj Mishra | Task Start | Mr. Ravindra Patel | 14 | SE visited site found 516166 code so cleared code by connecting Ikonnect, found no other fault code in DTC tested DG on load found ok. | OPEN | Prabhakar Kumar
1 | South | 211609395 | 15-01-2025 19:48 | 5.5 | CC1.1013.../2400024 | Genset Trip | Open | HEGDAL CONSTRUCTIONS | NA | visit pending | Open | Mr. Anil Kumar H G
2 | South | 211609388 | 15-01-2025 19:18 | 125.4 | 4H.8041.../2320068 | Out Put problem Call by : Customer Name :Sudhi Contact :8943649197 | Open | POWERMECH DIESELS | NA | Cancelled | Cancelled | Mr. Sanjaimon S
3 | South | 211609353 | 15-01-2025 18:48 | 25 | GP3.8702.../2421061 | Red lamp alarm issue Called by customer Name Shivayya Swamy: Number: 9008528421 | Open | GUTTI SHANTHI | 16 | Red alarm, clear the DTC | Task start | Mr. Anil Kumar H G
4 | South | 211608779 | 15-01-2025 15:52 | 58.5 | T4.8941.../2422362 | Automation issue Call by KGD Name: Jamuna Number:9036094197 | Closed | MANJUNATH | 15 | No issue found, just adjust the door beeding | Closed | Mr. Anil Kumar H G
5 | South | 211608651 | 15-01-2025 15:18 | 30 | 3H.8902.../2421843 | Starting Problem | Task Start | Axis Bank Ltd | LR | DG not starting as the EGR Valve issue, flash the dummy file, but still the issue not resolved, need to replace the EGR valve | Task start | Mr. NandhaGopal | KRM Check
6 | South | 211608470 | 15-01-2025 14:25 | 125.4 | 4H.8041.../2420605 | Canopy Door Lock Issue Call By Customer Name :-Vinay Kumar Mobile No :-9143659659 | Closed | Dhruva Women & Child Hospitals | 26.59 | Door lock issue, adjust the door lock | Closed | Mr. MD Saleem
7 | South | 211608460 | 15-01-2025 14:19 | 15 | GP3.8501.../2421721 | AMF Panel Problem Call by : Customer Name :Nazeer Contact :9846175175 | Closed | CHOCO LUSH | 8 | Site attend and checked engine all components after changed start delay seconds as per customer request (30 sec to 5 sec) After tested engine run condition and automation found ok | Closed | Mr. Sanjaimon S
8 | South | 211608343 | 15-01-2025 13:41 | 250 | F6.8841.../2420399 | Ad blue level variation | Closed | St. AUGUSTINES FORANE CHURCH | 105 | Ad blue level variation in some time engine starting, then remove Ad blue tank cap and check Ad blue level in tank ,then remove connections and check QLT sensor check, remove and reconnect the sensors, some loose connection are cleared, all error codes, then check all parameters from the engine, then start the engine | Closed | Mr. NandhaGopal | Under Observation
9 | South | 211608311 | 15-01-2025 13:30 | 25 | GP3.8702.../2420754 | Dg issue | Cancelled | ATC Telecom Infrastructure Private Limited |  | Cancelled | Cancelled | Mr. Anil Kumar H G
10 | South | 211610755 | 16-01-2025 12:31 | 20 | GP3.8601.../2421692 | Oil Leakage Issue Call By Customer Name :- Sidhhesh Mobile No :-9526023109 | Open | M/s. PARASSINI BAKERS | 12.9 | oil leakage from turbro in pipe, tighten the clamp | Task start | Mr. Anil Kumar H G
11 | South | 211610712 | 16-01-2025 12:21 | 20 | GP3.8601.../2420203 | Under speed problem Call by : Customer Name : YESU Contact : 9959779289 | Task Start | S. R. Biz Spot. | 3 | Airlock issue customer due to low diesel in tank | Task start | Mr. NandhaGopal
12 | South | 211610672 | 16-01-2025 12:13 | 500 | DV8.8501.C4../2420117 | Electrical Problems | Task Start | SURYA VASTHRALAYAM PRIVATE LIMITED | 1.13 | tripping.after detailed inspection found that genset tripping due to earth fault.so need to detailed inspection | Task start | Mr. Sanjaimon S | Details Required
13 | South | 211610636 | 16-01-2025 12:07 | 30 | 3H.8902.../2421826 | Tripping issue Call By Customer Name :- Praveen Mobile No :-7829532149 | Task Start | M/s.VAIBHAVI DIESEL | 12.15 | dg trip while running emergency stop alarm.check emergency switch.check the wiring connections of emergency switch.the positive wire has loose connections, tighten the wire .and put the cable ties. | Task start | Mr. Anil Kumar H G
14 | South | 211610476 | 16-01-2025 11:35 | 125.4 | 4H.8041.../2320068 | Output issue | Task Start | POWERMECH DIESELS | 20 | confirmed that no output issue due to MCCB trip. then reset the MCCB | Closed | Mr. Sanjaimon S | Under Observation
15 | South | 211610420 | 16-01-2025 11:11 | 0 | 5H.5351.../2520025 | FUEL LEAKAGE-NANDAN | Task Start | AJAX ENGINEERING PRIVATE LIMITED |  | visit pending | Task Start | Mr. Anil Kumar H G
16 | South | 211610158 | 16-01-2025 10:05 | 25 | GP3.8702.../2420346 | Coolent Leakage problem Call By : Customer Name : Sham Shivrao Contact No : 8346965568 | Task Start | Linga Innovation | 3 | coolant leakage from radiator hose | Closed | Mr. NandhaGopal
17 | South | 211610147 | 16-01-2025 09:57 | 0 | 5H.5106.../2400003 | Starting Issue Email by OEM Name - BULL MACHINES PVT LTD | Task Start | MUGRODY CONSTRUCTION WORKS | 145 | checked the engine oil level in oil dipstick high level ok.so advice the customer no oil level low in dipstick.currectly checked and rifitted the oil dipstick. | Closed | Mr. Anil Kumar H G
18 | South | 211610050 | 16-01-2025 09:14 | 200 | 6H.8435.../2420152 | Starting/Stopping Issue | Completed | PARVA BALAJI PROJECTS | 123 | adblue level low, top-up the adblue | Closed | Mr. Anil Kumar H G
1 | NORTH | 211611028 | 16-01-2025 12:44 | 500 | F6.8843.C4../2420002 & 2420002 | VOC -MAINTENANCE ALARM RESET Customer Name -Devendra Singh Customer Number -9193530008 Mode- SR Generated through CDI calling. | Open | Brij Healthcare & Research Centre. |  | Cancelled-SR open by mistake | Cancelled | Sudhir Awasthi
2 | NORTH | 211610711 | 16-01-2025 12:21 | 500 | DV8.8501.C4../2420075 | Error Code issue Call By Customer Name :- Ram Kumar Mobile No :- 9999011576 | Task Start | SANDHAR TECHNOLOGIES LIMITED | 52 | SPN/FMI 1761/15, 523584/15 low def level topup the def, clear the dtc then issue resolve | Closed | Kapil Solanki
3 | NORTH | 211610651 | 16-01-2025 12:06 | 320 | F6.8802.../2420300 | ICU Protect Alaram. Call by customer. Name:- Gaurav Khanna Mobile No.:- 9034000731 | Task Start | Marvel Home Fashion | 31.33 | SPN/FMI-655/5 ; Found in Injector no. 5 Blue wire broken so re-connected the same & resolve the issue | Closed | Ved Prakash Gupta
4 | NORTH | 211610644 | 16-01-2025 12:02 | 57 | T4.8941.../2320085 | Battery issue Call By Customer Name ;-Sachin Khare No :- 9999436017 | Task Start | Sunder Mavi Hospital |  | Update pending | OPEN | Kapil Solanki
5 | NORTH | 211610625 | 16-01-2025 12:02 | 20 | GP3.8604.../2420082 | Undervoltage tripping issue | Task Start | Reliance Jio Infocomm Limited | 490 | Flash the controller for the under voltage alarm | Closed | Sudhir Awasthi
6 | NORTH | 211610559 | 16-01-2025 11:51 | 25 | GP3.8702.../2420023 | Automation issue Call by Customer Name : Pradeep Varma No : 9818448984 | Task Start | Pradeep Verma | 63 | Battery voltage low, Check electrolite level ok then check voltage found 11.5 then check the charger found charger output voltage 12V after replace the Battery charger - then check voltage after 30 min. found 12.2V | Closed | Kapil Solanki | Under Observation
7 | NORTH | 211610533 | 16-01-2025 11:42 | 40 | 3H.8951.../2420081 | VOC -ABNORMAL SOUND DUE TO LOOSING OF ANY FASTENERS OF ACCESSORIES Customer Name -Sahil Sharma Customer Number -9953965999 Mode- SR Generated through CDI calling. | Open | NEW BHARDWAJ ELECTRICAL WORKS |  | Visit pending | OPEN | Kapil Solanki
8 | NORTH | 211610475 | 16-01-2025 11:34 | 58.5 | T4.8941.../2420927 | Leakage Issue | Completed | Riddhima Foods |  | Control panel wiring harness, burnt due to Emergency wire touch to MCB to R-phase | OPEN | Sudhir Awasthi | Details Required
9 | NORTH | 211610411 | 16-01-2025 11:15 | 40 | 3H.8951.../2420522 | Automation Issue Call By Customer Name - Ritik Mobile No -8307767638 | Task Start | Axis Bank Ltd | 7 | Dg was found in manual mode but customer complaint as not starting in Auto mode;same educated to customer | Closed | Ved Prakash Gupta
10 | NORTH | 211610401 | 16-01-2025 11:09 | 40 | 3H.8951.../2420304 | Leakage Issue | Task Start | Aman Surgical Center | 91 | Coolant leakage from radiator to waterpump hose Clamp loose tightness the same | Closed | Sudhir Awasthi
11 | NORTH | 211610338 | 16-01-2025 10:54 | 15 | GP3.8501.../2420456 | diesel leakage Call By Customer Name :- Pritesh Mobile No :-7710502200 | Task Start | Jagdeep Kaur | 133 | Fuel Leakage due to Fuel pipe clamp found faulty(electronic pump to Filter) so replace the clamp & resolve the issue | Closed | Ved Prakash Gupta | Details Required
12 | NORTH | 211610299 | 16-01-2025 10:45 | 30 | 3H.8902.../2420617 | Automation issue. | Task Start | Arshad Husian. | 94.33 | DG Stops when occurred on Auto mode,found 1C2 wire loose in Pannel at Distribution block so re-connected & run the DG,Issue resolved | Closed | Ved Prakash Gupta
13 | NORTH | 211610248 | 16-01-2025 10:32 | 7.5 | D3.8305.../2400128 | ENGINE STARTING ISSUE | Task Start | ICICI Bank | 5.3 | Update pending | OPEN | Sudhir Awasthi
14 | NORTH | 211610206 | 16-01-2025 10:20 | 40 | 3H.8951.../2420218 | Electrical Problems | Task Start | Ambrish Daga | 26 | Found Voltage flactuation issue then check & found AVR Blue wire loose tightness the same then issue resolve- Engineer not taken the photo | Closed | Kapil Solanki
15 | NORTH | 211610139 | 16-01-2025 10:02 | 200 | 6H.8435.../2420205 | Electrical Problems | Task Start | Aisshpra Gems & Jewels. | 736 | High adblue alarm flash the ecu issue resolve | Closed | Sudhir Awasthi | Details Required
16 | NORTH | 211610129 | 16-01-2025 09:57 | 500 | DV8.8501.C4../2420048 | Urea Issue. Call by Customer. Name:- Rajkumar . Mobile No.:- 9467425910 | Task Start | Shahi Dyeing Pvt. Ltd. | 571 | SPN/FMI 4331/1, 4384/1, 1761/14, 4426/15, 1761/15, 523584/15, 4441/5, 4376/4, 523576 110/0 all error code clear-under observation | OPEN | Kapil Solanki
17 | NORTH | 211610093 | 16-01-2025 09:47 | 500 | DV8.8501.C4../2320030 | Coolant Leakage issue. Call by Customer. Name:-Fahim . Mobile No.:- 9084764335 | Task Start | Sobha Ltd. | 270 | Coolant leakage from radiator to waterpump hose Clamp loose tightness the same then issue resolve | Closed | Kapil Solanki
18 | NORTH | 211610090 | 16-01-2025 09:44 | 400 | DV8.8542.C4../2420026 | Door Lock issue Call By Customer Name :- Amith Kumar Mobile No :- 9540978813 | Task Start | SHREE NURSINGSAHAY MUDUNGOPAL ENGINEERS PVT LTD.. | 6.2 | Door lock not proper lock after adjust the lock | Closed | Kapil Solanki
19 | NORTH | 211610083 | 16-01-2025 09:37 | 125.4 | 4H.8041.../2320108 | RPM Issue. Call By customer. Name:- Vijay Kumar Mobile No.:- 9829973147 | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | 167 | Sulphur accumulated in Battery terminal, Clean the terminal the charge the battery After start the DG the issue reolve | Closed | Gourav Sharma
20 | NORTH | 211610070 | 16-01-2025 09:27 | 400 | DV8.8542.C4../2420086 | Sound Problem | Task Start | Apollo Hospitals (Indraprastha Medical Corporation Ltd.) | LR- | Abnormal sound from the Engine, Engine will be dismantle | OPEN | Kapil Solanki
21 | NORTH | 211610033 | 16-01-2025 08:14 | 58.5 | T4.8941.../2421994 | Starting Issue Call By Customer Name :-Omveer Singh Mobile No :7011204885- | Task Start | CHAUDHARY GENERATOR SERVICE | 280 | SPN/FMI 100/3 High oil pressure Check the wiring harness conection found ok but during night DG run 3 to 4 hours then show the alarm | OPEN | Kapil Solanki | KRM Check, Under observation
22 | NORTH | 211609370 | 15-01-2025 19:18 | 58.5 | T4.8941.../2423036 | Battery Charging Issue Email By KGD Name:-Pradeep Tyagi | Task Start | S S Jain Traders | 87 | Charging Over Voltage Alarm occured;DC Alternator Voltage found more than usual(17 V),Alternator has been tested previously(25 December) , Will check same Today with Float Battery to test Battery cell are shorted or not | OPEN | Sudhir Awasthi
23 | NORTH | 211609313 | 15-01-2025 18:24 | 625 | DV0.8501.C4../2320023 | High oil consumption Call by Customer Name : karan singh No : 9643330742 | Open | KW SECURITY AND SERVICES PRIVATE LIMITED | 37 | Wrong reporting sr-Customer panel side issue | Closed | Kapil Solanki
24 | NORTH | 211609037 | 15-01-2025 17:15 | 15 | GP3.8501.../2420657 | INSTANCE ID:-100776816 SITE ID:- 13771 CALL BY CUSTOMER// DG ISSUE:- DG ALARM/AUTOMATIC STARTING ISSUE NAME:- MAHESH NUMBER:- 8800250303 | Closed | BHARTI AIRTEL LIMITED | 3 | Customer panel side problem-Customer panel relay may be defective accordingly to Engineer | Closed | Kapil Solanki
25 | NORTH | 211609063 | 15-01-2025 17:06 | 15 | GP3.8501.../2420389 | Starting issue | Closed | Suresh Kumar Rathee. | 142 | Starting Issue due to 2A1 fuse found faulty in Pannel & resolve the Issue | Closed | Ved Prakash Gupta
26 | NORTH | 211608908 | 15-01-2025 16:28 | 20 | GP3.1021.../2420369 | INSTANCE ID:-100779503 SITE ID:-I-UE-SANS-ENB-G001 CALL BY CUSTOMERA:- DG ISSUE :- DG UNDER VALTAGE ISSUE NAME :- Adarsh Pandey NUMBER :- 9559883130 | Closed | Reliance Jio Infocomm Limited | 124 | Under voltage alarm, flash the controller after issue resolve | Closed | Sudhir Awasthi
27 | NORTH | 211608858 | 15-01-2025 16:15 | 125.4 | 4H.8041.../2420257 | Voltage Fluctuation and Automation issue Call By Customer Name :- Ram Kishore Mobile No :- 9024470308 | Closed | SHRI KRISHANA GOPAL GAU SEWA SAMITI | 39.4 | Update pending | OPEN | Gourav Sharma
28 | NORTH | 211608841 | 15-01-2025 16:02 | 15 | GP3.8501.../2420105 | Starting issue Call By Customer Name :- Panday Mobile No :- 8383912867 | Closed | Tuteja Steel Corporation. | 34 | Dg not start in Auto customer side panel issue, but check in manual condition found running ok | Closed | Kapil Solanki
29 | NORTH | 211608840 | 15-01-2025 16:02 | 58.5 | T4.8941.../2423265 | Preventive maintenance Call By Customer Name- ASHWANI BHATIA ... Mo.No.- 9810276717 | Task Start | ANMOL TECHNO CRAFT | 23 | Update pending | OPEN | Kapil Solanki
30 | NORTH | 211608740 | 15-01-2025 15:44 | 50 | T4.8941.../2422781 | Starting/Stopping Issue | Task Start | Axis Bank Ltd | 2.15 | Canopy Lock found faulty ; applied oil on same & resolve the issue,Fuel level found low so top-up the same & start the DG,Running fine | Closed | Ved Prakash Gupta
31 | NORTH | 211608703 | 15-01-2025 15:34 | 125.4 | 4H.8041.../2420484 | Abnormal Sound issue call by KGD name - Pushpender Kour no - 9357612800 | Open | Guru Nanak Cardiac Care Hospital | 88 | Customer raised complaint as abnormal sound but no such issue observed on site ; same told to customer | Closed | Ved Prakash Gupta
32 | NORTH | 211608662 | 15-01-2025 15:22 | 160 | 6H.8475.../2420209 | VOC -Code error is showing on display Customer Name -Davinder Tyagi Customer Number -9258016233 Mode- SR Generated through CDI calling. | Closed | VINAYAK TRANSCO PRIVATE LIMITED | 17 | SPN/FMI 3031/14 High adblue alarm, flash the file issue resolve | Closed | Kapil Solanki
33 | NORTH | 211608623 | 15-01-2025 15:05 | 62.5 | T4.8941.../2420125 | Starting/Stopping Issue | Closed | RS. Udhyog | 49 | ECU Protect Alarm occurred with 97/5 ; found leakage from Water Separator Filter slightly So Open & clean the same ,Issue resolved after re-fitted | Closed | Ved Prakash Gupta
34 | NORTH | 211608564 | 15-01-2025 14:51 | 15 | GP3.8501.../2420099 | AMF Panel issue Call By Customer Name :- Shweta . Mobile No :- 9958891400 | Closed | Vijay Kumar. | 11.38 | Customer select on manual mode then Engineer select the auto mode in controller then start the DG auto & manual both condition after that issue resolve | Closed | Kapil Solanki
35 | NORTH | 211608473 | 15-01-2025 14:26 | 82.5 | 5H.8901.../2420288 | Coolant Leakage issue Call By Customer Name :- Saurabh Mobile No :- 6393101926 | Closed | Dy Commissioner Administration trade tax | 55 | Coolant leakage from radiator to waterpump hose Clamp loose tightness the same & low def level topup the def issue resolve | Closed | Sudhir Awasthi
1 | North | 211613352 | 17-01-2025 10:58 | 200 | 6H.8435.../2320031 | Sound/Vibration Issue | Task Start | OIL INDIA LTD. | 1529 | Fan belt broken, replace the belt call from KOEL team-Update pending | OPEN | Gourav Sharma | Frist change -652, second change- 734 hour ,thierd change-1510 hour
2 | North | 211613220 | 17-01-2025 10:24 | 58.5 | T4.8941.../2423193 | Display Issue Call By Customer Name :- Deepu Mobile No :-9587073666 | Open | D D Engineering Work | 71.48 | Diesel sensor issue Controller not showing the Fuel Level option then set from contoller after show the Display & Check now show Circuit open & Door lock problem - Engineer visit again | OPEN | Gourav Sharma | Details Required
3 | North | 211613003 | 17-01-2025 08:09 | 58.5 | T4.8941.../2422379 | Starting Issue Call By Customer Name:-Deepak Ji No:-9312703668 | Open | ASHOK DADHICH | 31 | Airlock in fuel line, remove the air after start the Dg running ok, then issue resolve | Closed | Gourav Sharma
4 | North | 211611912 | 16-01-2025 16:36 | 20 | GP3.8604.../2420117 | INSTANCE ID:-100741915 SITE ID:- I-RJ-BNSU-ENB-G004 CALL BY CUSTOMER\\ DG ISSUE:-DG ISSUE NAME-Lukendra NUMBER:-9351228578 | Task Close | Reliance Jio Infocomm Limited | 150 | Controller show the Under voltage alarm then suggested by koel team flash the Ecu | Closed | Gourav Sharma
5 | North | 211611656 | 16-01-2025 15:36 |  | DV8.8508.C4../2420003 | line rejection | Task Start | Jakson & Company | LR | Controller show the Coolant level switch So, ASE Change the controller Version, version change A old Change into version A08 & according update the software | Closed | Gourav Sharma
6 | North | 211611648 | 16-01-2025 15:32 |  | DV8.8508.C4../2420006 | LINE REJECTION | Closed | Jakson & Company | LR | Controller show the Coolant level switch So, ASE Change the controller Version, version change A old Change into version A08 & according update the software | Closed | Gourav Sharma
7 | North | 211611641 | 16-01-2025 15:29 |  | DV8.8508.C4../2420008 | LINE REJECTION | Closed | Jakson & Company | LR | Controller show the Coolant level switch So, ASE Change the controller Version, version change A old Change into version A08 & according update the software | Closed | Gourav Sharma
8 | North | 211618054 | 18-01-2025 11:36 | 125.4 | 4H.8041.../2420083 | Low Battery Voltage Alarm Call By Customer Name :- Anup Gopinath Mobile No :- 9995389057 | Task Start | Algo Industries | 55 | Battery charger connection not done from customer end, Connect the charger battery charge- Today take the update from customer | Closed | Gourav Sharma
9 | North | 211615162 | 17-01-2025 15:30 |  | DV8.8508.C4../2420006 | LINE REJECTION | Closed | Jakson & Company | LR-1 | DG hunting problem, Change trottle valve after that same issue found then change the ECU after that issue resolve | Closed | Gourav Sharma
10 | North | 211615050 | 17-01-2025 15:20 | 58.5 | T4.8941.../2423031 | Electrical Problems | Closed | SHRI BANDE KA BALAJI | 29 | update pending | OPEN | Gourav Sharma
11 | North | 211614489 | 17-01-2025 13:11 | 750 | DV2.8501.C4../2420036 | Voltage Fluctuation | Completed | M/S G S PHARMBUTOR PRIVATE LIMITED | 82 | Customer Sync. Panel issue- Customer run the DG running ok but DG stopping time 3min. But customer panel stopping time low so, panel show the alarm | Closed | Kapil Solanki
12 | North | 211614484 | 17-01-2025 13:08 | 20 | GP3.8601.../2320039 | Starting/Stopping Issue | Task Start | Mohammad Wali | 1192 | Low electrolite level topup the elecrtrolite charge the battery issue resolve | Closed | Kapil Solanki
13 | North | 211614312 | 17-01-2025 12:42 | 20 | GP3.1010.../2300003 | Low Battery Voltage Alarm Call By Customer Name :- Ravinder . Mobile No :- 9667939908 | Task Start | Hosexperts | 60.36 | Battery water low so battery water top-up | Closed | Kapil Solanki
14 | North | 211613395 | 17-01-2025 11:10 | 250 | DV8.9840.../2420009 | Starting Issue Call By Customer Name :- Pradeep Yadav Mobile No :- 8527090334 | Task Start | METAFLEX DOORS INDIA PRIVATE LIMITED. | 9.21 | SPN/FMI 3227/17 Pressure flactute so set the pressure from ZPR 4.2 but now pressure not below 4 to 5 above set & leakage the gas now Engineer use the taflon tape fitting & Educate the customer for close the gas leakage | Closed | Kapil Solanki
15 | North | 211613384 | 17-01-2025 11:04 | 30 | 3H.8902.../2421841 | Load issue Call By Customer Name :- Sameer Bajaj Mobile No :- 9717332008 | Task Start | RED BEACON LLP | 1.45 | Unbalance load, R-0, Y-2, B-10 Educate the customer for balance the Load | Closed | Kapil Solanki
16 | North | 211613097 | 17-01-2025 09:57 | 125.4 | 4H.8041.../2420182 | Starting/Stopping Issue | Task Start | Sunil Generators | 140 | Wrong report SR by Customer- Customer need to DEF so SR will be open by customer | Closed | Kapil Solanki
17 | North | 211613058 | 17-01-2025 09:48 | 125.4 | 4H.8041.../2320180 | Starting issue Call by customer Name: Ramesh Number:8506043972 | Task Start | C. M. Infrastructure Pvt. Ltd. | 92 | Found Battery voltage low because Wrong connection fiited on relay board (P1- 2C1)& (O1-2C) | Closed | Kapil Solanki | Service History
18 | North | 211613024 | 17-01-2025 08:47 | 40 | 3H.8951.../2320059 | Starting Issue Call By Customer Name :-Kishan Pal ... Mobile No :- 9582450595 | Closed | Shiva Cares HP. Petrol Pump | 415 | Battery voltage low, battery charger off from customer end So, battery discharge | Closed | Kapil Solanki
19 | North | 211613020 | 17-01-2025 08:15 | 125.4 | 4H.8041.../2320009 | Electrical Problems | Task Start | Dr. Pardeep Berry, MS Amita Singh, Miss Aditi Mathur | 37 | Wrong report by customer- Customer panel side problem | Closed | Kapil Solanki
20 | North | 211612999 | 17-01-2025 07:59 | 500 | DV8.8501.C4../2420009 | Trip_Genset_Low_Voltage | Open | QH. Talbros Private Limited |  | Under Cancellation- | Cancelled | Kapil Solanki
21 | North | 211612390 | 16-01-2025 19:14 | 125.4 | 4H.8041.../2420683 | Starting Issue Call By Customer Name - VIPIN KATHURIA S FASTNERS Number - 9891500846 | Closed | S. FASTNERS | 68.1 | Battery voltage low because battery charger connection not be done because customer site working on fitting work so, charger connection done temprary | Closed | Kapil Solanki
22 | North | 211611946 | 16-01-2025 16:42 | 58.5 | T4.8941.../2422111 | Power Supply Issue. Call by Customer. Name:- Mundra Kumari Mobile No.:-8800283254 | Task Start | Himanshu Yadav. | 26 | Customer panel side issue | Closed | Kapil Solanki
23 | North | 211618379 | 16-01-2025 14:39 | 125.4 | 4H.8041.../2320189 | Starting/Stopping Issue | Closed | Rohit Industries | 152 | When start the DG, DG crank for 3sec, but not start cranking time 6sec. & under speed time 3sec. So DG show the under speed alarm then under speed alarm timing increase for 10sec. After that DG start | Closed | Kapil Solanki | KRM Check , Under Observation
24 | North | 211611354 | 16-01-2025 14:11 | 160 | 6H.8475.../2420022 | Starting/Stopping Issue | Closed | Technologica Infotech Ltd. | 10 | Auto panel issue Mains MCB trip So, DG not start in Auto, | Closed | Kapil Solanki
25 | North | 211618480 | 18-01-2025 12:58 | 57 | T4.8941.../2320025 | Leakage Issue | Task Start | PSG ELECTRICALS | 61 | Leakage from Water seprator to FIP pump pipe benjo bolt loose and tightened the bolt leakage stopped | Closed | Kapil Solanki
26 | North | 211618397 | 18-01-2025 12:36 | 125.4 | 4H.8041.../2320163 | Automation Issue Call By Customer Name :- Rajeev . Mobile No :- 8459775078 | Task Start | Panchachuli Sehkari Aavak Samiti | 142 | SPN/FMI 3031/14 High adblue alarm Flash the file | Closed | Kapil Solanki
27 | North | 211618091 | 18-01-2025 11:42 | 30 | 3H.8902.../2420416 | Starting/Stopping Issue | Task Start | M/s Aashima Fuel & Gas Station | 2.59 | DG trip due to MCB supply wire loose tightness to be all then issue resolve | Closed | Kapil Solanki | Details required
28 | North | 211617724 | 18-01-2025 10:22 | 125.4 | 4H.8041.../2420712 | Starting Issue Call By Customer Name :Ajay .- Mobile No :- 9953427214 | Task Start | SPAN INDIA PRIVATE LIMITED | 11 | NRV found chocked Clean the NRV after issue resolve | Closed | Kapil Solanki | Tank check, Commisioning date check
29 | North | 211616636 | 17-01-2025 21:01 | 82.5 | 5H.8901.../2420130 | Door not lock properly | Closed | Kamla eye foundation pvt ltd | 88 | Door lock not proper close, adjust the door lock | Closed | Kapil Solanki
30 | North | 211616525 | 17-01-2025 18:34 | 125.4 | 4H.8042.C4../2420596 | White & black smoke issue | Task Start | B .S . ENGINEERING | 61 | When DG start in first time then we found Engine gives the white smoke then check & found DOC choked with urea Clean the DOC & clean DM with hot water after trial on load 1 hour found no any issue in last 3 days-Under observation | OPEN | Kapil Solanki | KRM Check, Photos required
31 | North | 211616467 | 17-01-2025 18:17 | 58.5 | T4.8941.../2422321 | Maintanance due alarm issue Call By Customer Name :- Raju .. Mobile No :- 9212005372 | Closed | RAJU GENERATORS | 262 | Maintenance due alarm, reset the alarm | Closed | Kapil Solanki
32 | North | 211616244 | 17-01-2025 17:22 | 200 | 6H.8435.../2320024 | Abnormal Sound Issue Call By Customer Name - Prandhan Kumar Mo No -9661089533 | Task Start | M/s AEW PROTECH PRIVATE LIMITED | 633 | Found Abnormal sound from the DG when check & found Charging alternator mounting bracket bolt was damage | OPEN | Kapil Solanki
33 | North | 211614849 | 17-01-2025 14:41 | 30 | 3H.8902.../2320008 | Automation issue Called by customer Name : Rajneesh Numbe r: 9205336856 | Closed | Mrs. Anju Maini | 16 | Auto panel issue Mains MCB trip So, DG not start in Auto, | Closed | Kapil Solanki
34 | North | 211614713 | 17-01-2025 14:04 | 250 | F6.8841.../2320015 | Electrical Problems | Closed | HIND TERMINALS [P] LTD | 578 | SPN/FMI 3031/14, 3364/8 3031/28, 520527/16, 4365/2, 3033/3 Check wiring connection in panel found no issue then reset the all fault code aftyer trial on load 30min. Found no issue | Closed | Kapil Solanki | Under Observation
35 | North | 211614605 | 17-01-2025 13:33 | 15 | GP3.8501.../2421551 | Voltage Issue Call By Customer Name :- Ashish Kumar Mobile No :- 9878490390 | Open | ALIVA RANI SWAIN | 5 | Mains wire fuse(MR wire) found blown in Pannel so replace the same & resolve the issue | Closed | Ved Prakash Gupta
36 | North | 211614482 | 17-01-2025 13:07 | 58.5 | T4.8941.../2422073 | Starting/Stopping Issue | Task Start | Zealong INC. | 53.65 | Auto Stopping issue due to MCB from mains input to Battery charger & auto connection to pannel found off on site , corrected same & resolve the issue | Closed | Ved Prakash Gupta
37 | North | 211613444 | 17-01-2025 11:17 | 15 | GP3.8501.../2421242 | Inspection/Maintenance | Task Start | ALIF EMPORIUM | 283.2 | Under Cancellation-Resolved on Telephonic discussion | Cancelled | Ved Prakash Gupta
38 | North | 211613411 | 17-01-2025 11:11 | 30 | 3H.8902.../2420081 | Sound/Vibration Issue | Closed | Nav Nirman Contruction Company | 43.45 | Abnormal sound found due to bolt of clamp of Silencer found loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta
39 | North | 211613075 | 17-01-2025 09:41 | 750 | DV2.8501.C4../2420011 | Fan belt broken issue Call by Customer Name : DEVENDER SAINI No : 8607600450 | Task Start | Sleek Brake Products | 945 | Radiator & CAC got damaged due to bearing failure in the fan drive assembly,as per Srideep Mitra Sir,suggested ro arrenge parts to restore DG ; EDO Place for same | Open | Ved Prakash Gupta
40 | North | 211611798 | 16-01-2025 16:15 | 30 | 3H.8902.../2420923 | DG Issue | Task Start | Axis Bank Ltd | 46.1 | Under Cancellation- Not Followed warranty Policy | Cancelled | Ved Prakash Gupta
41 | North | 211611468 | 16-01-2025 14:51 | 250 | F6.8841.../2420348 | Starting/Stopping Issue | Closed | Xaverian Healthcare & Clinincal Lab. | 19 | Emergency switch found pressed on site so release the same & educated to customer | Closed | Ved Prakash Gupta
42 | North | 211618669 | 18-01-2025 13:54 | 82.5 | 5H.8901.../2420054 | Oil Leakage Issue Call By Customer Name :- Ashish ... Mobile No :- 8053646542 | Task Start | Colour Tex Industries Pvt. Ltd. | 180.9 | SPN/FMI-6595/0,3031/15 related to AdBlue quality ,Check the cocentration & Level,found ok,Clean the DEF line & DM with hot water , Remove the code & resolve the issue | Closed | Ved Prakash Gupta | Under Observation
43 | North | 211618257 | 18-01-2025 12:13 | 400 | DV8.8542.C4../2320010 | Starting/Stopping Issue | Task Start | BPCL. Haryana | 226 | Starting issue , found communication failure between ECU & DCU ; DCU not able to flash ; T4 & T6 found interchanged ,corrected same,re-fitted both DCU connector & Flash both ECU & DCU,issue resolved | Closed | Ved Prakash Gupta
44 | North | 211617749 | 18-01-2025 10:26 | 320 | F6.8802.../2420229 | Abnormal Sound Issue Call By Customer Name :- Vikas Mobile No :-7419909382 | Closed | Welfare Association of Roman Court Residents | 59.8 | Abnormal sound found due to Silencer bolt found loose at exhaust silencer end so tightened the same & resolve the issue | Closed | Ved Prakash Gupta
45 | North | 211616426 | 17-01-2025 17:57 | 62.5 | T4.8941.../2320097 | Battery Issue Call By Customer Name - Surendra .. Number - 7988586645 | Closed | Bhajana Home Dacor Private Limited | 372.38 | Battery found failed previously so SR opened for new Battery installation | Closed | Ved Prakash Gupta
1 | South | 211614184 | 17-01-2025 12:22 | 320 | F6.8802.../2420128 | ECU Malfunction Alarm & Tripping issue Call By Customer Name :- Ram . Mobile No :- 8553714764 | Task Start | AMRUTHA RAMA CONSTRUCTIONS PRIVATE LIMITED | 2 | As per customer complaint found 3031/14 code shown in display. So as per RRT team instructions flash the ECU with dummy file (F6_D3.1234_V0). Now issue resolved. Engine running ok. | Closed | Mr. Anil Kumar H G
2 | South | 211613996 | 17-01-2025 11:49 | 125.4 | 4H.8042.C4../2420758 | commissing | Task Start | H A VINOD KUMAR | LR | to check the oil level and coolant level and v belt tension and battery doesn&apos;t connect and silencer not connected and load is not available | Closed | Mr. Anil Kumar H G
3 | South | 211613422 | 17-01-2025 11:12 | 160 | 6H.8475.../2420224 | Starting Problem Call by : Customer Name :Bakiyaraj Contact :9786912637 | Task Start | Devaki Ceramics. | 20 | Engine not taking, SE on site is suspecting Block loading, further inspection pending | Task start | Mr. NandhaGopal
4 | South | 211613279 | 17-01-2025 10:45 | 15 | GP3.8501.../2421570 | Starting Issue call by KGD Name ;- Prakash Mob No ;- 9448476151 | Task Start | Shiva Fuels Station |  | update pending | Task start | Mr. Anil Kumar H G
5 | South | 211612436 | 16-01-2025 20:03 | 30 | 3H.8902.../2320139 | Trip_Genset_Low_Voltage | Open | SLN Hotel & Resorts |  | visit pending | open | Mr. Anil Kumar H G
6 | South | 211611761 | 16-01-2025 15:56 | 40 | 3H.8951.../2421110 | MCCB | Task Start | Sathya Agencies Pvt. Ltd. Andhra Pradesh | LR | attend the site check the dg incoming Genset supply mcb was failed . commissioning time check the engine we found the mcb was failure condition | Task start | Mr. MD Saleem
7 | South | 211611184 | 16-01-2025 13:25 | 20 | GP3.8601.../2421250 | Voltage Problem Call by : Customer Name : Sampath kumar Contact : 9894782881 | Open | MURUGAN AGENCIY | NA | Cancelled | Cancelled | Mr. NandhaGopal
8 | South | 211615267 | 17-01-2025 16:02 | 30 | 3H.8902.../2420109 | INSTANCE ID:-100763528 SITE ID:-5689 CALL BY CUSTOMERA:- DG ISSUE :- DG STARTING PROBLEM NAME :-JIBIN NUMBER :- 9108335949 | Task Start | Axis Bank Ltd | 44.57 | As per the customer complaint visit the site dg not starting.check the dg and observe the problem.the problem was battery was less voltage.check the battery charger connection disconnected.reconnect the battery charger connection and charge the battery ok.started the engine running ok | Closed | Mr. Anil Kumar H G
9 | South | 211615057 | 17-01-2025 15:25 | 58.5 | T4.8941.../2420932 | Inspection/Maintenance | Open | Malateshwara Granites |  | visit pending | open | Mr. Anil Kumar H G
10 | South | 211615075 | 17-01-2025 15:21 | 500 | DV8.8501.C4../2320053 | Oil Leakage Issue Call By Customer Name :- Babu Mobile No :- 8464928352 | Open | Upper India Inorganic Industries Limited |  | visit pending | open | Mr. NandhaGopal
11 | South | 211614822 | 17-01-2025 14:32 | 15 | GP3.8501.../2421098 | Automatically Switching off & Diesel Leakage Problem Call by : Customer Name :parthasarathy Contact :9566020461 | Task Start | CHAITANYA GOURMET PRIVATE LIMITED | 61 | diesel leakage due to electrical feed pump house clamp loose condition retighed the hose clamp. engine tripping due to customers using over current and unbalance load inform to customer share the load. | Closed | Mr. NandhaGopal
12 | South | 211614670 | 17-01-2025 14:03 | 58.5 | T4.8941.../2421406 | Oil Leakage Problem Call by : Customer Name :Lawrence Contact :9972590992 | Task Start | M/s. S. S Security Services | 29 | Oil leakage from head | Task start | Mr. Anil Kumar H G
13 | South | 211614682 | 17-01-2025 13:57 | 25 | GP3.8702.../2420803 | Starting Problem Call by : Customer Name : Venkatesh Goud Contact : 9010720630 | Closed | Venkatesh Goud | 21 | Emergency switch 11 no wire loose contact. | Closed | Mr. MD Saleem
14 | South | 211618323 | 18-01-2025 12:20 | 125.4 | 4H.8042.C4../2420866 | Error Code Issue Call By Customer Name - Reddy .. Number - 9743346111 | Task Start | Gulbarga Enterprises | 2 | 3031/28 , 516166/0, 4095/1,3031/14 shown in display. Clear the DTC found ok | Task start | Mr. Anil Kumar H G
15 | South | 211618078 | 18-01-2025 11:43 | 0 | GP3.8702.../2421922 | WIRING HARNESS FAILURE REPALCMENT ACTIVITY | Completed | SUNBEAM GENERATORS PVT LTD | 1.17 | Engine wiring harness burn during testing | Cmopleted | Mr. NandhaGopal
16 | South | 211618093 | 18-01-2025 11:42 | 0 | 5H.5351.../2520019 | ERROR CODE | Task Start | AJAX ENGINEERING PRIVATE LIMITED | LR | Coolant leakage from temperature sensor side | Closed | Mr. Anil Kumar H G
17 | South | 211618017 | 18-01-2025 11:31 | 0 | 5H.5351.../2520024 | ECU NOT RESPONDING | Task Start | AJAX ENGINEERING PRIVATE LIMITED | LR | Check the cluster and ECU command is not responding, as per HO(nikhil patil) SE replace the ecu from other engine, issue resolved | Task start | Mr. Anil Kumar H G
18 | South | 211618025 | 18-01-2025 11:31 | 0 | T4.8941.../2422648 | FUEL LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | LR | Fuel leakage due to fuel return line crimp damage | Task start | Mr. NandhaGopal
19 | South | 211618004 | 18-01-2025 11:25 | 25 | GP3.8702.../2420521 | Starting Problem Call by :Customer Name : Guru prasad Contact : 9963027225 | Task Start | CAFE MADHURAM | 40 | Controller not ON due to 2C fuse failure So replace the fuse ,issue resolved | Closed | Mr. Anil Kumar H G
20 | South | 211617773 | 18-01-2025 10:37 | 160 | 6H.8475.../2420375 | Red lamp alarm and problem code | Task Start | Vijay Super Speciality & Cancer Centre | 14 | 4095/2 code shown in display. Remove the dosing module connector & refitted then clear the DTC. | Closed | Mr. NandhaGopal | Under Observation
21 | South | 211617664 | 18-01-2025 10:08 | 320 | F6.8802.../2420228 | Load checking Call by : Dealar Name : Contact : Customer name : Customer number : | Completed | SABARI WOOD AND PLYWOODS | NA | Cancelled | Cancelled | Mr. NandhaGopal
22 | South | 211616951 | 18-01-2025 00:47 | 625 | DV0.8501.C4../2320011 | Starting Issue Call By Customer Name :- Vector No :- 9361746165 | Task Start | Dadha Pharma LLP. | 19 | supply model above normal code appear check the wire removed and refitted the wire checked the all connection checking ok | Closed | Mr. NandhaGopal | KRM Check
23 | South | 211616600 | 17-01-2025 19:11 | 15 | GP3.8501.../2420928 | AMF panel problem Call by : Customer Name : Hari Contact : 9980107172 | Task Start | GEETHANJALI HARISH | 13.5 | Found underspeed alarm. So checked the fuel line found Ele. Feed pump ferrule no 2 is loose so tighten the wire issue resolve. | Closed | Mr. Anil Kumar H G
24 | South | 211616490 | 17-01-2025 18:21 | 0 | 5H.5351.../2520033 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | As per the customer complaint error code issue from the engine. after check the error code is showing the ( 110/4 coolant temperatures sensor error). Found coolant level low so top up & clear the error code and finally started the engine observed on running condition working found ok | Closed | Mr. Anil Kumar H G
25 | South | 211616483 | 17-01-2025 18:18 | 0 | 5H.5351.../2520023 | ERROR CODE | Closed | AJAX ENGINEERING PRIVATE LIMITED | LR | As per the customer complaint error code issue from the engine. after check the error code is showing the (97/5 water in fuel). Found sensor loose so tighten the sensor & clear the error code and finally started the engine observed on running condition working found ok | Closed | Mr. Anil Kumar H G
26 | South | 211616464 | 17-01-2025 18:14 | 30 | 3H.8902.../2420003 | Starting Issue Call By Customer Name :- Narayan Mobile No :-9840299619 | Task Start | Dr. Santha Narayanan | 22 | visit the site check the engine check the problem, battery voltage is low then check the battery distilled water condition is ok, battery charger working properly,so took the battery to charging and fix the stand by now engine running normaly no issues | Task start | Mr. NandhaGopal
27 | South | 211616379 | 17-01-2025 17:47 | 30 | 3H.8902.../2421614 | VOC: DG tripping. | Task Start | ICICI Bank Limited | 6 | found engine tripping due to 157/14 visited the site connect the I- konnect tooll started the engine ,with in 10 min engine is getting tripping , check the DTC parameters 157/14 error code is appeared,check all the wires loose. connection tighten all wire connection, changed main relay 2A1 wire .0.75 sq.mm to 2.5 sq mm started the engine run the engine one hour we observed there is no error code found | Task start | Mr. NandhaGopal
1 | East | 211618281 | 18-01-2025 12:14 | 30 | 3H.8902.../2420735 | Voltage Issue Call By Customer Name :- Hemant Kumar Mobile No :-9301654903 | Closed | Hemanta Kumar Panda | 67 | Customer required service no issue in DG | CLOSED | Ujjwal Das
2 | East | 211616228 | 17-01-2025 17:27 | 40 | 3H.8951.../2421571 | LOAD | Cancelled | M/s. Shyam Power Solution. | 58 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das
3 | East | 211614487 | 17-01-2025 13:10 | 25 | GP3.8702.../2420235 | Leakage Issue | Closed | ORCHID CONSTRUCTION | 79 | SE found Fuel Leakage was due fuel filter benzo loose. After tightening the benzo no leakage in fuel system , issue resolved | CLOSED | Prosanjit saha
4 | East | 211614378 | 17-01-2025 12:53 | 40 | 3H.8951.../2420743 | DG automation is not work due to automation panel are not sync | Open | ATC Telecom Infrastructure Private Limited | 67 | Update Pending | OPEN | Prosanjit saha
5 | East | 211614371 | 17-01-2025 12:51 | 30 | 3H.8902.../2421915 | DG automation is not work due to automation panel are not sync | Open | ATC Telecom Infrastructure Private Limited | 54 | Update Pending | OPEN | Prosanjit saha
6 | East | 211611579 | 16-01-2025 15:21 | 20 | GP3.8601.../2420215 | DG not starting-503189 | Task Start | ICICI Bank Limited | 34 | 1761/16 (Low DEF level) after top up the DEF tank Issue resolved. | CLOSED | Ujjwal Das
7 | East | 211618454 | 18-01-2025 12:54 | 30 | 3H.8902.../2420349 | Under Speed Alarm issue Call By Customer Name :- Krishna Aditya . Mobile No :- 9875616966 | Closed | Matri Enterprise | 23 | Alarm: No speed signal, so SE take out MPU check it's continuty found OK then clean it and refitted with appropriate gap then DG start normally. | CLOSED | Prosanjit saha | Under observation
8 | East | 211610287 | 16-01-2025 10:40 | 20 | GP3.8601.../2420762 | Starting/Stopping Issue | Closed | M/s. Sundarban Ayurved Bhawan. | 13 | SE found engine not starting because of battery was discharged due to battery charger loose connection Then connect the battery charger connection and recharge the battery. Then start the engine and this engine run good onload condition ok. | CLOSED | Prosanjit saha
9 | East | 211610136 | 16-01-2025 10:00 | 58.5 | T4.8941.../2423028 | Alarm issue Call By Customer Name :- GANESH Kumar Mobile No :- 9102352999 | Open | ENVYNN CLIMATECH SOLUTIONS PRIVATE LIMITED | 34 | SE visited site found 516166 code so cleared code by connecting Ikonnect, found no other fault code in DTC tested DG on load found ok. | CLOSED | Prosanjit saha
10 | East | 211620780 | 19-01-2025 12:42 | 125.4 | 4H.8041.../2420847 | Starting Issue Call By Customer Name- Adarsh Verma No-8434075821 | Open | Saran Heart Care |  | Visit pending | OPEN | Prabhakar Kumar
11 | East | 211619561 | 18-01-2025 17:08 | 45 | 3H.8951.../2421369 | Diesel Leakage Issue Call By KGD Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. |  | Update pending | OPEN | Prabhakar Kumar
12 | East | 211618751 | 18-01-2025 14:22 | 15 | GP3.8501.../2420548 | Sound/Vibration Issue | Open | Shiv Sankar Diesels |  | Visit pending | OPEN | Ujjwal Das
13 | East | 211618150 | 18-01-2025 11:51 | 58.5 | T4.8941.../2420396 | Red Lamp On Alarm Issue Call By Customer Name;-Rahul ... No:-8210103085 | Closed | Mishra Automobiles Unit 2 | 172 | Red lamp alarm was due to low fuel level so topup and also found DG not starting showing under voltage to found controller voltage sensing wire loose at controller jack so tighten properly issue resolved. | CLOSED | Prabhakar Kumar
14 | East | 211618062 | 18-01-2025 11:39 | 125.4 | 4H.8041.../2420658 | Leakage Issue | Closed | Divine Savior Church |  | Update pending | OPEN | Ujjwal Das
15 | East | 211616599 | 17-01-2025 19:10 | 250 | F6.8841.../2420119 | Starting Problem Call by : Customer Name :Amlan Contact :9365909973 | Closed | Health Planet. | 42 | Visit the site and found discharge battery, so check and found battery charger not providing voltage at battery due to loosen of its B+ wire so tighten properly issue resolved. | CLOSED | Ujjwal Das
16 | East | 211611051 | 16-01-2025 12:55 | 20 | GP3.8601.../2420654 | Control panel issue Call by customer Name: Pravin Dutta Number:7002877585 | Closed | Computech India | 669 | Update pending | OPEN | Ujjwal Das
17 | East | 211610432 | 16-01-2025 11:18 | 30 | 3H.8902.../2420583 | Starting/Stopping Issue | Task Start | Shine Enterprise |  | Visit pending | OPEN | Ujjwal Das
18 | East | 211610009 | 16-01-2025 08:02 | 30 | 3H.8902.../2420356 | Fuel Sensor Issue Call By Customer Name :-Rajesh Kumar Roy Mobile No :-8809887503 | Closed | Rajesh Kumar Roy | 52 | Fuel level alarm Showing on display, so SE found controller 25no. Wire loose at controller, after tightening issue resolved. | CLOSED | Prabhakar Kumar | Service History
19 | East | 211593974 | 2025-10-01 10:01 | 30 | 3H.8902.../2420892 | Starting Issue Call By Customer Name :- Rawat Ji Mobile No :-8637507378 | Open | LINKCON ENGINEERING PRIVATE LIMITED |  | At the time of commissioning found DG Canopy defective and also found that there was lube oil in intake manifold and EGR valve so GOEM will held this case. SO DG will send to GOEM plant. | CLOSED | Ujjwal Das
1 | West | 211618695 | 18-01-2025 14:03 | 625 | DV0.8501.C4../2420058 | Error Code. Call by Service. Name:-Ashok Parmar Mobile No.:- 9601472233 | Open | Transworld Logistics Pvt. Ltd. | 4.11 | The genset starts for 15 minutes and then stop . Checked the fuel line, interfacebox connections found Ok So today our SD/ASE engineer will be visiting the site. | CLOSED
2 | West | 211618682 | 18-01-2025 14:00 | 58.5 | T4.8941.../2422032 | Diesel leakage issue Called by customer Name : Sohail Diwan Number: 8153053986 | Closed | Mom DJ. Sound | 6 | Fuel level was not showing proper,So changed the gauge and issue resolved. Fuel lekage from fuel tank plate so tightened the same. | CLOSED
3 | West | 211618539 | 18-01-2025 13:23 | 125.4 | 4H.8042.C4../2420595 | Door Faulty Call By Customer Name :- Snehal Mobile No :-9404960031 | Closed | INDU CONSTRUCTION | 28 | Canopy door lock issue so proper fitted the lock. | CLOSED
4 | West | 211618531 | 18-01-2025 13:16 | 30 | 3H.8902.../2421645 | Automation Issue Call By Customer Name :-Jayesh Pawar Mobile No :- 8484840149 | Closed | Jayesh Bharat Pawar | 8 | Automation issue, MCB output wire was interchanged so corrected the same. | CLOSED
5 | West | 211614838 | 17-01-2025 14:37 | 250 | F6.8841.../2420181 | Starting/Stopping Issue | Closed | Alard College of Engineering and Management. | 152 | Low adblue level. | CLOSED
6 | West | 211614724 | 17-01-2025 14:12 | 250 | F6.8841.../2420405 | Main contractor problem | Task Start | Alan Electronic Systems Pvt. Ltd. | 2 | Automation issue, So checked and found the relay 15RB2 coil supply wire loose. | CLOSED | Service history check
7 | West | 211613584 | 17-01-2025 11:29 | 160 | 6H.8475.../2420214 | Start Issue Email By - GOEM Name - ROHIT KAMBLE | Task Start | Kritija Construction. | 494 | SPN/FMI-654/5, Checked the continuity from ECU to enjector found ok. Flashed and replaced the ECU but problem is same. | OPEN
8 | West | 211602861 | 13-01-2025 13:27 | 320 | F6.8802.../2420235 | Coolant Leakage Issue Email by GOEM Name - Ranjan Kowale | Task Start | Meta Arch Design Built | 33.2 | Coolant leakage from cylinder head. Opend the cylinder head and found the gasket failure so changed the gasket. Drained the oil but no metal particals found. | OPEN
1 | South | 211621978 | 20-01-2025 10:51 | 15 | GP3.8501.../2420988 | Battery voltage low Email By - KGD Name -M.K.GURUMURTHY | Open | Sunita Mukund Chirumalai | NA | visit pending | Task start | Mr. Anil Kumar H G
2 | South | 211621957 | 20-01-2025 10:46 | 200 | 6H.8435.../2420097 | Abnormal Sound Call by : Customer Name :Balamurugan S Contact :9514460515 | Task Start | SRLPS Foods Pvt. Ltd. | 40 | check the problem, radiator fan belt is loose condition so sound raised then tight the radiator fan belt with correct tension ,now no sound issue, engine running normaly | Task start | Mr. NandhaGopal
3 | South | 211621872 | 20-01-2025 10:26 | 82.5 | 5H.8901.../2420588 | Automatically switching off Call by : Customer Name : Praveen Contact : 7997991294 | Open | Sneha Farms Pvt. Ltd. | 17.25 | DG not starting as the fuel level was low, advice the customer to maintain the fuel level | Closed | Mr. Sanjaimon S
4 | South | 211621809 | 20-01-2025 10:09 | 15 | GP3.8501.../2420053 | Maintenance Due Call by : Customer Name : Muthu selvan Contact : 9578469959 | Completed | S. R. A. Agencies | 1816 | Found Maintenance Due and Battery Voltage High Alarm Due to Battery Distilled Water Level Low and Battery High Charging 15.2v So Engine Not Starting, Battery Charging Voltage Normal 14.6v and SPN 602, FMI 11 Warning Reset, Started the Engine Running Performance ok, | Closed | Mr. NandhaGopal
5 | South | 211621709 | 20-01-2025 09:43 | 40 | 3H.8951.../2420755 | Error problem & AMF Panel Problem Call by : Customer Name : Palguna Contact : 9440047705 | Task Start | M/s. D. N. R. Poultry Farms | 62 | air lock (Update pending) | Task start | Mr. NandhaGopal
6 | South | 211621703 | 20-01-2025 09:40 | 500 | DV8.8501.C4../2320018 | ECU Amber Lamp On Alarm And Abnormal Sound Call By Customer Name :- Kalandi Charan Behra Mobile No :-6371057009 | Task Start | SHOBA LIMITED | 277 | 1761/15, 97/2, 156/14, 655/3 found in ikonnect so fill the DEF and clear the DTC. | Closed | Mr. Anil Kumar H G | Under Observation
7 | South | 211620929 | 19-01-2025 18:14 | 30 | 3H.8902.../2421315 | Display Problem Call by : Customer Name : Raja Contact : 8072613468 | Task Start | S. MAHESH BABU | 25.57 | Display Showning programing mode & parameter not showing. SO SE visited the Site & Switch off controller again on issue resolved | Closed | Mr. NandhaGopal
8 | South | 211620924 | 19-01-2025 17:59 | 15 | GP3.8501.../2420544 | Maintenance Due Alarm Call by Customer Name - Harish . Mobile No - 9113977600 | Task Start | Dak Infra Projects | 92 | control panel RG fuse is defective and replace the new fuse after started the engine | Closed | Mr. Anil Kumar H G
9 | South | 211620880 | 19-01-2025 16:26 | 30 | 3H.8902.../2420391 | Alarm Problem Call by : Customer Name :Nanu Contact :7012302535 | Task Start | Sunithas. | 216 | Emergency switch connection clip loose, tight the connection, then start the engine, | Closed | Mr. Sanjaimon S
10 | South | 211620703 | 19-01-2025 10:39 | 25 | GP3.8702.../2420608 | Air lock problem Call by : Customer Name : Naresh Contact : 9100766758 | Task Start | Yanamadala Grand Srihari Fuel Station | 48 | Air lock issue in diesel filter, remove the air lock | Task start | Mr. NandhaGopal
11 | South | 211620131 | 18-01-2025 18:44 | 25 | GP3.8702.../2420630 | Genset Trip | Closed | Dr Sara Thomas, Smile Brite Dental Center | 36.11 | Customer using DG on unbalance load | Closed | Mr. Anil Kumar H G
12 | South | 211618859 | 18-01-2025 14:51 | 25 | GP3.8702.../2420712 | Starting Problem Call by : Customer Name : Haroon Contact :9008306761 | Task Start | Sathya Agencies Pvt. Ltd. .. | 15 | SPN 97/FMI 5 SPN 157 / FMI14 no issue found, clear the DTC | Task start | Mr. NandhaGopal
13 | South | 211618698 | 18-01-2025 14:04 | 40 | 3H.8951.../2420825 | Trip_Genset_High_Voltage | Closed | Sri Madhura Jewellery Pvt. Ltd. | 17 | Problem as been raised with KRM unit. charging alternator voltage normal.Battery check. Charging alternator check. Panel board check. battery charger check. No issue in genset. Engine running condition normal | Closed | Mr. NandhaGopal | KRM Check
14 | South | 211622415 | 20-01-2025 12:30 | 45 | 3H.8951.../2421184 | Starting Problem Call by : Customer Name : S.Viswanatha Reddy Contact : 8919080402 | Task Start | SHIVA SAI ENTERPRISES | NA | update pending | Task start | Mr. NandhaGopal
15 | South | 211622401 | 20-01-2025 12:25 | 200 | 6H.8435.../2420164 | fuel indicator problem Call by : Customer Name : Rajesh Contact : 9553558195 | Open | Balaji Educational Society | NA | Visit pending | Open | Mr. NandhaGopal
16 | South | 211622339 | 20-01-2025 12:18 | 35 | 3H.8902.../2422082 | Tripping problem Call by : Customer Name :Suresh Contact :9488361201 | Task Start | Gokulam Textiles And Readymades | NA | 2791/18, 5838/1 code shown in display. So checked the EGR connector found ok . Then Flash the ECU now working ok. | Task start | Mr. NandhaGopal | Under Observation
17 | South | 211622299 | 20-01-2025 12:04 | 58.5 | T4.8941.../2420344 | Display Showing "Maintenance Due" Call by : KGD Name :bhuvaneshwar Contact : 9346475710 KGD number : 9347338159 | Task Start | C. Bhuvaneshwar Reddy | NA | update pending | Task start | Mr. NandhaGopal
1 | East | 211624218 | 20-01-2025 18:05 | 15 | GP3.8501.../2420474 | Starting/Stopping Issue | Task Start | SAVEER BIOTECH LTD.. |  | Visit pending | OPEN | Ujjwal Das
2 | East | 211622884 | 20-01-2025 14:21 | 20 | GP3.8601.../2420266 | Fuel Leakage Issue Email by KGD Name - NAGALAND POWERKRAFT | Open | Chakesang Baptist Church |  | Visit pending | OPEN | Ujjwal Das
3 | East | 211622566 | 20-01-2025 12:56 | 82.5 | 5H.8901.../2420074 | Starting Issue Call By Customer Name ;-Manohar Singh No :- 7479913858 | Closed | Dwarkapati Foods LLP. | 63 | Customer side issue there was automation problem and also found amber lamp on due to the low adblue level so educated customer to maintain DEF level. | CLOSED | Prabhakar Kumar
5 | East | 211621889 | 20-01-2025 10:31 | 30 | 3H.8902.../2420496 | Automation Issue Call By customer Name: -Sunil Kumar Rajak No: -9835673046 | Closed | Sunil Kumar Rajak | 36 | Customer's issue was that DG start at night while main available, So SE reset the main voltage cuttoff setting in LVM | CLOSED | Prabhakar Kumar
6 | East | 211621731 | 20-01-2025 09:55 | 82.5 | 5H.8901.../2420498 | Starting Issue Email by KGD Name - sunrise power | Open | PRADHAN DEVELOPERS |  | visit pending | OPEN | Prabhakar Kumar
7 | East | 211621657 | 20-01-2025 09:26 | 250 | F6.8841.../2420327 | LUBE OIL LEAKAGE | Task Start | Mithila Earthing Solutions | 6.6 | Found lube oil leakage at filter due to o-ring damage so replaced the lube oil filter by ASM approval | CLOSED | Prabhakar Kumar
9 | East | 211619589 | 18-01-2025 17:14 | 320 | F6.8802.../2420157 | Control Panel Issue Email By - GOEM Name - Arup Kr. Ray | Closed | M/S. AROGYA HOSPITAL & RESEARCH CENTRE | 20 | DG Does not start on Auto so found in automation panel voltage sensing for Rphase fuse burnt, fuse replaced fuse issue resolved also found amber lamp on due to low urea level so educated customer to topup urea and maintain minimum 50% | CLOSED | Ujjwal Das
10 | East | 211619561 | 18-01-2025 17:08 | 45 | 3H.8951.../2421369 | Diesel Leakage Issue Call By KGD Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. |  | visit pending | OPEN | Prabhakar Kumar
11 | East | 211618751 | 18-01-2025 14:22 | 15 | GP3.8501.../2420548 | Sound/Vibration Issue | Open | Shiv Sankar Diesels | 83 | ASE visited site and found DG have abnormal sound at gear casing side then further foud idle gear broken and crankshaft and oil pump gear was also got damage DG will be repalced. | OPEN | Ujjwal Das
12 | East | 211618593 | 18-01-2025 13:33 | 125.4 | 4H.8041.../2420875 | Voltage Fluctuation | Closed | Moon House Projects Limited | 40 | DG was not starting showing under voltage and so SE checked for air lock issue and aslo found electric feed pump not working due to loose connection at feed pump relay output point so tighten same and cleared airlock issue resolved. | CLOSED | Prabhakar Kumar
13 | East | 211618062 | 18-01-2025 11:39 | 125.4 | 4H.8041.../2420658 | Leakage Issue | Closed | Divine Savior Church | 35 | There was diesel seepage at fuel filter outlet pipe due to the banjo copper washer defective replaced the washer issue resolved. | CLOSED | Prabhakar Kumar
14 | East | 211614573 | 17-01-2025 13:30 | 160 | 6H.8475.../2420162 | Abnormal Sound Issue Call By Customer Name :- Suresh Mobile No :-6002824186 | Closed | Ms Ankur Enterprise | 132 | There was some abnormal sound then on inspection found fan belt loose so tighten issue resolved | CLOSED | Ujjwal Das
15 | East | 211611051 | 16-01-2025 12:55 | 20 | GP3.8601.../2420654 | Control panel issue Call by customer Name: Pravin Dutta Number:7002877585 | Closed | Computech India | 669 | SE found controller is not getting on then found control 2 no wire +tive supply fuse burn so replaced the fuse issue resolved. | CLOSED | Ujjwal Das
16 | East | 211610432 | 16-01-2025 11:18 | 30 | 3H.8902.../2420583 | Starting/Stopping Issue | Closed | Shine Enterprise | 25 | DG not starting due to loose connection of battery clamp and also found battery clamp broken so replaced by new one issue resolved. | CLOSED | Ujjwal Das
17 | East | 211601117 | 2025-12-01 08:53 | 30 | 3H.8902.../2422023 | Starting Issue Call By Customer Name :-Satpal Sharma Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS |  | SE alinged site will be attend tomorrow . Asset is in remote location | OPEN | Ujjwal Das
18 | East | 211622935 | 20-01-2025 14:37 | 20 | GP3.8601.../2421104 | Starting issue Call By Customer Name :- Prince Mobile No :-9547866525 | Open | Md. Akbar Alam | 78 | Today SE will visit site | OPEN | Prosanjit saha
19 | East | 211622923 | 20-01-2025 14:30 | 250 | F6.8841.../2420212 | Tripping Issue Call by customer Name: Subhrath Das Number:9937045664 | Open | DANIELI CORUS REFRACTORY SOLUTIONS PRIVATE LIMITED | 45 | SE visited site found 516166 code so cleared code by connecting Ikonnect, found no other fault code in DTC tested DG on load found ok. | CLOSED | Ujjwal Das
20 | East | 211571279 | 2025-05-01 08:55 | 25 | GP3.8702.../2421034 | Starting Issue Call By Customer Name :-Proshenjit Saha Mobile No :-7001964817 | Task Start | PROSANJIT SAHA | 22 | DG was not starting and its PRV count were also increasing frequently so rep;laced the commmon rail but then DG wasnot starting witout any code so replaced the ECU so further on inspection found DTC SPN 2802 FMI 4 so it indicated that ECU not getting proper 12V so checking found looseconnection at XDBK4 loose connection of 2A wire after tighteng issue resolved no need to replace ECU or Common rail | CLOSED | Prosanjit saha
1 | North | 211613506 | 17-01-2025 11:28 | 5.5 | CC1.1013.../2400303 | Genset Trip | Task Start | YUVTARA INTERNATIONAL PVT LTD | 165 | Engineer visit with Koel ASE ESN- CC1.1013/2400528 Found Engine speed fault in 1.2 hrs Check Event log, low fuel level Warning after Educate the customer for maintain the fuel level | Closed | Gourav Sharma
2 | North | 211612408 | 16-01-2025 20:06 | 125.4 | 4H.8041.../2420904 | Starting/Stopping Issue | Closed | Purvanchal Vidyut Vitran Nigam Limited. | 4 | Air locking issue found benjo bolt loose from water seprator tightness the same issue resolve | Closed | Sudhir Awasthi
3 | North | 211611992 | 16-01-2025 16:48 | 125.4 | 4H.8041.../2420452 | Starting Issue Call By customer Name : Ranveer Singh No : 8433230254 | Task Start | Aadya Industries. | 540 | Controller show the maintenance alarm, after reset the alarm then DG running both Condition Auto & Manual | Closed | Sudhir Awasthi
4 | North | 211611715 | 16-01-2025 15:57 | 5.5 | CC1.1013.../2400528 | Automation Issue Call By service Dealer Name - Deepu Rathod Mobile No -7849829464 | Closed | AARUSHI CONSTRUCTION | 1 | Exhaust jali block removed by customer | Closed | Gourav Sharma
5 | North | 211611435 | 16-01-2025 14:39 | 58.5 | T4.8941.../2421662 | Starting/Stopping Issue | Closed | Purvanchal Vidyut Vitran Nigam Limited. | 3 | Under speed alarm check fuel line found ok then check Crank sensor found ok after check CAN wire loose from Contoller then issue resolve | Closed | Sudhir Awasthi | CC check
6 | North | 211611408 | 16-01-2025 14:29 | 30 | 3H.8902.../2421130 | AMF Panel Fitting Issue Call By Customer Name :- Amit Mobile No :-8265820510 | Closed | MAA SANTOSH JI SERVICE STATION_RBNL | 22.4 | AMF panel wiring fitting & Sync activation | Closed | Sudhir Awasthi
7 | North | 211618622 | 18-01-2025 13:44 | 15 | GP3.8501.../2420526 | Starting/Stopping Issue | Task Start | Mohammad Hussain House. | 27 | checked and found 2b wire supply loose after that tightnenss wiring properly | Closed | Sudhir Awasthi
8 | North | 211618512 | 18-01-2025 13:12 | 62.5 | T4.8941.../2420520 | Red lamp alarm issue Call By Customer Name - Yogendra Mobile No - 7428254724 | Task Start | Pacelami and Fab Company. | 189 | Over load & Unbalance load R-6, y-45, B-16 Educate the customer please maintain the load | Closed | Kapil Solanki
9 | North | 211618467 | 18-01-2025 12:53 | 125.4 | 4H.8042.C4../2420640 | Voltage Fluctuation | Task Start | Arihant Dies & Moulds Pvt. Ltd. | 6 | update pending | OPEN | Kapil Solanki
10 | North | 211618416 | 18-01-2025 12:47 | 58.5 | T4.8941.../2420573 | Voltage Fluctuation Issue Call By Customer Name - Tejpal Singh Number - 9810773777 | Task Start | MAG FILTERS AND EQUIPMENTS PRIVATE LIMITED | 74 | Customer side load issue | Closed | Kapil Solanki
11 | North | 211618379 | 18-01-2025 12:34 | 5.5 | CC1.1013.../2400477 | Starting/Stopping Issue | Task Start | SHRI TEJA ENTERPRISES | 164 | Check Found Engine Speed fault Alarm Check Fuel tank found dirty Pump chocked with dust fuel filter Check found badly choke Pump setting seal broken, DG running 165 hrs service not done yet,New Fuel filter replaced but Pump not build pressure for firing , need to Replace the Pump | Closed | Gourav Sharma
12 | North | 211618020 | 18-01-2025 11:29 | 125.4 | 4H.8041.../2420019 | Starting/Stopping Issue | Closed | Rahee Infratech Ltd. | 3852 | update pending | OPEN | Kapil Solanki
13 | North | 211617997 | 18-01-2025 11:28 | 40 | 3H.8951.../2420338 | Starting issue Call by customer Name: Naresh . Number: 9873422640 | Task Start | Bhojpuri Avadhi Sammaj | 20 | Over load & Unbalance load B-70A , Educate the customer please maintain the load | Closed | Kapil Solanki
14 | North | 211617730 | 18-01-2025 10:24 | 20 | GP3.1021.../2420471 | DG Conteunue air | Task Start | Reliance Jio Infocomm Limited | 76 | fuel tank to fuel lifting motor hose pipe clip loose and fuel low level down of 50% after then top-up diesel in fuel tank and hose clip tight- photo click on Efsr but efsr not be download | Closed | Sudhir Awasthi
15 | North | 211617704 | 18-01-2025 10:16 | 625 | DV0.8501.C4../2420158 | Starting Problem | Task Start | Radikale Engineering Pvt. Ltd.. | LR_17 | update pending | OPEN | Kapil Solanki
16 | North | 211617511 | 18-01-2025 08:20 | 57 | T4.8941.../2420185 | Starting Issue Call By Customer Name :- Atmaram Mobile No :-9810571470 | Closed | Jay Garud Gas Station | 37.4 | found the Under speed alarm all wire tightness of control panel then issue resolve | Closed | Kapil Solanki | Under Observation
17 | North | 211617386 | 18-01-2025 07:09 | 125.4 | 4H.8042.C4../2420636 | Starting/Stopping Issue | Closed | THE PUNJAB NATIONAL BANK EMPLOYEES S/D CGHS LTD | 12.59 | Voltage setting over voltage 250- 270 in Controller because mains supply voltage in day Low but during night Voltage increase | Closed | Kapil Solanki
18 | North | 211616621 | 17-01-2025 19:29 | 125.4 | 4H.8041.../2320187 | Starting Issue Call By Customer Name :-SK Bhingraj Mobile No :-9837313870 | Closed | Rush Enterprises | 92 | Low fuel level alarm, Educate the Customer kindly top up the Fuel & Check the fuel % value | Closed | Kapil Solanki
19 | North | 211615433 | 17-01-2025 16:33 | 58.5 | T4.8941.../2421558 | Inspection/Maintenance | Closed | Anand Synthetics | 40 | Low Coolant level Need to required 2 lit. | Closed | Sudhir Awasthi
20 | North | 211615264 | 17-01-2025 16:00 | 40 | 3H.8951.../2421384 | Oil Leakage Issue Call By Customer Name :-Prashant Mobile No :-9027507780 | Closed | Axxiom Ventures (OPC) Private Limited | 10 | Oil leakage due to banjo Loose tightness the same issue resolve | Closed | Kapil Solanki | Details required
21 | North | 211615050 | 17-01-2025 15:20 | 58.5 | T4.8941.../2423031 | Electrical Problems | Closed | SHRI BANDE KA BALAJI | 29 | update pending | OPEN | Gourav Sharma
22 | North | 211614719 | 17-01-2025 14:08 | 320 | F6.8802.../2420041 | Leakage Issue | Closed | M/S EINS TECHNIK PRIVATE LIMITED | 311 | coolant leakage from radiator hose pipe clamp tight hose pipe clamp, but clamp is free, so replace the hose pipe clamp | Closed | Kapil Solanki
23 | North | 211622634 | 20-01-2025 13:06 | 320 | F6.8802.../2420011 | Main Alternator Faulty | Task Start | MALIK ENTERPRISES |  | update pending | OPEN | Kapil Solanki
24 | North | 211622567 | 20-01-2025 12:56 | 82.5 | 5H.8901.../2420586 | Tipping issue Call By Customer Name : Madan .. No : 9891064222 | Task Start | J And J Global Sourcing LLP | 3 | Auto wire loose tightness the same issue resolve | Closed | Kapil Solanki
25 | North | 211622388 | 20-01-2025 12:26 | 160 | 6H.8475.../2420031 | Inspection/Maintenance | Completed | TRAIN HIGH |  | DEF required to customer | Closed | Kapil Solanki
26 | North | 211621821 | 20-01-2025 10:09 | 125.4 | 4H.8041.../2420241 | Starting/Stopping Issue | Closed | MALABAR GOLD PRIVATE LIMITED | 1055 | found the dg fuel tank pipe loose then fuel pipe proper tight | Closed | Kapil Solanki
27 | North | 211621783 | 20-01-2025 10:01 | 125.4 | 4H.8041.../2420745 | Starting/Stopping Issue | Task Start | JAIN GENERATOR HIRING CO.. | 1376 | SPN/FMI 7598/7, 4095/1,2 & (51/0 in DM -2) Today visit with tool | OPEN | Kapil Solanki
28 | North | 211621746 | 20-01-2025 09:54 | 30 | 3H.8902.../2320070 | Silencer Issue And Priventive Maintenance Call By Customer Name :-Rk Manish Mobile No :- 9810913739 | Closed | Shivam Tubes | 184 | Exhaust bracket broken so abnormal sound from the Dg | OPEN | Kapil Solanki
29 | North | 211621652 | 20-01-2025 09:03 | 15 | GP3.8501.../2420190 | Automation Issue Call By Customer Name :- Col. Rajeev Sud Mobile No :-9910111991 | Closed | HIMALAYA GENERATORS | 127 | Voltage setting over voltage 250- 265 in Controller because mains supply voltage in day Low but during night Voltage increase | Closed | Kapil Solanki
30 | North | 211620930 | 19-01-2025 18:48 | 57 | T4.8941.../2320250 | Starting/Stopping Issue | Closed | Shivmani Hospital | 224 | Leakage from Filter to pump benjo washer defective change the washer & tightness the same issue resolve | Closed | Kapil Solanki
31 | North | 211620816 | 19-01-2025 15:08 | 125.4 | 4H.8041.../2320054 | Red Lamp Alarm Issue Call By Customer Name- Rohtas na No- 9268607916 | Task Start | XC# | 610 | SPN/FMI 51/0 ITV jammed this code found on 24/DEC. but same issue check itv found ok clean the ITV and fitted again then - UNDER OBSERVATION | OPEN | Kapil Solanki
32 | North | 211620814 | 19-01-2025 14:53 | 160 | 6H.8475.../2420025 | Tripping issue Call By Customer Name :- Mustak Mobile No :-9058614379 | Closed | M/s. SHREERAM CONCRETE | 2199 | Load issue- Today visit Engineer | OPEN | Kapil Solanki
33 | North | 211620292 | 19-01-2025 00:47 | 58.5 | T4.8941.../2420677 | Trip_Genset_Low_Voltage | Open | AKASH GENERATOR SERVICES |  | Visit pending | OPEN | Kapil Solanki
34 | North | 211620055 | 18-01-2025 18:07 | 125.4 | 4H.8042.C4../2420566 | Amber Lamp Alarm Issue Call By Customer Name- Amit Sharma Mo.No.- 9210049072 | Closed | DUTTA ENGG. WORKS | 11 | update pending | OPEN | Kapil Solanki
35 | North | 211620003 | 18-01-2025 17:55 | 160 | 6H.8475.../2420034 | Sound issue Call By Customer Name: Veer Singh Number: 8810530257 | Closed | ANANDEE HOMES | 200 | V-belt loose tightness the same after SPN/FMI 516166/0 reset the alarm | Closed | Kapil Solanki
36 | North | 211619564 | 18-01-2025 17:10 | 320 | F6.8802.../2420215 | Urea leakage issue Call By Customer Name ;-Shravan Kumar No :- 9953895963 | Closed | IMPACT MACHINE TOOLS | 23 | Def overflow from tank | Closed | Kapil Solanki
37 | North | 211618744 | 18-01-2025 14:17 | 125.4 | 4H.8041.../2420241 | Starting Problem Call by : Customer Name :Suhail Sir Contact :8891683583 | Closed | MALABAR GOLD PRIVATE LIMITED | 1050 | update pending | OPEN | Kapil Solanki
38 | North | 211620920 | 19-01-2025 17:44 | 160 | 6H.8475.../2420233 | Genset Trip | Task Start | Dr .Heera Diagnostic Centre Pvt ltd | 10.7 | Def & Coolant level low top up required | Closed | Gourav Sharma
39 | North | 211620898 | 19-01-2025 17:36 | 25 | GP3.8702.../2320003 | Battery issue call by customer name - Satyvir Sharma no - 9799207333 | Task Start | Pawan Tanay Chem Plast Pvt. Ltd. | 189 | Battery 2 cell down From Negative side 1 & 3 cell spec.gravity found 1100 & 1150, Battery voltage 13V show in the controller & Multimeter | Closed | Gourav Sharma
40 | North | 211620825 | 19-01-2025 14:20 | 125.4 | 4H.8041.../2420281 | Starting issue Call by customer Name: Anil Number:8630144045 | Closed | Dr. Leena Chauhan | 2.5 | starting problem due to air lock in fuel line and RL2 Output O2 wire loose tightness the same issue resolve | Closed | Sudhir Awasthi
41 | North | 211620767 | 19-01-2025 12:07 | 20 | GP3.8601.../2420091 | battery Issue Call by customer Name:Trilokinath Pant Number:6398141730 | Task Start | Rajeshwari Hotels and Resorts Private Ltd. | 16 | Found low fuel & Air lock in fuel line remove the air start the DG running well | Closed | Sudhir Awasthi
42 | North | 211620678 | 19-01-2025 11:01 |  | 6H.8475.../2420442 | LINE REJECTION | Closed | Jakson & Company | 1 | update pending | OPEN | Gourav Sharma
43 | North | 211620129 | 18-01-2025 18:41 | 58.5 | T4.8941.../2422991 | Starting/Stopping Issue | Closed | Sant Joseph School | 29 | Maintenance due alarm,reset the alarm issue resolve | Closed | Sudhir Awasthi
44 | North | 211619676 | 18-01-2025 17:30 |  | DV8.8501.C4../2420189 | ECM ERROR CODE | Closed | Electro Equipments | 0.8 | ECU flash Guided by ASE | Closed | Sudhir Awasthi | KRM Check
45 | North | 211618869 | 18-01-2025 14:51 | 30 | 3H.8902.../2320086 | Starting Issue Call By Customer Name :- Anwar Mobile No :- 9837622506 | Closed | JAKSON & COMPANY | 73 | Check DG set found Emergency button push realease the same after found 2A no. wire loose in self starter tightness the same issue resolve | Closed | Sudhir Awasthi
46 | North | 211618718 | 18-01-2025 14:19 | 160 | 6H.8475.../2420222 | DOOR LOCK ISSUE Email by GOEM Name - Neeraj Saini | Closed | Yamuna Synthetics Pvt Ltd | 24 | Canopy door lock adjust | Closed | Gourav Sharma | GOEM issue
47 | North | 211621645 | 20-01-2025 08:23 | 20 | GP3.1021.../2420391 | INSTANCE ID:-100779493 SITE ID:- I-UE-MRPR-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG LOW FUEL ALARM/MAINS CONTACTOR FAULTY NAME:- ARJUN NUMBER:- 7068013561 | Task Start | Reliance Jio Infocomm Limited | 40 | Fuel level not showing in the controller, Because remove the all 6 wires by technician, After connect the wire accordingly guided by VISHAL after controller display on/Off blink | OPEN | Sudhir Awasthi
1 | West | 211617939 | 18-01-2025 11:11 | 500 | DV8.9313.../2400002 | Fitting of KRM unit | Closed | RAIL COACH FACTORY RCF | 629.51 | KRM was replaced with old KRM. | Closed | Jagdeep Saini
2 | West | 211617936 | 18-01-2025 11:08 | 500 | DV8.9313.../2400001 | Fitting of KRM unit | Task Start | SENIOR SECTION ENGINEERS | 589.56 | KRM was replaced with old KRM. | OPEN | Jagdeep Saini
3 | West | 211617807 | 18-01-2025 10:42 | 400 | DV8.8542.C4../2420064 | Tripping Issue Call By Customer Name - Prasad Mobile No -8451027468 | Closed | KKG RMC INFRA PVT LTD | 187.25 | Low adblue level. | Closed | Jagdeep Saini
4 | West | 211617726 | 18-01-2025 10:23 | 30 | 3H.8902.../2421353 | DG set supply is fluctuating. | Closed | ICICI Bank Limited | 1.36 | The engineer visited the site for load trail and educated the customer about the auto and manual modes of the genset. | Closed | Amit Shandilya
5 | West | 211617718 | 18-01-2025 10:19 | 30 | 3H.8902.../2422031 | DG set Starting in Auto mode | Open | ICICI Bank Limited |  | Cancelled | Closed | Jagdeep Saini
6 | West | 211617655 | 18-01-2025 10:11 | 200 | 6H.8435.../2420061 | Emergency Alarm Issue Call By Customer Name :- Vivek Mobile No :-9511897002 | Task Start | CIP. Farm Private Limited | 78 | Low adblue level. | Closed | Jagdeep Saini
7 | West | 211615287 | 17-01-2025 16:06 | 30 | 3H.8902.../2421149 | KG-ALTERNATORS-OTHERS FAILURES | Closed | VENTURE STEELS PVT LTD | 1 | Line Rejection SR, Space heater required in alternator as area is soggy and wet | Closed | Amit Shandilya
8 | West | 211615257 | 17-01-2025 16:01 | 30 | 3H.8902.../2421168 | KG-ALTERNATORS-OTHERS FAILURES | Closed | VENTURE STEELS PVT LTD | LR | Line Rejection SR, Space heater required in alternator as area is soggy and wet | Closed | Amit Shandilya
9 | West | 211615249 | 17-01-2025 15:55 | 30 | 3H.8902.../2421185 | KG-ALTERNATORS-OTHERS FAILURES | Closed | VENTURE STEELS PVT LTD | LR | Line Rejection SR, Space heater required in alternator as area is soggy and wet | Closed | Amit Shandilya
10 | West | 211615237 | 17-01-2025 15:49 | 30 | 3H.8902.../2421181 | KG-ALTERNATORS-OTHERS FAILURES | Closed | VENTURE STEELS PVT LTD | LR | Line Rejection SR, Space heater required in alternator as area is soggy and wet | Closed | Amit Shandilya
11 | West | 211614676 | 17-01-2025 14:08 | 40 | 3H.8951.../2421121 | Sound/Vibration Issue | Closed | Vakman Ventures | 21.2 | Exhaust cilencer cliding was loose. So abnormal sound was coming from the genset. | Closed | Vijay Patil
12 | West | 211614535 | 17-01-2025 13:20 | 30 | 3H.8902.../2421914 | KRM activation | Cancelled | Jagdamba Poultry Farm |  | Cancelled | Closed | Jagdeep Saini
13 | West | 211614435 | 17-01-2025 13:10 | 58.5 | T4.8941.../2422764 | Starting Issue Call By Customer Name - Sandeep Mobile No -9881858879 | Closed | Ambition flying club pvt ltd | 5.54 | DG contactor was not holding so tightened the relay coil wire and problem solved. | Closed | Jagdeep Saini
14 | West | 211620881 | 19-01-2025 16:27 | 25 | GP3.8702.../2421816 | Diesel Tank leakege | Task Start | Lcc Projects Pvt. Ltd. . | LR | Fuel tank leakage issue. | OPEN | Vijay Patil | Goem issue
15 | West | 211620707 | 19-01-2025 10:45 | 58.5 | T4.8941.../2420890 | Starting Issue Call by Customer Name -JIGAR TRIVEDI Mobile No - 9925455770 | Open | Euro Anchor Sanitaryware Industries Private Limited. | 71.8 | Alarm- Fail to start and 157/14, Genset was not cranking sometimes. So tightented the all wire connections on relay board 13RB1 but issue was same so replaced the relay board and issue resolved. | Closed | Amit Shandilya
16 | West | 211614174 | 17-01-2025 12:20 | 30 | 3H.8902.../2421542 | DG not starting 503449 | Open | ICICI BANK LTD | 1.2 | Contactor holding Issue,So need to be replace. | OPEN | Amit Shandilya | Service history
17 | West | 211614147 | 17-01-2025 12:14 | 5.5 | CC1.1013.../2400411 | Starting Issue Email By - KGD Name - Surekha Auti | Closed | Royal Shuttlers Arenaa | 30 | The genset was tripping due to overload-23A, so the engineer suggested 80% load to the customer and suggested to increase the load in a phased manner. | Closed | Jagdeep Saini
18 | West | 211614100 | 17-01-2025 12:03 | 625 | DV0.8501.C4../2420043 | servicing | Closed | Mind Space Shelters LLP. | 50.1 | Automation problem, genset was starting in auto mode but would stop immediately. So engineer checked and found that remote start wire was connected to load side, corrected the connections and problem was solved. | Closed | Jagdeep Saini | KRM Data not showing.
19 | West | 211614005 | 17-01-2025 11:50 | 30 | 3H.8902.../2421544 | Electrical Problems | Closed | Dr. Gunes Nirmal Nursing Home | 9 | Customer Side issue. | Closed | Jagdeep Saini
20 | West | 211613497 | 17-01-2025 11:32 | 30 | 3H.8902.../2422032 | Alarm issue EGR vlv H bridge flt-over crt | Closed | SAMARTH ENTERPRISES | 153.1 | SPN/FMI- 2791/18, DTC cleared but our suggestion to the engineer is to flash the ECU if this error code repeats. | Closed | Jagdeep Saini
21 | West | 211613584 | 17-01-2025 11:29 | 160 | 6H.8475.../2420214 | Start Issue Email By - GOEM Name - ROHIT KAMBLE | Task Start | Kritija Construction. | 494 | SPN/FMI-654/5, Checked the continuity from ECU to enjector found ok. Flashed and replaced the ECU but problem is same. Customer wants to replce the DG. | OPEN | Jagdeep Saini
22 | West | 211613419 | 17-01-2025 11:15 | 625 | DV0.8501.C4../2420051 | ECU Amber alarm Issue Email By - Customer Name -Ravikiran Mal | Closed | Mind Space Shelters LLP. | 52.2 | Low DEF level. | Closed | Jagdeep Saini
23 | West | 211613006 | 17-01-2025 08:40 | 58.5 | T4.8941.../2422959 | FUEL LEAKAGE | Closed | Medinnova System Private Limited. | LR | Fuel leakage from the leak-off pipe, so the NRV was removed and reinstalled, and the problem was solved. | Closed | Amit Shandilya
24 | West | 211611457 | 16-01-2025 14:40 | 15 | GP3.8501.../2421368 | Engine serial number on the controller is showing one digit more | Task Start | JAKSON & COMPANY | LR | Engine serial number was not showing correctly in the controller, programmed the controller. | Closed | Amit Shandilya
25 | West | 211611262 | 16-01-2025 13:41 | 5.5 | CC1.1013.../2400117 | Controller Issue Cal By Service Dealer Name - Mohsin . Number - 9156357673 | Task Start | Mr. Navneet Kumar.. | 16.2 | The genset was starting in Auto mode because mains was unhealthy - 175V. So the customer complained that the genset was starting even when mains was available. | Closed | Jagdeep Saini
26 | West | 211610678 | 16-01-2025 12:16 | 20 | GP3.1021.../2420135 | Fuel Sensor issue | Closed | Reliance Jio Infocomm Limited | 12 | Alarm-Fuel Open LT, Fuel level sensor wire was open so connected the wire properly. | Closed | Amit Shandilya
27 | west | 211626014 | 21-01-2025 12:29 | 625 | DV0.8501.C4../2420032 | Error Code issue Call By service dealer Name :- Ashok Parmar Mobile No :- 9601472233 | Task Start | Transworld Logistics Pvt. Ltd. | 5 | SPN/FMI- 4336/2,523531/1, 4358/2 A Bank dosing module was not spraying DEF even at above 170 degrees. Hence DEF connections from DEF tank to supply module were checked and it was found that the connections were interchanged | OPEN | Amit Shandilya | 17/1/2025
28 | west | 211623829 | 20-01-2025 16:51 | 160 | 6H.8475.../2420181 | Starting Issue. Call By Customer. Name:-Sachin Kasid Mobile No.:- 9822890787 | Task Start | Divine Ventures & Lanke Birje Associates | 2 | The genset was not starting because fuel was not coming from the pump to the common rail. EDO placed for pump. | OPEN | Jagdeep Saini | KRM- Not SPN/FMI(Low Fuel Level)
1 | East | 211628336 | 21-01-2025 18:18 | 82.5 | 5H.8901.../2420053 | Automation issue Call By Customer Name :- Parmanand Mandal Mobile No :- 7365043398 | Task Start | Rapiscan Systems | 68 | Today SE will visit site | OPEN | Prosanjit saha
2 | East | 211628077 | 21-01-2025 17:24 | 15 | GP3.8501.../2420195 | Starting/Stopping Issue | Task Start | BIRAJA CONSTRUCTION | 43 | Visit Pending | OPEN | Ujjwal Das
3 | East | 211626691 | 21-01-2025 14:52 | 5 | CP1.1003.../2400068 | Starting/Stopping Issue | Task Start | M/s. HOTEL ANURADHA, | 32 | Visit Pending | OPEN | Ujjwal Das
4 | East | 211626460 | 21-01-2025 14:00 | 82.5 | 5H.8901.../2420075 | Huntting Issue Call By Customer Name:-Rajesh . Number:-9064207993 | Task Start | Bankura Store LLP. | 25 | Visit Pending | OPEN | Prosanjit saha
5 | East | 211626341 | 21-01-2025 13:34 | 625 | DV0.8501.C4../2420046 | Maintenance Due Alarm Call By Customer Name :- Manzarul haque . Mobile No :-9331023443 | Open | Kapany Engineering .Co. P. Ltd. | 46 | Customer required service no issue in DG | CLOSED | Prosanjit saha
6 | East | 211625703 | 21-01-2025 11:19 | 625 | DV0.8501.C4../2420144 | Leakage Issue | Closed | Snonwman Logistick Ltd. | 76 | SE found Fuel Leakage was due fuel filter benzo loose. After tightening the benzo no leakage in fuel system , issue resolved | CLOSED | Prosanjit saha
7 | East | 211623914 | 20-01-2025 17:08 | 20 | GP3.8601.../2320035 | Leakage Issue | Closed | The Himalaya Sweets | 8 | SE found fuel leakage from suction hose.,Then open the hose & clean it properly & then refitted. After that found no leakage from there. Issue resolved. | CLOSED | Prosanjit saha | Service History
8 | East | 211622935 | 20-01-2025 14:37 | 20 | GP3.8601.../2421104 | Starting issue Call By Customer Name :- Prince Mobile No :-9547866525 | Closed | Md. Akbar Alam | 12 | SE found DG not started due to loose connection at start relay output point(3) so tigten issue resolved. | CLOSED | Prosanjit saha
9 | East | 211626013 | 21-01-2025 12:29 | 125.4 | 4H.8041.../2420524 | Starting/Stopping Issue | Task Start | M/s. Jaiswal Trading | 233 | Visit pending | OPEN | Ujjwal Das
10 | East | 211624218 | 20-01-2025 18:05 | 15 | GP3.8501.../2420474 | Starting/Stopping Issue | Closed | SAVEER BIOTECH LTD.. | 43 | Update pending | OPEN | Ujjwal Das
11 | East | 211622884 | 20-01-2025 14:21 | 20 | GP3.8601.../2420266 | Fuel Leakage Issue Email by KGD Name - NAGALAND POWERKRAFT | Open | Chakesang Baptist Church | 187 | Visit pending | OPEN | Ujjwal Das
12 | East | 211621731 | 20-01-2025 09:55 | 82.5 | 5H.8901.../2420498 | Starting Issue Email by KGD Name - sunrise power | Open | PRADHAN DEVELOPERS | 111 | Amber alarm showing due to low adblue level and also customer need service SR will be cancelled | OPEN | Prabhakar Kumar | Service History
13 | East | 211619561 | 18-01-2025 17:08 | 45 | 3H.8951.../2421369 | Diesel Leakage Issue Call By KGD Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. | 82 | Site visit is pending | OPEN | Prabhakar Kumar
14 | East | 211601117 | 2025-12-01 08:53 | 30 | 3H.8902.../2422023 | Starting Issue Call By Customer Name :-Satpal Sharma Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS |  | SE alinged site will be attend today . Asset is in remote location | OPEN | Ujjwal Das
1 | North | 211626402 | 21-01-2025 13:47 | 500 | DV8.8501.C4../2320021 | Inspection/Maintenance | Task Start | SUPRA CRAFT PACKAGING (P) LTD. | 433 | Found expension bellow crack replace the same | Closed | Gourav Sharma | Failed Part
2 | North | 211626122 | 21-01-2025 12:45 | 30 | 3H.8902.../2420262 | Starting Issue Call By Customer Name :- Lal Singh Mobile No :-7827447526 | Task Start | Mrs. Simran Pal | 1.45 | Battey discharge, mains supply off from customer end (CC done on 25-11-024) | Closed | Kapil Solanki
3 | North | 211626109 | 21-01-2025 12:44 | 58.5 | T4.8941.../2422800 | Tripping Alarm Issue Email By - OEM Name - JITENDRA GAJJA | Task Start | VISHAL KUMAR TAK | 36 | Check KRM found EGR related fault code 2791/18 (UPDATE PENDING) | OPEN | Gourav Sharma
4 | North | 211625968 | 21-01-2025 12:17 | 20 | GP3.8601.../2420464 | Flickering | Task Start | Red Rose Convent School | 98 | Voltage set from AVR then found no issue related Flickring | Closed | Sudhir Awasthi
5 | North | 211625920 | 21-01-2025 12:03 | 125.4 | 4H.8041.../2420092 | VOC -ENGINE NOT STARTING DUE TO RECOIL STATOR ASSEMBLY FAULTY Customer Name -Raj Customer Number -7297072739 Mode- SR Generated through CDI calling. | Task Start | Raj Engineering Works | 15 | Found CAC hose defective replace the same, but load issue Today ASE visit | OPEN | Gourav Sharma | Details Required
6 | North | 211625870 | 21-01-2025 11:57 | 20 | GP3.8604.../2420114 | INSTANCE ID:-100741914 SITE ID:- I-UE-KAMZ-ENB-9000 CALL BY CUSTOMER// DG ISSUE:- DG STARTING PROBLEM NAME:- Adit NUMBER:- 7309283862 | Task Start | Reliance Jio Infocomm Limited | 1338 | Under Voltage alarm J1939 Check wiring harness continuity is OK, we are arranging new coolant temperature sensor for replacement | OPEN | Sudhir Awasthi
7 | North | 211625790 | 21-01-2025 11:41 | 58.5 | T4.8941.../2423193 | VOC -FUEL LEVEL SENSOR DEFECTIVE . Customer Name -Deepu Customer Number -9587073666 Mode- SR Generated through CDI calling. | Task Start | D D Engineering Work | 72 | update pending | OPEN | Gourav Sharma
8 | North | 211625697 | 21-01-2025 11:23 | 30 | 3H.8902.../2420473 | Starting Issue Call By Customer Name : Aaisha .. No : 9958891400 | Task Start | Centre Half Service Station. | 11 | DG not start in auto check the panel found wire was loose tightness the same the issue resolve | Closed | Kapil Solanki
9 | North | 211625246 | 21-01-2025 09:40 | 125.4 | 4H.8041.../2320177 | Maintenance Sue Alarm Call By Customer Name :- Sohel Khan Mobile No :- 9330493306 | Task Start | Great Food Plaza and Catering Pvt. Ltd. | 559 | Controller show the maintenance due alarm & SPN/FMI 3031/14 reset the alarm & flash the latest file | Closed | Kapil Solanki
10 | North | 211624497 | 20-01-2025 23:46 | 30 | 3H.8902.../2320011 | Alarm & Starting Issue Call By Customer Name :- Parmeet Singh No :- 9899282225 | Open | Parmeet Singh Nayar |  | Visit pending | OPEN | Kapil Solanki
11 | North | 211624441 | 20-01-2025 19:20 | 125.4 | 4H.8041.../2320108 | Tripping Issue Call By Customer Name - Vijay Kumar Number - 9829973147 | Closed | SSSP. Speciality Packagings Pvt. Ltd. | 168 | found throttle valve jammed connect Ikonnect and checked DTC found SPN/FMI 51/0 Throttel valve jammed valve open.then I checked voltage on connector pin no 3 and ground found 5.2 DC voltage and pin no 1&2 5.1DC voltage . reconnect and cleared DTC | Closed | Gourav Sharma
12 | North | 211624364 | 20-01-2025 18:33 | 125.4 | 4H.8041.../2420683 | Starting Issue Call By Customer Name - VIPIN KATHURIA S FASTNERS Number - 9891500846 | Task Start | S. FASTNERS | 71.14 | DG not start remove the air Engine start but When give the load then found DG trip with under speed alarm after Check ITV found ok then check again fuel line then we found NRV faulty - Same replace Today | OPEN | Kapil Solanki
13 | North | 211624018 | 20-01-2025 17:35 | 20 | GP3.8604.../2420198 | VOC -Genset is not starting Customer Name -Shailesh Customer Number -8299698446 Mode- SR Generated through CDI calling. | Open | Reliance Jio Infocomm Limited |  | Cancelled-Problem solve in Tele. Discussion | Cancelled | Sudhir Awasthi
14 | North | 211623572 | 20-01-2025 16:15 | 40 | 3H.8951.../2421533 | Starting Issue. Call by Customer. Name:- Shital Jha Mobile No.:- 9868027165 | Task Start | Boustead Controls & Electric India Pvt. Ltd. | 1.2 | Battery voltage low, Customer use the own battery charger but Battery not proper charge, Educate the customer please connection our battery charger | OPEN | Kapil Solanki
15 | North | 211623468 | 20-01-2025 15:55 | 250 | F6.8841.../2420179 | Leakage Issue | Closed | RHENUS CONTRACT LOGISTICS INDIA PRIVATE LIMITED | 118 | Coolant leakage from radiator hose clamp bottom side | Closed | Kapil Solanki
16 | North | 211622655 | 20-01-2025 13:19 | 15 | GP3.8501.../2421857 | Genset Trip | Closed | R. K. Traders | 3 | Fuel level low & Educate the customer for maintain the fuel & Area space properly because it is rental DG | Closed | Sudhir Awasthi
17 | North | 211622634 | 20-01-2025 13:06 | 320 | F6.8802.../2420011 | Main Alternator Faulty | Task Start | MALIK ENTERPRISES | 146 | Nidec team shaded the Alternator - SD engineer only couple the alternator | Closed | Kapil Solanki | Details Required
18 | North | 211622244 | 20-01-2025 11:50 | 250 | DV8.9840.../2420009 | Starting/Stopping Issue | Task Start | METAFLEX DOORS INDIA PRIVATE LIMITED. | 10.29 | DG start in first crank but not start in sencond crank generate the fault code Crank sensor & cam sync Check the continuty with ECU found ok.found rusting in flywheel and clean it- Under observation | OPEN | Kapil Solanki | Gas Engine
19 | North | 211617938 | 18-01-2025 11:10 | 20 | GP3.8604.../2420177 | INSTANCE ID:-100742276 SITE ID:-I-UE-BNDH-ENB-9069 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- GRISH NUMBER:- 9696104358 | Closed | Reliance Jio Infocomm Limited | 460 | Under voltage alarm found 16RB1-R11 relay wire loose tightness the same issue resolve | Closed | Sudhir Awasthi
20 | North | 211617753 | 18-01-2025 10:30 | 125.4 | 4H.8041.../2320009 | Nosel issue Call by customer Name: Pramod Kumar Number:7838691135 | Cancelled | Dr. Pardeep Berry, MS Amita Singh, Miss Aditi Mathur |  | Cancelled-Problem solve in Tele. Discussion | Cancelled | Kapil Solanki
21 | North | 211615295 | 17-01-2025 16:12 | 58.5 | T4.8941.../2421961 | Starting/Stopping Issue | Closed | ELITE MOTORS | 51 | Tightness the wiring in panel & found battery terminal | Closed | Sudhir Awasthi
22 | North | 211614503 | 17-01-2025 13:13 | 20 | GP3.1021.../2420461 | INSTANCE ID:-100784731 SITE ID:-I-UE-ABDD-ENB-0934 CALL BY CUSTOMERA:- DG ISSUE :- DG UNDER VOLTAGE ALRAM/G13,39 ALRAM NAME :-KRISHNAKANT NUMBER :- 8299698840 | Open | Reliance Jio Infocomm Limited |  | Under Cancellation- | Cancelled | Sudhir Awasthi
23 | North | 211613260 | 17-01-2025 10:33 | 25 | GP3.8702.../2421267 | Voltage Fluctuation | Open | ICICI Bank Limited |  | Under Cancellation- | Cancelled | Sudhir Awasthi
24 | North | 211613089 | 17-01-2025 09:50 | 25 | GP3.8702.../2420272 | Genset Trip | Completed | VEER BALAJI FUEL CENTRE | 40 | SPN/FMI 100/1 Check wiring found ok then replace the lub oil sensor but issue is same | OPEN | Sudhir Awasthi
25 | North | 211627445 | 21-01-2025 16:08 | 25 | GP3.8702.../2420572 | Leakage Issue | Closed | Birpal | 110 | coolant leakage from Engine Radiator hose pipe Engine Radiator hose pipe clamp proper tight and check Engine coolant leakage problem done. | Closed | Kapil Solanki
26 | North | 211626637 | 21-01-2025 14:38 | 58.5 | T4.8941.../2420784 | Starting/Stopping Issue | Task Start | Auriga Homes | 172 | found emergency stop alarm indicat. check and found Panel emergency switch wire 1H loose tightness the properly then issue resolve | Closed | Sudhir Awasthi
27 | North | 211622460 | 20-01-2025 12:36 | 400 | DV8.8542.C4../2420014 | Starting Issue Call By Customer Name :- Tara Chand Mobile No :-9728993286 | Task Start | Powercam Electricals Pvt. Ltd. | 220 | Auto starting Issue ; Customer Pannel side Issue,Auto comand not get by Customer's side | Closed | Ved Prakash Gupta
28 | North | 211622453 | 20-01-2025 12:33 | 25 | GP3.8702.../2420011 | AMF Panel not working,electricity issue electricity cut every 15 to 20 second kindly check on priority-504176 | Open | ICICI Bank Limited |  | Under Cancellation-work not comes under KOEL scope | Cancelled | Ved Prakash Gupta
29 | North | 211622381 | 20-01-2025 12:22 | 25 | GP3.8702.../2420298 | Auto mission issue | Task Start | gurudwara sri guru singh sabha | 7 | KG640 controller setting is not set and set the KG 640 controller setting and connection the main wire is MR1 found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | Details Required
30 | North | 211622005 | 20-01-2025 10:55 | 125.4 | 4H.8041.../2420163 | Sound/Vibration Issue | Task Start | Polyfil Haryana. | 314 | SPN/FMI-1761/16 ; Low AdBlue Level ; Top-up the same & same educated to customer ; Fan Belt found slightly loose so tightened the same | Closed | Ved Prakash Gupta
31 | North | 211621905 | 20-01-2025 10:35 | 58.5 | T4.8941.../2422086 | Starting/Stopping Issue | Task Start | S R S Engg Co | 41.23 | Starting issue due to 2B3 wire found loose in Relay Board so Tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
32 | North | 211620873 | 19-01-2025 16:10 | 30 | 3H.8902.../2420044 | Starting/Stopping Issue | Task Start | Mr. Laykat Rai | 123 | controller show alarm under speed so Check engine air locking,No issue found , dg voltage and set controller settings after settings check engine start and stop | Closed | Ved Prakash Gupta
33 | North | 211620794 | 19-01-2025 13:14 | 40 | 3H.8951.../2421308 | Starting Issue Call by Customer Name - ANIL KUMAR Mobile 9971230939 | Task Start | ANIL KUMAR GENSETS | 447 | Expansion Ballow found broken on site ,EDO Placed for same;recieved by 27 Jan | Open | Ved Prakash Gupta
34 | North | 211628294 | 21-01-2025 18:06 | 400 | DV8.8542.C4../2420085 | Fuel Gauge Issue Email By KGD Name:-Poonam Shedage | Open | Accurate Powertech India Private Limited |  | Under Cancellation-same rectified on telephonic discussion | Cancelled | Ved Prakash Gupta
35 | North | 211626956 | 21-01-2025 15:43 | 500 | DV8.8501.C4../2320041 | Genset Trip | Task Start | Ian Macleod Distillers India Pvt. Ltd. | 291 | SPN/FMI-97/2 Water in Fuel in previous codes & 1761/16 Low AdBlue Level ; check the fuel condition from Water separator & tank , found ok ,Top-up the AdBlue & resolve the Issue | Closed | Ved Prakash Gupta
36 | North | 211626498 | 21-01-2025 14:20 | 82.5 | 5H.8901.../2420804 | Under Speed Alarm Issue Call By Customer Name - Naveen .. Number - 7015471751 | Task Start | Dhani Power Solutions | 164.35 | SPN/FMI-1761/16 ; Low AdBlue Level ; Top-up the same & same educated to customer | Closed | Ved Prakash Gupta
37 | North | 211626504 | 21-01-2025 14:14 | 160 | 6H.8475.../2420400 | Leakage Issue | Closed | Veepee Graphic Solutions Pvt. Ltd. | 2.22 | Coolant Leakage found on top of Radiator due to Clamp found loose so Tightened the same & resolve the issue | Closed | Ved Prakash Gupta
38 | North | 211626442 | 21-01-2025 14:00 | 82.5 | 5H.8901.../2420022 | Starting/Stopping Issue | Task Start | C. L. ENTERPRISES | 117 | Starting issue due to Battery Charger was off by Customer,same educated to customer to keep battery charger on for Auto starting | Closed | Ved Prakash Gupta
39 | North | 211626390 | 21-01-2025 13:47 | 15 | GP3.8501.../2420097 | Starting Issue Call By Customer Name - Dilawar . Number - 7973401214 | Task Start | Fertilizer Centre | 128 | Supply wire to Battery Charger found defective so change the wire for supply to Charger & resolve the Issue | Closed | Ved Prakash Gupta
40 | North | 211626218 | 21-01-2025 13:08 | 15 | GP3.8501.../2420293 | Leakage Issue | Closed | Dr. Sandeep Malik. | 36 | Lube oil leakage found due to drain plug nozzle found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
41 | North | 211626121 | 21-01-2025 12:45 | 125.4 | 4H.8041.../2420018 | Alarm Issue Call By Customer Name : Varun Goyal Mobile No : 9899266223 | Open | Sharkline Appliances |  | Under Cancellation-Rectified on Call | Cancelled | Ved Prakash Gupta
42 | North | 211625719 | 21-01-2025 11:25 | 30 | 3H.8902.../2420951 | Starting/Stopping Issue | Task Start | Khalsa Construction Company | 734 | Emergency switch found pressed on site so release the same & same educated to customer | Closed | Ved Prakash Gupta
43 | North | 211625432 | 21-01-2025 10:24 | 160 | 6H.8475.../2420087 | AUTOMATION | Closed | Sattva Multispeciality Hospital | 4 | Automation installation done in Customer's Pannel so re-install the same in Controll pannel,Auto starting issue resolved | Closed | Ved Prakash Gupta
44 | North | 211625421 | 21-01-2025 10:19 | 15 | GP3.8501.../2420341 | Starting problem | Closed | JAN SEWA SANSTHAN | 44.5 | Starting Issue,2A1 fuse found faulty in Pannel so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
45 | North | 211625394 | 21-01-2025 10:17 | 82.5 | 5H.8901.../2420648 | error code issue | Task Start | NARAYAN CONSTRUCTION |  | Under Cancellation-Multiple SR open on same asset | Cancelled | Ved Prakash Gupta
46 | North | 211623843 | 20-01-2025 16:51 | 200 | 6H.8435.../2420227 | Starting/Stopping Issue | Closed | The Royal Velvet. | 17 | Coolant leakage found on bottom side of Radiator so change the clamp & Top-up the water in Radiator | Closed | Ved Prakash Gupta
47 | North | 211623840 | 20-01-2025 16:49 | 320 | F6.8802.../2420264 | Leakage Issue | Closed | The Royal Velvet. | 18 | Coolant Level found low on site so top-up the same & run the DG for 30 minutes,issue resolved | Closed | Ved Prakash Gupta
48 | North | 211623227 | 20-01-2025 15:09 | 400 | DV8.8542.C4../2420034 | Trip_Genset_Low_Voltage | Closed | Directorate Of Urban Local Bodies Haryana. | 467 | Engine Starting issue in first crank in moning,check all the parameters of DG but no such issue found | Closed | Ved Prakash Gupta
49 | North | 211622833 | 20-01-2025 14:08 | 500 | DV8.8501.C4../2320073 | VOC -Under voltage problem in genset Customer Name -Manmohan Gupta Customer Number -9350613807 Mode- SR Generated through CDI calling. | Task Start | A C POLYCOATERS PRIVATE LIMITED | 144 | RPM Derail in first crank in Morning;EDO Placed for modified lift pump | Open | Ved Prakash Gupta
1 | North | 211630482 | 22-01-2025 13:03 | 30 | 3H.8902.../2420420 | Abnormal Sound Issue Call By Customer Name :- Sunil Gupta Mobile No :-9599034695 | Closed | Sunil Kumar Gupta. | 79 | check abnormal sound is coming from silence, check and found silence spot stip create abnormal sound, tightness with washer, and check dg set start and stop ok now no abnormal sound coming from DG set | Closed | Kapil Solanki
2 | North | 211630395 | 22-01-2025 12:47 | 20 | GP3.1021.../2420471 | VOC-ENGINE NOT STARTING - AIR LOCK IN FUEL SYSTEM Customer Name -Atul Singh Customer Number -9984209830 Mode- SR Generated through CDI calling. | Task Start | Reliance Jio Infocomm Limited |  | Visit Pending | OPEN | Sudhir Awasthi
3 | North | 211630373 | 22-01-2025 12:37 | 20 | GP3.1021.../2420461 | INSTANCE ID:-100784731 SITE ID:-I-UE-ABDD-ENB-0934 CALL BY CUSTOMER:- DG ISSUE :- DG UNGER VOLATGE ISSUE /J13,39 NAME :-KRISHNAKANT NUMBER :- 8299698840 | Task Start | Reliance Jio Infocomm Limited |  | Visit Pending | OPEN | Sudhir Awasthi
4 | North | 211630147 | 22-01-2025 11:47 | 25 | GP3.8702.../2421007 | Starting/Stopping Issue | Task Start | T. V. Today Network Limited. | 7 | found automation issue checked accordingly then found selector switch in manual condition in amf panel correct the same and educate the customer about the same and then check showing error code 97/5 in dm 1 checked and clear the dtc issue resolved | Closed | Sudhir Awasthi
5 | North | 211630102 | 22-01-2025 11:34 | 200 | 6H.8435.../2420193 | Starting/Stopping Issue | Task Start | United Power Solution. | 4.7 | Battery water level low and coolant leval low and battery tarminal is loose and tight and engine is running ok manual and auto start dg set and oil service due (CC done ON 18-10-2024) | OPEN | Kapil Solanki
6 | North | 211630045 | 22-01-2025 11:22 | 40 | 3H.8951.../2320031 | Protect Lamp On Alarm Call By Customer Name :- Jogindra Mobile No :-9811262581 | Open | Sai Lighting Components |  | Visit Pending | OPEN | Kapil Solanki
7 | North | 211629991 | 22-01-2025 11:13 | 57 | T4.8941.../2320093 | Sarting Issue Call By Customer Name :- Rishav Gupta Mobile No :- 9810539132 | Task Start | ROHIN STEEL INDUSTRIES | 150.31 | Check battery voltage was lowbecause rats had cut the wiring and battery charger connection done on the board and engine is running ok manual | OPEN | Kapil Solanki
8 | North | 211629753 | 22-01-2025 10:54 | 57 | T4.8941.../2420460 | Leakage Issue | Closed | Yogi Raj Shri Ram Chiritable Trust | 28 | Fuel leakage found check high pressure pipe (FIP to common) faulty then replace high pressure pipe and start engine running normally leakage problem | Closed | Sudhir Awasthi | Service History
9 | North | 211629503 | 22-01-2025 10:16 | 625 | DV0.8501.C4../2420041 | Error code issue | Task Start | THE PROJECT MANAGER CONSTRUCTION UNITUTTARAKHAND PAY JAL NIGAM | LR-7 | Multiple error code show in the Controller then Check & Found 2Amp. fuse defective after Flash the ECU & DCU after that issue resolve | Closed | Sudhir Awasthi
10 | North | 211629333 | 22-01-2025 09:02 | 30 | 3H.8902.../2420303 | Genset Trip | Cancelled | Senani Service Station. |  | Cancelled- SR open by mistake | Cancelled | Kapil Solanki
11 | North | 211630529 | 22-01-2025 13:13 | 320 | F6.8802.../2320008 | Coolant Leakage and White Smoke issue Call By Customer Name ;- Gohar Bashir No :- 7006488097 | Open | Golden Agrosense | 108 | Visit pending | KRM | Ved Prakash Gupta
12 | North | 211630141 | 22-01-2025 11:42 | 1000 | DV8.8502.C4../2420001 & 2420002 | Starting Issue Call By Service Dealer Name :- Shalini Mobile No :-7973080439 | Task Start | SRG. Developers & Promoters | 142 | GCB Fail To Stop ; Checked & Found Auxialary Contactor found faulty due to which GCB not able to hold ; same complaint raised to L & T | Open | Ved Prakash Gupta
13 | North | 211630005 | 22-01-2025 11:15 | 5.5 | CC1.1013.../2400002 | Battery issue & Oil leakage issue Call By Customer Name :- Sandip Kumar Shahu Mobile No.:- 9078505468 | Task Start | RANK SOLUTIONS SERVICES | 22 | Battery Voltage found low due to mains supply not connected to Battery Charger so connected the same & resolve the issue after Charging | Closed | Ved Prakash Gupta
14 | North | 211629801 | 22-01-2025 10:56 | 57 | T4.8941.../2320183 | Starting issue | Task Start | TECHNOCRAT MOULDINGS PRIVATE LIMITED | 195.41 | Y-Phase Under Voltage Alarm showing on controller , Checked & found Y Phase fuse faulty so replace the same & resolve the issue | Closed | Ved Prakash Gupta
15 | North | 211629765 | 22-01-2025 10:53 | 20 | GP3.8601.../2320002 | Starting problem | Task Start | PHOTON COMPUTERS INDIA PRIVATE LIMITED | 164.36 | R-Phase Under Voltage Alarm showing on controller , Checked & found R Phase fuse faulty so replace the same & resolve the issue | Closed | Ved Prakash Gupta
16 | North | 211626498 | 21-01-2025 14:20 | 82.5 | 5H.8901.../2420804 | Under Speed Alarm Issue Call By Customer Name - Naveen .. Number - 7015471751 | Closed | Dhani Power Solutions | 164.35 | SPN/FMI-1761/16 , AdBlue Level Low ; Top-up the same & educate customer to keep level minimum 50% | Closed | Ved Prakash Gupta
17 | North | 211622688 | 20-01-2025 13:24 | 320 | F6.8802.../2320008 | Coolant Leakage and White Smoke issue Call By Customer Name ;- Gohar Bashir No :- 7006488097 | Task Start | Golden Agrosense |  | Under Cancellation-Rectified on Call | Cancelled | Ved Prakash Gupta
18 | North | 211622554 | 20-01-2025 12:52 | 125.4 | 4H.8041.../2420231 | Abnormal Sound Issue Call By Customer Name - RAHUL ARRORA Number - 9779785649 | Task Start | Itechnolabs Software Pvt. Ltd. | 52.11 | SPN/FMI-1761/16 , AdBlue Level Low ; Top-up the same & educate customer to keep level minimum 50% | Closed | Ved Prakash Gupta
19 | North | 211622468 | 20-01-2025 12:36 | 40 | 3H.8951.../2420061 | Starting issue Call By Customer Name :- Veer. Mobile No :- 9878777181 | Task Start | Kamaths Natural Retail Pvt. Ltd. | 64 | Controller was not getting +ve supply once confirmed after bypass ; Check Battery supply to controller & re-conneceted the ECU Connector & ECU to Controller connector ; afterthat on the controller,issue resolved | Closed | Ved Prakash Gupta | Under Observation
20 | North | 211622389 | 20-01-2025 12:26 | 320 | F6.8802.../2420096 | Electrical Problems | Task Start | Gurdev Hospital | 75 | DG Starting Issue in auto mode so check connections then found to auto connections wire non1c2 and 49 losse connections then retight the connection | Closed | Ved Prakash Gupta
21 | North | 211621919 | 20-01-2025 10:42 | 20 | GP3.8601.../2420660 | Abnormal Sound Issue Call By SD Name:-Aakib Rashid No:6006437838 | Task Start | Rahat Complex. | 120.5 | Customer raised complaint as Starting Issue but no such issue observed on site | Closed | Ved Prakash Gupta
22 | North | 211619971 | 18-01-2025 17:44 | 320 | F6.8802.../2420305 | Electrical Problems | Closed | SPV RESORTS AND BANQUETS PVT LTD | 7 | Check all the wiring connection &found MCB 2B1 loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta | Service History
23 | North | 211626450 | 21-01-2025 14:05 | 25 | GP3.8702.../2320025 | Starting Issue Call By Customer Name :- Tilak Mobile No :- 9082651 | Closed | Ind Spinx Precision Limited (Unit-B) | 62 | Battery -ve terminal found loose so connected the same & clean the terminals ,issue resolved | Closed | Ved Prakash Gupta
24 | North | 211626033 | 21-01-2025 12:26 | 40 | 3H.8951.../2420480 | DG PROBLEM | Open | ICICI Bank Limited | 168 | Customer raised complaint as Starting Issue but no such issue observed on site | Closed | Ved Prakash Gupta
25 | North | 211625470 | 21-01-2025 10:32 | 15 | GP3.8501.../2421377 | Black Smoke Issue. Call by Customer. Name:- Jetendra Kumar Mobile No.:-8082848412 | Task Start | BHARAT GENERAL STORE | 135 | Visit pending | Open | Ved Prakash Gupta
26 | North | 211625438 | 21-01-2025 10:25 | 58.5 | T4.8941.../2422632 | Starting Issue And battery Issue call by customer Name: Number: | Open | Bharat Rajeev and Associattes |  | Under Cancellation-Wrongly Open | Cancelled | Ved Prakash Gupta
27 | North | 211624296 | 20-01-2025 18:21 | 15 | GP3.8501.../2420585 | Starting Issue Call By Customer Name :- Navjout Kaur Mobile No :-7999999316 | Open | I. S. Trading C/o. |  | Under Cancellation-Customer not given approval | Cancelled | Ved Prakash Gupta
28 | North | 211624067 | 20-01-2025 17:32 | 30 | 3H.8902.../2421481 | Starting/Stopping Issue | Closed | SANT MALHOTRA | 6.3 | Starting issue due to Mains phase supply to controller found interchange | Closed | Ved Prakash Gupta | Details Required
1 | East | 211630758 | 22-01-2025 14:21 | 160 | 6H.8475.../2420276 | Automation Issue | Task Start | Energito Electricals Pvt. Ltd. | 64 | Today SE will visit site | OPEN | Prosanjit saha
2 | East | 211630709 | 22-01-2025 14:04 | 15 | GP3.8501.../2420238 | Electrical Problems | Task Start | Nath Grocery. | 4 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Prosanjit saha
3 | East | 211628336 | 21-01-2025 18:18 | 82.5 | 5H.8901.../2420053 | Automation issue Call By Customer Name :- Parmanand Mandal Mobile No :- 7365043398 | Task Start | Rapiscan Systems | 48 | Customer side issue there was automation problem and also found amber lamp on due to the low adblue level so educated customer to maintain DEF level. | CLOSED | Prosanjit saha
4 | East | 211628077 | 21-01-2025 17:24 | 15 | GP3.8501.../2420195 | Starting/Stopping Issue | Task Start | BIRAJA CONSTRUCTION | 15 | SR created by mistake so cancelled customer need service. | CANCELLED | Ujjwal Das
5 | East | 211626460 | 21-01-2025 14:00 | 82.5 | 5H.8901.../2420075 | Huntting Issue Call By Customer Name:-Rajesh . Number:-9064207993 | Task Start | Bankura Store LLP. | 56 | Customer required service no issue in DG | CLOSED | Prosanjit saha
6 | East | 211630501 | 22-01-2025 13:07 | 5.5 | CC1.1013.../2400160 | Fueal Pump[ problm Call By Service Dealer Name :- Yashika Mobile No :- 9693063331 | Task Start | Swapan Electrical. | 101 | This is and old case reopened due dealer merging PMG and its solenoid was defective was under EDO. | OPEN | Prabhakar Kumar
7 | East | 211630447 | 22-01-2025 12:55 | 10 | GP3.8301.../2420203 | Maintenance Due Alarm issue and Preventive Maintenance Call By Customer Name :- Manish Mobile No :- 8981989532 | Open | MA BINDWASHANI BHAWAN | 123 | SR created by mistake so cancelled customer need service. | CANCELLED | Prabhakar Kumar
8 | East | 211630341 | 22-01-2025 12:29 | 40 | 3H.8951.../2420759 | Starting/Stopping Issue | Task Start | Amvisha Real Estate Developers Pvt. Ltd. | 19 | visit pending | OPEN | Prabhakar Kumar
9 | East | 211630311 | 22-01-2025 12:26 | 30 | 3H.8902.../2420408 | Starting/Stopping Issue | Task Start | Shine Enterprise | 779 | SPN: 2791,FMI: 31, SPN: 5838,FMI: 1/2 so checked for EGR valve found it was choked so cleaned it and then refitted and cleared all DTC then started DG for trail found no code issue resolved. | CLOSED | Ujjwal Das
10 | East | 211629422 | 22-01-2025 09:53 | 125.4 | 4H.8042.C4../2420841 | Display issue Call By Customer Name :- Amitav Chakraborty Mobile No :- 8178893958 | Cancelled | National Highways Infra Projects Pvt. Ltd. | 16 | Problem resolved without visit o telephonic communication, controlller was not getting on due to DC MCB off. | CANCELLED | Ujjwal Das
11 | East | 211626671 | 21-01-2025 14:47 | 40 | 3H.8951.../2420560 | Starting Issue Cal By Customer Name:-Usha Singh Usha Singh No:- 6205954286 | Task Start | Usha Singh | 132 | SE visited and found DG not cranking so checked battery voltage found OK 12.18V then checked for cranking voltage found Ok 10.78V then checked relay found working properly then further found starter motor solonoid 3 no. wire loose tighten it issue resolved. | OPEN | Prabhakar Kumar
12 | East | 211626013 | 21-01-2025 12:29 | 125.4 | 4H.8041.../2420524 | Starting/Stopping Issue | Task Start | M/s. Jaiswal Trading | 233 | DG was not starting showing underspeed alarm, so checked for airlock tighten all filters, adaptors and banjo bolts proper by cleanning then removed air by fuel filter after that cranked DG started normally issue resolved. | OPEN | Ujjwal Das
13 | East | 211625963 | 21-01-2025 12:12 | 15 | GP3.8501.../2420001 | Red Lamp on Alarm. Call By Customer. Name:- Suraj Kumar Singh Mobile No.:- 7061818030 | Task Start | Deepak Hospital | 368 | Emergency switch was pressed on teleponic communication issue resolved cancellation mail send to helpdesk | CLOSED | Prabhakar Kumar
14 | East | 211624218 | 20-01-2025 18:05 | 15 | GP3.8501.../2420474 | Starting/Stopping Issue | Closed | SAVEER BIOTECH LTD.. | 43 | No issue was in DG only maintanance due alarm on the genset and found emergency switch was pressed | OPEN | Ujjwal Das
15 | East | 211622884 | 20-01-2025 14:21 | 20 | GP3.8601.../2420266 | Fuel Leakage Issue Email by KGD Name - NAGALAND POWERKRAFT | Open | Chakesang Baptist Church | 187 | Lube oil leakage from the oil sump drain adapter welding nut crack at welding area, sump under EDO | OPEN | Ujjwal Das | Details Required
16 | East | 211619561 | 18-01-2025 17:08 | 45 | 3H.8951.../2421369 | Diesel Leakage Issue Call By KGD Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. | 82 | Today SE will visit site | OPEN | Prabhakar Kumar | Failed Part
17 | East | 211601117 | 2025-12-01 08:53 | 30 | 3H.8902.../2422023 | Starting Issue Call By Customer Name :-Satpal Sharma Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS |  | Customer runs DG under 20-30 % load due which soot deposition occured at EGR valve and found SPN: 2791,FMI: 31, SPN: 5838,FMI: 1/2 so checked for EGR valve found it was choked so cleaned it and then refitted and cleared all DTC then started DG for trail found no code issue resolved. | OPEN | Ujjwal Das
1 | West | 211630993 | 22-01-2025 15:30 | 15 | GP3.8501.../2420623 | Starting Issue Call By Customer Name :- Prateek Patel No :- 9978777177 | Closed | Ganesh Enterprise Gj. | 3 | Genset starting issue due to battery cable loose connection. | CLOSED |  | 2024-11-09
2 | West | 211630814 | 22-01-2025 14:36 | 5.5 | CC1.1013.../2400406 | Starting/Stopping Issue | Task Start | AMRUT SHRY CONTAINER COMPANY | 477 | Accidental case, canopy and fuel line damage. | OPEN
3 | West | 211630623 | 22-01-2025 13:37 | 400 | DV8.8542.C4../2420048 | Starting issue | Closed | Ishvaha Enterprises Pvt. Ltd. | 2.3 | SE visited on site for sync activity. | CLOSED
4 | West | 211629709 | 22-01-2025 10:44 | 5.5 | CC1.1013.../2400425 | Starting/Stopping Issue | Task Start | AMRUT SHRY CONTAINER COMPANY | 611 | Fuel solenoid wire damage and exhaust silencer damage. | CLOSED
5 | West | 211629493 | 22-01-2025 10:13 | 58.5 | T4.8941.../2422032 | Diesel Leakage Issue & Display Issue. Call By Customer Name :- Sohail Diwan Mobile No :- 9662531194 | Closed | Mom DJ. Sound | 20 | Fuel leaking from fuel tank plate, fuel gauge was not giving proper value of fuel. So replaced the same. | CLOSED
6 | West | 211629307 | 22-01-2025 08:11 | 58.5 | T4.8941.../2423060 | Oil Leakage Issue Call By Customer Name :-Rakesh Mobile No :-8849978537 | Closed | HANUMAN RAM S/O KHUMA RAM | 189 | Oil leakage from front oil seal radiator site. So replaced the oil seal. | CLOSED
7 | West | 211626014 | 21-01-2025 12:29 | 625 | DV0.8501.C4../2420032 | Error Code issue Call By service dealer Name :- Ashok Parmar Mobile No :- 9601472233 | Closed | Transworld Logistics Pvt. Ltd. | 18 | DEF connection was interchange so dosing module chockup. Need to be replace. | OPEN
8 | West | 211626008 | 21-01-2025 12:26 | 125.4 | 4H.8042.C4../2420162 | Leakage Issue | Closed | YMCA OASIS | 254 | Flyweel side oil leakage so replaced oil seal. | CLOSED | Photo Required
9 | West | 211628274 | 21-01-2025 17:59 | 200 | 6H.8435.../2420271 | Starter replacement | Task Start | KALA GENSET PRIVATE LIMITED | LR | The genset was not cranking because the starter motor solenoid was not working. | CLOSED
1 | North | 211636761 | 23-01-2025 18:45 | 250 | F6.8842.C4../2420015 | ECU Amber ka alarm aarha h | Open | Satyam Packaging | 29.27 | Visit pending | OPEN | Gourav Sharma
2 | North | 211636241 | 23-01-2025 16:52 | 125.4 | 4H.8042.C4../2420345 | LINE REJECTION | Open | TS. Jaina Construction | 4.21 | Visit pending | OPEN | Gourav Sharma
3 | North | 211635463 | 23-01-2025 16:25 | 57 | T4.8941.../2320139 | Starting Issue Call By Customer Name :-Manish Kumar Mobile No :- 9625939742 | Task Start | Msafe | 204 | SPN/FMI 157/14 Battery low because charger connection not done from customer end, Now connect the charger & battery charging, Clear the fault code | Closed | Kapil Solanki
4 | North | 211635029 | 23-01-2025 15:54 | 10 | GP3.8301.../2420297 | Inspection/Maintenance | Closed | BINA PRASAD | 4 | Battery Voltage low charger not connected, Supply disconnected from customer end because customer use the solar system Custome make the home | Closed | Kapil Solanki
5 | North | 211634958 | 23-01-2025 15:28 | 125.4 | 4H.8041.../2320115 | Starting Issue Call By Customer Name :- Sunil Parmar Mobile No :-9251419839 | Task Start | Sonysales Packaging India Pvt. Ltd. | 257 | Battery low charger not connected, Supply disconnected from customer end | Closed | Gourav Sharma
6 | North | 211634794 | 23-01-2025 14:50 | 500 | DV8.8501.C4../2420129 | Starting/Stopping Issue | Closed | S. S. Enterprises | 86 | Update pending | OPEN | Gourav Sharma
7 | North | 211634728 | 23-01-2025 14:38 | 500 | DV8.8501.C4../2320039 | Starting/Stopping Issue | Closed | Alphine Infra Projects Pvt. Ltd. | 117 | SR open for Whatsapp bot training | Closed | Kapil Solanki
8 | North | 211634709 | 23-01-2025 14:28 | 20 | GP3.1010.../2300003 | GensetLowSpeed_66,% | Closed | Hosexperts | 60.4 | Controller show the under speed alarm reset the alarm check fuel line found ok now dg set with out load starting ok no leakage and engine condition normally okay because on site load N/A and customer advised that this engine service due | Closed | Kapil Solanki
9 | North | 211634598 | 23-01-2025 14:10 | 250 | F6.8841.../2320021 | Maintenance Due Alarm Call By Customer Name :- Nasim ... Mobile No :-8178330262 | Closed | ASJK. corporate Service Pvt. Ltd. | 527.43 | Radiator chock internally & Customer open the urea tank cap because it is dusty area service due Quatation sent to the customer for service | Closed | Kapil Solanki
10 | North | 211634587 | 23-01-2025 14:03 | 125 | F6.9840.../2420020 | Red Lamp On Alarm And Tripping Issue Call By Customer Name :- Nitesh Sharma Mobile No :- 9717878570 | Task Start | B Continental Hotel |  | Update pending | OPEN | Kapil Solanki
11 | North | 211634454 | 23-01-2025 13:30 | 320 | F6.8802.../2420215 | KRM issue | Task Start | IMPACT MACHINE TOOLS | 25 | Engine RPM is not show on the customer mobile after contact with KRM helpdesk then now Dg always show ON the condition, may be required sim change because network issue- UNDER OBSERVATION | OPEN | Kapil Solanki | krm cHECK
12 | North | 211634331 | 23-01-2025 13:01 | 40 | 3H.8951.../2420491 | DG to Delta SPS Automation. | Open | ATC Telecom Infrastructure Private Limited | 6.35 | Under Cancellation- | Cancelled | Kapil Solanki
13 | North | 211634321 | 23-01-2025 12:54 | 40 | 3H.8951.../2421185 | Starting/Stopping Issue | Closed | Axis Bank Ltd | 1.58 | Emergency button was pressed released the same | Closed | Kapil Solanki
14 | North | 211634320 | 23-01-2025 12:54 | 625 | DV0.8501.C4../2420158 | ECU Alarm Issue Call By Customer Name - Vijay Singh Number - 9631858684 | Task Start | Radikale Engineering Pvt. Ltd.. | 23.33 | ECU & DCU Flash After that issue resolve | Closed | Kapil Solanki | Dosing Module Issue
15 | North | 211633963 | 23-01-2025 12:11 | 25 | GP3.8702.../2420903 | Starting issue Call by Customer Name :Ganpat Singh No : 7792801856 | Closed | NAGANARAY CONSTRUCTION CO | 26 | Found Controller ON/OFF switch wire loose tightness the same issue resolve | Closed | Gourav Sharma
16 | North | 211633901 | 23-01-2025 12:02 | 57 | T4.8941.../2320066 | Load Issue Call by customer Name:- Amit Sharma No:- 9873644503 | Closed | Mercury Investments Ltd. | 97 | Customer side panel issue | Closed | Kapil Solanki
17 | North | 211633417 | 23-01-2025 10:31 | 58.5 | T4.8941.../2420922 | Starting issue Call By Customer Name :- Mahesh Chand Mobile No :- 9816035098 | Closed | MILLENIUM EMBROIDERY | 98 | Check & found no any alarm in DM1 & 2 then check in Event log found Charge fail when check the charging alternator then found WL point clip was disconnected, Connect the wire the issue resolve | Closed | Kapil Solanki
18 | North | 211633405 | 23-01-2025 10:23 | 125.4 | 4H.8041.../2420705 | Door Issue & Low Urea Level Call By Customer Name :- Gagan Mobile No :-8273823676 | Closed | ZEUSIP ADVOCATES LLP | 105 | Canopy door lock adjust & top up the def | Closed | Kapil Solanki
19 | North | 211633171 | 23-01-2025 09:18 | 82.5 | 5H.8901.../2420389 | Stopping Issue Call By Customer Name :-Jai Deep Mobile No :- 9873906425 | Closed | Suruchi Apparments | 3 | Customer side panel issue Dg stopping time 5 min from customer panel | Closed | Kapil Solanki
20 | North | 211631134 | 22-01-2025 16:01 | 30 | 3H.8902.../2420262 | Starting Issue Call By Customer Name :- Lal Singh Mobile No :-7827447526 | Closed | Mrs. Simran Pal | 10 | Found battery charger faulty replace the same issue resolve | Closed | Kapil Solanki
21 | North | 211630744 | 22-01-2025 14:14 | 125.4 | 4H.8042.C4../2420462 | Abnormal sound and Canopy door Issue Call by Customer Name : Kachan mishra No : 8130780192 | Closed | IMPACTQA SERVICES [P] LTD | 3.4 | Wrong Report- No abnormal Sound found in DG | Closed | Kapil Solanki
22 | North | 211636676 | 23-01-2025 18:18 | 10 | GP3.8301.../2420250 | door lock problem | Task Start | Mahadev Enterprises. . | 37.93 | Door Lock Issue , same fixed with the help of hinge & resolve the Issue | Closed | Ved Prakash Gupta
23 | North | 211636228 | 23-01-2025 16:52 | 200 | 6H.8435.../2420032 | Genset Trip | Task Start | Dr. Meenu Bansal |  | Under Cancellation-Same rectified on call | Cancelled | Ved Prakash Gupta
24 | North | 211635021 | 23-01-2025 15:48 | 58.5 | T4.8941.../2423328 | Automation Issue Call By Customer Name :- Surender Mobile No :- 9896315544 | Open | Shivaay Printers | 11.2 | Auto-Starting issue found due to 11 no. wire found loose on distribution box,re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
25 | North | 211633263 | 23-01-2025 09:48 | 200 | 6H.8435.../2420191 | Starting Issue Call By Customer Name :- Rajiv Singh Mobile No :-8708726681 | Closed | Kaveri Foods | 30 | Starting issue due to battery voltage found low(6.1 V),Battery was not connected to Charger,connected same on Float battery & sent DG Battery for charging | Closed | Ved Prakash Gupta
26 | North | 211633229 | 23-01-2025 09:41 | 30 | 3H.8902.../2420923 | Dg issue | Closed | Axis Bank Ltd | 46 | Customer Complaint as starting issue but no such issue observed on site , Fuel Level was found Low(Less than 10%) No any code found in DM1 or DM2 | Closed | Ved Prakash Gupta
27 | North | 211632477 | 22-01-2025 19:01 | 250 | F6.8841.../2420138 | Starting Issue Email By Customer Name:- Vikas | Closed | Vikas Stainless Pvt. Ltd. | 110 | SPN/FMI-1761/16 ,AdBlue Level Low & Radiator found Choked ,Top-up the DEF & Clean the Radiator ; Recommanded to shift the DG from this site | Closed | Ved Prakash Gupta
28 | North | 211630882 | 22-01-2025 14:53 | 15 | GP3.8501.../2420585 | Starting Issue Call By Customer Name :- Navjout Kaur Mobile No :-7999999316 | Closed | I. S. Trading C/o. | 34.1 | Controller theft ;same replaced on Paid basis | Closed | Ved Prakash Gupta
29 | North | 211630823 | 22-01-2025 14:34 | 250 | F6.8841.../2420005 | Leakage issue | Closed | Prime Industries | 163 | Fuel Leakage found from HP Pipe from FIP to Common Rail on Common Rail ; Tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | Service History
1 | East | 211634508 | 23-01-2025 13:36 | 500 | DV8.8501.C4../2320004 | * Starting Issue Call By Customer Name :- Nitesh Kumar No :- 9572166785 | Task Start | Indian Potash Limited | 154 | This is an previous case - starter motor was defective and was under EDO, for reinstallation SR opened | OPEN | Prabhakar Kumar
2 | East | 211633155 | 23-01-2025 09:12 | 320 | F6.8802.../2420204 | Trip_Genset_Low_Voltage | Open | Biju Kaumbang |  | visit pending | OPEN | Ujjwal Das
3 | East | 211632447 | 22-01-2025 18:41 | 20 | GP3.8601.../2421228 | Under Speed Alarm Issue Call By Customer Name - Aayush Number - 9570302828 | Task Start | Shakuntala Mart | 25 | DG was not starting due to the emergency alarm so on call resolved issue by giving direct -tive supply to emergency Switch, to restore issue as customer demand was to give instant solution. SE will visit tomorrow . | OPEN | Prabhakar Kumar
4 | East | 211632234 | 22-01-2025 17:47 | 250 | F6.8841.../2420383 | Black Smoke Issue Call By Customer Name :- Ajit Mobile No :-8271064990 | Task Start | Mithila Earthing Solutions | 3.54 | Error code issue showing ECU internal fault with SPN-516166 FMI-0 was showing engineer visit the site reset the alarm issue resolved . | CLOSED | Prabhakar Kumar
5 | East | 211630341 | 22-01-2025 12:29 | 40 | 3H.8951.../2420759 | Starting/Stopping Issue | Task Start | Amvisha Real Estate Developers Pvt. Ltd. | 19 | DG was not starting due to low voltage so put the Battery on charge but not get charge, and so need to replaced the battery | OPEN | Prabhakar Kumar
6 | East | 211619561 | 18-01-2025 17:08 | 45 | 3H.8951.../2421369 | Diesel Leakage Issue Call By KGD Name :- Komkom Neha Mobile No :- 9234456624 | Open | K. L. Bhasin & C/o. Petrol Pump. | 82 | SE found the silencer broken at welding so by welding restored the issue. There was no hunting or vibration on DG also found foundation was also per guidelines, the radiator was also found repaired by any adhesive material before commisioning . | CLOSED | Prabhakar Kumar
7 | East | 211630774 | 22-01-2025 14:27 | 25 | GP3.8702.../2420145 | Tripping Issue Call By Service Dealer Name :- Rajesh Kumar Mobile No :-9229206575 | Closed | Baijnath Kumar | 53 | Found exhaust expansion below damage need to replace | CLOSED | Prabhakar Kumar
8 | East | 211633300 | 23-01-2025 10:00 | 20 | GP3.8601.../2420685 | Shut down alarm issue Call By Customer Name :- Akhilesh Prasad Mobile No :-9778074795 | Closed | VEERMAN ENTERPRISES | 35 | Found Emergency switch on, Operator was not avialable on site so customer had open the SR | CLOSED | Ujjwal Das
9 | East | 211632479 | 22-01-2025 19:04 | 15 | GP3.8501.../2421431 | Starting Issue Call By Customer Name :- Vijay Number :- 8172068268 | Closed | PURBASHA SAHA | 43 | SE found DG not start due to fuel level low after top up the fuel level,DG running ok | CLOSED | Prosanjit saha
10 | East | 211630758 | 22-01-2025 14:21 | 160 | 6H.8475.../2420276 | Automation Issue | Task Start | Energito Electricals Pvt. Ltd. | 64 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Prosanjit saha
1 | West | 211631188 | 22-01-2025 16:10 | 58.5 | T4.8941.../2422942 | Engine not starting | Task Start | Roongta Group Builders & Developers | 1 | SPN/FMI- 97/5 (Water in fuel_ self test) Checked the panel wiring found ok. According to the SD engineer, the genset is starting after overriding the controller and pressing the start button. Today the SD engineer will go to the site with the water separator filter. | OPEN
2 | West | 211630985 | 22-01-2025 15:25 | 30 | 3H.8902.../2420560 | Automation Issue Call By Customer Name :- Nitin Chandra Mobile No :-9011496463 | Closed | Vimaakr House | 52.28 | Complaint received from customer that the controller is automatically switching from auto mode to manual mode. But when the engineer visited the spot, no problem was found there | CLOSED
3 | West | 211630950 | 22-01-2025 15:15 | 58.5 | T4.8941.../2420788 | Starting Issue Call By Customer Name :- Yagnik Parmar Mobile No :-9904654660 | Open | BND TECHNOLOGIES PRIVATE LIMITED | 22 | Allarm-Fail to start So tightened all the wire connections in the panel and connected the iKonnect tool and made the PRV count from 2 to 0. This case Is under observation. | CLOSED
4 | West | 211630835 | 22-01-2025 14:50 | 20 | GP3.8601.../2420718 | red lamp alarm & Tripping issue Call By Customer Name :- RAJU KOLIKOLI Mobile No :- 9619737924 | Task Start | A. Shashi Enterprises | 439 | Alarm- Canopy emergency alarm So tightened the 11 number wire and issue resolved. | CLOSED
5 | West | 211630784 | 22-01-2025 14:24 | 750 | DV2.8501.C4../2420057 | Voltage Fluctuation | Completed | Nyati Hotels & Resorts Pvt. Ltd. | 24 | Low DEF level The genset was synced properly but during biasing the genset was hunting so we are arranging the potentiometer. | CLOSED
6 | West | 211629364 | 22-01-2025 09:23 | 0 | 4H.8042.C4../2420868 | Alternator Voltage not build up | Task Start | JAKSON & COMPANY | LR | The alternator was not buildup voltage because the AVR wire was cut. | CLOSED | Details Required | GOEM ISSUES
7 | West | 211624041 | 20-01-2025 17:31 | 58.5 | T4.8941.../2422831 | DISPLAY ISSUE | Task Start | Goel Power Engineers | LR | Display was not showing so EDO placed for the controller. | OPEN |  | GOEM ISSUES
8 | West | 211622127 | 20-01-2025 11:21 | 20 | GP3.8601.../2420180 | Exhaust Lineage issue in manifold.. | Task Start | Goel Power Engineers | LR | Exhaust manifold was broken so replaced it. | CLOSED |  | GOEM ISSUES
1 | South | 211629593 | 22-01-2025 10:33 | 25 | GP3.8702.../2420157 | Battery Charging issue Call By Customer Name :- Vijay Mobile No :- 8499904581 | Open | HATSUN AGRO PRODUCT LIMITED. | 17.42 | Battery voltage low | Closed | Mr. MD Saleem
2 | South | 211629396 | 22-01-2025 09:50 | 20 | GP3.8601.../2420141 | Coolant water Low Problem Call by : Customer Name :Mathew Varghese Contact :9539800961 | Open | MUNDAKAPADAM MANDIRAM HOSPITAL | 49 | Cooltant leakage from | Closed | Mr. NandhaGopal
3 | South | 211628680 | 21-01-2025 20:10 | 20 | GP3.8601.../2421153 | Red lamp issue Called by customer Name ; Rahul Number9020780320 | Open | Ananda fuels | 69 | SE visited the side no issue found so checked the event log found EGR (2791/5) open load error code so checked the connector found ok. Run the engine for 2,3 times no issue found. | Closed | Mr. Sanjaimon S | ECU fault
4 | South | 211628396 | 21-01-2025 18:52 | 20 | GP3.8601.../2421692 | Starting Issue Call By Customer Name :- Shijesh .. Number :- 8123871790 | Task Start | M/s. PARASSINI BAKERS | 36 | Visited the site checked and found diesel mix with the engine oil sump, further we are checked toughly fuel line system, and we can t get clue from engine side, so finally we are removed mixed oil and replaced the new oil and kept few days under observation. Customer paid for it. | Closed | Mr. Anil Kumar H G
5 | South | 211628371 | 21-01-2025 18:28 | 82.5 | 5H.8901.../2420274 | AMF panel issue Call by : Customer Name : Subash Contact : 9159759555 | Task Start | Rapiscan Systems Pvt Ltd | 13.37 | Visit the side check the complind engine not taken load check the load customer using three phasee induction motor starting current (97) AMS Turing kick load customer in fire pump panel tripping customer using over load finnaly auto sensing eb line connect to battery charger working. Customer side issue | closed | Mr. NandhaGopal
6 | South | 211628215 | 21-01-2025 17:45 | 58.5 | T4.8941.../2420277 | Starting Issue Call By Customer Name :- Ravi .. Mobile No :-9345512752 | Closed | Sri Gurusaraswathi Mills | 155 | All wiring checked control on/ off switch loose condition so controller sometime not proper working after wire very tight and engine controller output voltage sensing wiring disconnect so engine no output engine off condition. after wiring full tight checked. engine start performance found ok. running condition normal. engine oil condition bad so new oil and oil filter diesel filter changed. air filter clean it.v belt tension ok. all hose and all wiring tight checked ok. radiator coolant top-up. battery distill water level checked ok | Closed | Mr. NandhaGopal
7 | South | 211627876 | 21-01-2025 16:34 | 125.4 | 4H.8042.C4../2420837 | Error code problem Call by : Customer Name :Jaya Kumar Contact :9790015256 | Closed | MODERN MATCHES PRIVATE LIMITED | 27 | 1761/16 Adblue low top the same | Closed | Mr. NandhaGopal
8 | South | 211626978 | 21-01-2025 15:49 | 20 | GP3.8601.../2421535 | Starting Issue Email by OEM Name - J.Jayapriya | Task Start | Srimanthany Janakiraman | 4 | Visit the site for earth leakage in main alternator body issue & checked alternator winding connection found normal.Meggering done for main stator & Excitor stator found 500mega ohm's.Dg Starter the generator run with load checked the generator body found no earth leakage in the canopy body. Checked the engine oil & coolant level found normal checked the fan belt tightness found normal checked the other perimeters found normal. | Closed | Mr. NandhaGopal
9 | South | 211626698 | 21-01-2025 14:56 | 15 | GP3.8501.../2422165 | OIL PRESURE SWITCH FAILURE | Closed | SUNBEAM GENERATORS PVT LTD | LR | Attended the above site for oil pressure switch failure complaint.Inspected the generator and start the generator but not get start and LOP open fault and engine speed sensor erratic fault enabled.Checked the oil pressure switch continuity,no continuity found,then checked the new oil pressure switch continuity found normal,so removed the faulted oil pressure switch and replaced new oil pressure switch.Then start the generator get started and reset the faults.Generator all parameters are found within the limit. | Closed | Mr. NandhaGopal
10 | South | 211626714 | 21-01-2025 14:55 | 320 | F6.8802.../2420089 | Alarm Issue Call By Customer Name - Mr. PRADEEP Number - 7569034019 | Closed | Heavenly Hills Resorts LLP. | 112 | 3031/14 ,1761/16 so topup def after start and running ok | Closed | Mr. Anil Kumar H G | ECU fault check
11 | South | 211626343 | 21-01-2025 13:35 | 20 | GP3.8601.../2420476 | Starting Problem Call by : Customer Name :Zohib Contact :9845109364 | Closed | ZOHAIB AHMED | 3.47 | carried out of visited the site and check the problem and problem is dg over speed alarm. And clear the error and rest the controller panel and clear the issue and started the engine running condition ok. | Closed | Mr. Anil Kumar H G
12 | South | 211626257 | 21-01-2025 13:20 | 82.5 | 5H.8901.../2420502 | AMF Panel Problem & Fuel tank tap problem Call by : Customer Name : Alex Contact : 7305054611 | Task Start | Metro Trading Company | 47 | Visited the site above customer complaint for engine not start in auto mode check the engine eb side issue. so engine not starting, Correct the eb check the auto mode properly start and stop. checked all parameters working normal | Closed | Mr. NandhaGopal
13 | South | 211626049 | 21-01-2025 12:31 | 25 | GP3.8702.../2420507 | DG not starting,DG not working -504175 | Closed | ICICI Bank Limited | 9 | Reached site checked dg then.checked battery found the battery positive connection luse.and fitted the connection and checked the battery voltage found ok.then checked the connections found ok . started the dg in manual & checked the parameters.all are up to limit.done load test also.run the dg with load for 45 minutes.all parameters were upto limit.no faults detected. | Closed | Mr. NandhaGopal
14 | South | 211626040 | 21-01-2025 12:29 | 200 | 6H.8435.../2420223 | Starting/Stopping Issue | Closed | JOYALUKKAS INDIA LIMITED | 217 | Visited the site & check the engine condition, v belt tension, radiator fan guard, radiator guard vibration & retight the radiator guard & adjusted the v belt tension & engine started tested found ok. | Closed | Mr. Anil Kumar H G
15 | South | 211625981 | 21-01-2025 12:17 | 15 | GP3.8501.../2420118 | Inspection/Maintenance | Cancelled | Sri Shanmukhi Tradeers. | NA | Cancelled | Cancelled | Mr. MD Saleem
16 | South | 211625831 | 21-01-2025 11:49 | 15 | GP3.8501.../2420395 | AMF PELNAL Maintenance Due | Closed | HI Tech UPS | 50 | visit the site check the maintenance due so not sense in auto modo so hours is extended so check in auto mode so start the dg working good in load condition | Closed | Mr. Anil Kumar H G
17 | South | 211625748 | 21-01-2025 11:30 | 15 | GP3.8501.../2421410 | dg machine is not working properly | Closed | ICICI Bank | 2.1 | As per the customer control on/off switch was in on condition but display was not on. But at during the site visit dg display was on and observed error code 2802/4 which is low battery voltage. So checked battery voltage, battery charger. And condition are good. Terminals lugs of the battery are tight. So tightned all connections in the control panel wirings , controller + and -ve ,stater wirings ,ecu clips and all other clips . Then alarm cleared and tested. No errors now. Dg is running normally. Educated customer. and dg is kept under observation. | Closed | Mr. Sanjaimon S
18 | South | 211625613 | 21-01-2025 11:05 | 125.4 | 4H.8041.../2420756 | Starting/Stopping Issue | Closed | T. N. R. Constructions. | 17 | Battery discharge. So remove the recharged the battery | Closed | Mr. MD Saleem
19 | South | 211625413 | 21-01-2025 10:23 | 200 | 6H.9052.../2300008 | Automatically Switch off & Coolant Temperature High Call by : Customer Name :Chandra Mohan Contact :7339651390 | Closed | CDR & CO CONSTRUCTIONS | 887 | 110/0 check the engine lubrication oil level and conditions found ok . check the coolant level done. check the v belt tightness done check all radiator fan dust forming clean the radiator fan done. use the air done engine high temperature complaint solved start the engine with running few minutes | Closed | Mr. NandhaGopal
20 | South | 211625296 | 21-01-2025 09:58 | 250 | F6.8841.../2420339 | Diesel Leakage Problem Call by : Dealer Name :Kirshana kumar Contact :9500927427 | Closed | Montfort School C. B. S. E. | 33 | Checked Found Coolant Leakage From Radiator Bottom Hose Clip Side So Tightened then Leakage Arrested and Urea Level Low Warning Due to DEF Level Below 50%, DEF 20 Lts Tapped Level Found ok, Radiator Coolant Level Low As Per Kirloskar AO Instruction Coolant 2 Lts Tapped Then Level Found ok, All Hoses and Clips Tightened, All Wire Connection Tightened, Started the Engine Running Performance ok, Output Voltage Normal, Safety Checking and Load on Checked ok, No Leakage Engine Running Performance o | Closed | Mr. NandhaGopal
21 | South | 211625263 | 21-01-2025 09:47 | 25 | GP3.8702.../2420678 | Starting issue Call By Customer Name :- Dakshan Mobile No :-9380415254 | Closed | Mr. Ashrit Kishan | 223 | Showning Maintainace due alarm clear the Same | Closed | Mr. NandhaGopal
22 | South | 211624423 | 20-01-2025 19:25 | 20 | GP3.8601.../2420859 | Maintanance due alarm issue Called by customer Name ;Vishnu Number: 8088141299 | Closed | Shree Rajarajeshwari Fuel Hub | 72 | Observed the display SPN 190 & FMI 8 ( ENGINE SPEED SENSOR ERRATIC) so remove the MPU sensor and again refited found ok. | Closed | Mr. Anil Kumar H G
23 | South | 211624394 | 20-01-2025 19:02 | 125.4 | 4H.8042.C4../2420125 | Display problem And Battery problem Call by : Customer Name :Kannan Contact :7994252458 | Closed | NEW ALANKAR HYPER MARKET | 47 | under voltage shown in display. So checked AVR found fuse have failure so replaced fuse. Issued resolved | Closed | Mr. NandhaGopal
24 | South | 211624159 | 20-01-2025 17:52 | 125.4 | 4H.8042.C4../2420605 | AMF panel problem Call by : Customer Name : Ambika Contact : 9611258636 | Closed | INDIQUBE SPACES PRIVATE LIMITED | 1.3 | Visited the site and check the engine condition, check the EB sensing cable connections, connect the EB sensing cable connections & engine started tested found ok. | Closed | Mr. Anil Kumar H G
25 | South | 211624011 | 20-01-2025 17:32 | 15 | GP3.8501.../2421102 | Hunting Issue. Call By Customer. Name:- Prashant . Mobile No.:- 9148820253 | Task Start | PRASHANTH | 0 | Customer not allowed | 0 | Mr. Anil Kumar H G
26 | South | 211623859 | 20-01-2025 16:58 | 25 | GP3.8702.../2421579 | Starting/Stopping Issue | Closed | Vortex Fuels | 3 | 516166/0 ECU Malfunctioning issue. Connect i connected Tool and Flashes ECU and Engine controller . | Closed | Mr. Sanjaimon S | ECU fault
27 | South | 211623830 | 20-01-2025 16:52 | 250 | F6.8841.../2420253 | Error Code Issue & Preventive Maintenance Call By Customer Name - Ashraf .. Number - 9742006966 | Open | Ceerah | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G
28 | South | 211623668 | 20-01-2025 16:40 | 320 | F6.9051.../2420003 | Abnormal sound problem Call by : Customer Name : Vinay Contact : 8686227178 | Closed | KASAM INDUSTRIES | 28 | Adblue low top - up the Same | Closed | Mr. MD Saleem
29 | South | 211623578 | 20-01-2025 16:18 | 30 | 3H.8902.../2420726 | Tripping issue Call By Customer Name :- Eric Alan Mobile No :- 9844116110 | Closed | Mr. Eric Alan Pais | 37 | under speed alram showing. RYB Fuse wire connection loose. Thighten the Same. | Closed | Mr. Anil Kumar H G
30 | South | 211623569 | 20-01-2025 16:14 | 82.5 | 5H.8901.../2420463 | Power supply problem Call by : Customer Name :Veerababhu Contact :8122526734 | Closed | Sree Gupta Bhavan PVT LTD | 41.2 | DURING INSPECTION FOUND BODY EARTH CABLE IN MELTED CONDITION.UNDERSTOOD FROM THE CUSTOMER THAT THEY HAVE OBSERVED SMOKE ON LOAD CONDITION.CHECKED THE WIRINGS FOUND AUTO SENSING CABLE (6 CORES) IN SHORT CONDITION.WHICH IS NEAR TO EARTH CABLE. REMOVED THE MELTED AND DAMAGED CONNECTIONS FOR TESTING PURPOSE.TESTED THE DG SET WITH LOAD (MANUAL MODE).FOUND THE DG PERFORMANCE SATISFACTORY.ADVISED THE CUSTOMER TO MADE SEPERATE CONNECTIONS FOR AUTO MODE OPERATION AND NOT TO RUN THE DG SET UNBALANCE LOAD TO AVOID POSSIBLE DAMAGES TO THE DG SET. | closed | Mr. NandhaGopal
31 | South | 211622819 | 20-01-2025 14:10 | 30 | 3H.8902.../2421036 | Starting issue Call by customer Name: k Perumal Number:8939541036 | Closed | Sia Carriers LLP... | 2.5 | Noticed the engine conopy emergency button wire connection was in lose connection after reconnect the wire connection check ok all parameter found ok | Closed | Mr. NandhaGopal
32 | South | 211622657 | 20-01-2025 13:19 | 160 | 6H.8475.../2420129 | Coolant Leakage issue Call By Customer Name :- Rashid Mobile No :- 9739101745 | Closed | S R N Mehta School | 74 | visit site coolant leakage in house pipe replace clamps found ok taken load trail okay photo attached | Closed | Mr. Anil Kumar H G | GOEM issue
33 | South | 211622246 | 20-01-2025 11:51 | 25 | GP3.8702.../2421176 | Starting/Stopping Issue | Task Start | Flash Generator Hires | 272 | visited the site, checked everything systemwise found protect lamp on alarm indicating , so checked the DTC , found 100/1, low oil pressure fault . checked oil level , very low so topped up the oil 3.5 litre.found oil leakages from oil drain valve coupling copper washer side, oil dipstic ferrule side due to wrong positioning , & turbo drain hose side . all leakages cleared . also DTC cleared . started the engine found performance ok | Closed | Mr. NandhaGopal
34 | South | 211622232 | 20-01-2025 11:41 | 125.4 | 4H.8042.C4../2420418 | Leakage Issue | Task Start | Raravies Restaurant | 3 | Attended the site check the engine oil, oil filter, diesel filter, Air filter, fan belt, radiator water battery charge and water, fuel lines, return line leake crimping side,need to replace fuel line Photo attached | Closed | Mr. Sanjaimon S | GOEM issue
35 | South | 211633434 | 23-01-2025 10:34 | 40 | 3H.8951.../2420234 | Starting Problem Call by : Dealer Name : Priya Contact : 9892952105 Customer name : Sai contact number: 7305994365 | Task Start | Amaze Travels Private Limited. | 19 | Visited the site attend the dg set, Checked the dg starting system not cranking,due to control panel end battery charger input AC supply fuse to charger wire rat biting,so short to control panel body,so battery charger failure so reverse supply comming,so DC mcb tripping so not started the dg set,so disconnect the battery charger input supply,after on the dc mcb,after started the dg set started and running condition dg parameters satisfied found ok. | closed | Mr. NandhaGopal
36 | South | 211633364 | 23-01-2025 10:18 | 40 | 3H.8951.../2420887 | Starting issue Call By Customer Name :- Gopal Mobile No :- 7349379373 | Task Start | K. N. N. D. Associates Private Limited. . | 22 | DG not running in show on display Y Phase fuse (under speed) issues at clear the fault then after started the engine manual running with load voltage found ok | Closed | Mr. Anil Kumar H G
37 | South | 211633309 | 23-01-2025 10:03 | 500 | DV8.8501.C4../2420165 | Amber Lamp Issue Call By Customer Name :- Rajesh . No :- 9710281300 | Task Start | VELS | 48 | Adblue low top up the same. | closed | Mr. NandhaGopal
38 | South | 211633288 | 23-01-2025 10:00 | 125.4 | 4H.8042.C4../2420418 | Fuel Leakage Problem Call by : Customer Name :Junaid Contact :9846914962 | Task Start | Raravies Restaurant | 4 | Attended the site check the engine, then remove the broken fuel return pipe, then fitted new fuel return pipe, then start the engine, Engine working found ok | Closed | Mr. Sanjaimon S
39 | South | 211633168 | 23-01-2025 09:13 | 15 | GP3.8501.../2420275 | Starting Problem Call by : Customer Name :Ramkumar Contact :9787010492 | Task Start | KRISHH PACKAGING | 59 | Red lamp alarm shown in display and SE found Emergency push button pressed condition. So release emergency button to clear to alarm, now engine running ok. Educate customer for this. | Closed | Mr. NandhaGopal
40 | South | 211633003 | 23-01-2025 05:51 | 125.4 | 4H.8041.../2420494 | Starting Issue Call By Customer Name :- Venkat Raju No :- 9434262977 | Open | R. K. E. C. Projects Limited | NA | Visit pending | Open | Mr. NandhaGopal
41 | South | 211631266 | 22-01-2025 16:24 | 58.5 | T4.8941.../2422609 | AMF Panel Problem Call by : Customer Name :Prbagaran Contact :8012634533 | Cancelled | JAYALAKSHMI MEDICALS | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal
42 | South | 211631193 | 22-01-2025 16:12 | 40 | 3H.8951.../2420744 | Over heat & AMF panel problem Call by : Customer Name : Amith Reddy Contact : 9611199934 | Closed | Amith R | 25.58 | Emergency stop push button connctor loss | Closed | Mr. Anil Kumar H G
43 | South | 211631040 | 22-01-2025 15:33 | 82.5 | 5H.8901.../2420755 | Starting/Stopping Issue | Task Start | PRESTIGE ESTATES PROJECTS LIMITED | 3 | Visit the site check the auto not starting due to the r phase fuse fault replace the new fuse and check running found ok in auto mode check running found ok check the all parameters working engine running found ok | Closed | Mr. Anil Kumar H G
44 | South | 211630650 | 22-01-2025 13:46 | 125.4 | 4H.8042.C4../2420190 | Engine not starting-starting problem | Closed | Maharishi Vidya Mandir (CBSE) School, | 15 | Inspected the site and noticed engine not starting at first crank , noticed engine pre heat time adjusted at controller program at 8 sec to 12 sec then the first time start issue resolved so far we have an dg under observation for further 1 week of operation | Closed | Mr. NandhaGopal
45 | South | 211630606 | 22-01-2025 13:36 | 40 | 3H.8951.../2420879 | Starting/Stopping Issue | Closed | NF POWERTECH ENGINEERS | 51 | 157/14 ECU PRV count kept 0 . And ECU flashing done started the dg running normally and noted the parameters. | Closed | Mr. Anil Kumar H G | KRM check
46 | South | 211630581 | 22-01-2025 13:25 | 40 | 3H.8951.../2421253 | Electrical Problems | Closed | Axis Bank Ltd | 0 | Found Emergency button pressed, So engine not starting educated the customer. | 0 | Mr. NandhaGopal
47 | South | 211630116 | 22-01-2025 11:41 | 58.5 | T4.8941.../2423150 | NCD LAMP GLOW AND D.G TRIP | Closed | Raghamantra Jewellery | 1.1 | 2791/18 Fault cleared with respective tool. Flashing done. Now d.g working fine | Closed | Mr. NandhaGopal
48 | South | 211641137 | 25-01-2025 08:06 | 125.4 | 4H.8041.../2420794 | Starting/Stopping Issue | Open | R. Chitta. | 4 | WEAK BATTERY | Closed
49 | South | 211641085 | 24-01-2025 20:51 | 20 | GP3.8601.../2421335 | Trip_Genset_Low_Voltage | Open | B.G.NAIDU SWEETS PRIVATE LIMITED | Cancelled | Cancelled | Cancelled
50 | South | 211640937 | 24-01-2025 18:37 | 0 | 5H.5351.../2520053 | ECU FLASHING | Task Start | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
51 | South | 211640930 | 24-01-2025 18:33 | 0 | 5H.5351.../2520057 | ECU FLASHING | Task Start | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
52 | South | 211640913 | 24-01-2025 18:18 | 0 | 5H.5351.../2520013 | ECU FLASHING | Task Start | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
53 | South | 211639369 | 24-01-2025 15:30 | 30 | 3H.8902.../2420103 | AMF Panel Problem Call by : KGD Name : Ananth Reddy Contact : 9866224148 Dealer number : 9848025681 | Task Start | Ananth Mourya Enterprises | 67.5 | Air lock issue from Suction side | Closed
54 | South | 211639272 | 24-01-2025 15:03 | 20 | GP3.8601.../2420419 | Starting/Stopping Issue | Closed | Karnataka Fuel Station. | 348 | Visited site, carried out daily checks as per complaint observed the problem and found engine tripping with Speed sensor fault so checked all Parameters found speed NOX 5714 sensor wire K4 loosed condition, corrected the problem and after that started the engine observed engine running condition normal. | Closed
55 | South | 211639194 | 24-01-2025 14:47 | 0 | 5H.5351.../2520016 | ECU FLASH AND REGNERATIO TEST | Closed | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
56 | South | 211638978 | 24-01-2025 14:00 | 40 | 3H.8951.../2420427 | DG Not Switching on in Automode | Task Start | Bharti Airtel ANG | 85 | Visit the site checked the generator found engine not starting in Auto mode checked the KOEL AMF PANEL found negative sensing relay internal fault and removed the defective relay replace with 240VAC auto start relay and checked the dg parameters found normal started the generator run with load found normal. | Closed
57 | South | 211638869 | 24-01-2025 13:35 | 30 | 3H.8902.../2420020 | Starting/Stopping Issue | Closed | Kancherla Surya Prakash Educational Society. | 97 | Engine not starting due to fuse burn (y-phase). | Closed
58 | South | 211638818 | 24-01-2025 13:30 | 0 | 5H.5351.../2520001 | ECU FLASH AND REGENERATION TEST | Closed | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
59 | South | 211638808 | 24-01-2025 13:23 | 0 | 5H.5351.../2520019 | ECU FLASH AND RENERATION TEST | Closed | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
60 | South | 211638772 | 24-01-2025 13:10 | 40 | 3H.8951.../2420443 | DG not getting ON. Battery is not charging. | Closed | EBO MART PRIVATE LIMITED | 34.1 | Found Battery dead due to battery charger input supply is not coming | Closed
61 | South | 211638639 | 24-01-2025 12:46 | 0 | 5H.5351.../2520025 | ECU FLASH AND REGENERATION TEST | Closed | AJAX ENGINEERING PRIVATE LIMITED | 0 | Campaigning SR for REGENERATION TEST | 0
62 | South | 211638147 | 24-01-2025 11:14 | 0 | 6H.8435.../2420192 | STARTER MOTOR TERMINAL ISSUE | Task Start | SUNBEAM GENERATORS PVT LTD | LR | Starter moter side sparking occur so checked and found 3no wire damaged. | Closed
63 | South | 211638113 | 24-01-2025 11:06 | 0 | GP3.8501.../2422166 | CONTROLLER UP ARROW BUTTON NOT WORKING | Task Start | SUNBEAM GENERATORS PVT LTD | LR | CONTROLLER UP ARROW BUTTON NOT WORKING | Closed
64 | South | 211638089 | 24-01-2025 11:05 | 58.5 | T4.8941.../2421400 | Fuel Sensor Issue Call By Customer Name - Arjun .. Number - 8123385280 | Task Start | Sri Gavisiddheshwara Samsthan Sri Gavimath | 54 | attend the site check the oil and coolant leval found ok starting the engine check the fuel sensor not working properly remove the fuel sensor check the in manual and check the negative sensing in battery not working properly. (update pending) | Closed
65 | South | 211637954 | 24-01-2025 10:45 | 0 | 5H.5106.../2420001 | I trams installation purpose along with Koel team | Closed | Bull Machines Pvt Ltd | LR | VISITED THE SITE ALONG WITH H.O TEAM AND ASE'S AND INSTALLED THE I TRAMS AND ROUTED THE WIRING HARNESS PROPERLY AND CHECKED THE DATA ALL ARE FINE. | Closed
66 | South | 211637965 | 24-01-2025 10:41 | 58.5 | T4.8941.../2420858 | Automation Issue Call By Customer Name - Dally Thomson Mobile No -8123745155 | Closed | EKYA SCHOOL | 23 | DG not running Maine Y Phase fuse blown issue. So replaced the new fuse then after started the engine manual and auto running with load voltage found ok DG working found ok | Closed
67 | South | 211637963 | 24-01-2025 10:41 | 20 | GP3.8601.../2420062 | Starting Problem Call by : Customer Name :Senthil Contact : 9787220696 | Closed | Bobby and Boba Saloons Private Limited | 54 | Engine not start Battery distilled water is low top up the same engine running fine | Closed
68 | South | 211637914 | 24-01-2025 10:37 | 58.5 | T4.8941.../2420714 | AMF Panel Problem Call by : Customer Name :prasad Contact :9544347773 | Cancelled | THE COCONUT RESTAURANT LLP | Cancelled | AMF pannel issue. Not in our side so SR cancelled | Cancelled
69 | South | 211637913 | 24-01-2025 10:37 | 125.4 | 4H.8041.../2420572 | Alarm problem Call by : Customer Name :Thamarikannan Contact :9080194150 | Closed | I. F. F. C. O. Nanoventions Private Limited. | 14 | found ECU fault So removed and reconnecting ECU pin also used the I konnect tool clear SPN & FMI code also checked all electrical line and all connector tight checked found ok then start the engine running performance is normal with load tested ok | Closed
70 | South | 211637845 | 24-01-2025 10:20 | 5.5 | CC1.1013.../2400430 | Starting Problem Call by : Dealer Name :Govindan Contact : 9790033065 | Open | ICICI Bank | 0 | Visit pending | 0
71 | South | 211637734 | 24-01-2025 09:57 | 40 | 3H.8951.../2420091 | Starting Problem & Abnormal Sound Call by : Customer Name : Vaishnavi Contact : 9177745533 | Open | Prashinitha Rao Eraballi | 37 | Observed that under speed alarm, so checked & find out the fuel line connections loose from section pipe and leackup pipe connection, so tightneed all fuel lines and dg starting stopping found ok all parameters working ok dg running condition ok. | Closed
72 | South | 211636507 | 23-01-2025 17:46 | 20 | GP3.8601.../2420886 | Preventive Maintenance Call by : Customer Name : Avinash Contact : 9640803195 | Closed | M/s. J.N.S. Raju Constructions | 229.8 | Abnormal noise due to avm pads loose so re tightened the same. Last wet PM done on 02/12/24 after that genset run 160 hrs. started the Genset running condition is ok | Closed
73 | South | 211634976 | 23-01-2025 15:35 | 15 | GP3.8501.../2420177 | Flickering | Closed | Host Sale Tech India P. Ltd. | 14 | Minor hunting issue found so adjusted the Screw in fuel pump side. | Closed
74 | South | 211634830 | 23-01-2025 14:59 | 30 | 3H.8902.../2420407 | Genset Trip | Closed | Sans Restaurant and Cafe. | 163 | emergency switch wire lug contact loose so tightening the wire problem solving. | Closed
75 | South | 211634828 | 23-01-2025 14:58 | 250 | F6.8841.../2420275 | Starting issue Call By Customer Name :-Ranjeet Kumar Mobile No :-9738538673 | Task Start | RELIANCE PROJECTS & PROPERTY MANAGEMENT SERVICES LIMITED | 0 | Battery voltage low | 0
76 | South | 211634682 | 23-01-2025 14:22 | 15 | GP3.8501.../2420754 | Red lamp alarm problem Call by : Dealer Name : Prudhvi Contact : 9989210413 Dealer contact No: 9398413020 | Closed | SRI SAI KRISHNA FAMILY RESTAURENT | 28 | Checking the complaint red lamp alarm (E-S lock out ) alarm so remove the E-S lock out alarm found loose connection. and Maintenance due alarm open the setting remove the alarm and started the dg running condition found ok | Closed
77 | South | 211634413 | 23-01-2025 13:19 | 58.5 | T4.8941.../2421877 | Starting Issue. Call by Customer. Name:- Vinaygan No .:- 6385235499 | Closed | DEVTA GENSETS [P] LTD | 1020 | Visit the site checked the generator found tripping in under voltage checked the error in DM1 found spn-5838/2 and removed the egr cleaned the butterfly valve and refixed properly clear the error code with ikonnect tool and start the generator run with load found running normal. | closed
78 | South | 211634412 | 23-01-2025 13:19 | 250 | F6.8841.../2420235 | Coolant Leakage Problem Call by : Customer Name : Naga raj Contact : 9880429191 | Task Start | SHUBHAM THE VENUE | 72 | visited the engine as per customer complaint check and started the engine observed coolant leakage from radiator hose due to hose clamp loose so tightened the All radiator hoses clamps then started the engine observed coolant leakage problem solved but fault code showing . 516166/0 SO connected I connect tool clear fault code then started the engine 3 to 4 time observed no fault code. Photo | Closed
79 | South | 211634263 | 23-01-2025 12:46 | 25 | GP3.8702.../2420931 | Starting Issue And protect alarm issue Call By Customer Name :- Bhimraj No :- 9380033862 | Closed | Ashirwad Children Hospital. | 18 | (157/140)Connected the CPCB4 tool and adjust prv value 0, check the engine oil level and found upto the H mark, check the v belt and Air filter and found ok, check the battery electrolyte level inside the battery and found ok, check the coolant level inside the radiator and found upto the high mark, start the DG and found ok | Closed
80 | South | 211634058 | 23-01-2025 12:36 | 5 | CP1.1003.../2400015 | Exhaust fan issue Call by : Customer Name : MANIKANDAN Contact : 8870435085 | Closed | P.MANIKANDAN | 15 | Found alternator Rotor fan damaged, due to alternator mounting bad cut, As per koel AO instructions,so the new alternator mounting bad and rotor fan changed found ok, the all bolt and nut retighten found ok, start the engine performance ok, checked out put voltage found ok, checked load testing ok, | Closed
81 | South | 211634053 | 23-01-2025 12:34 | 58.5 | T4.8941.../2421802 | Starting Issue. Call by Customer. Name:- Vinaygan .:- 6385235499 | Closed | DEVTA GENSETS [P] LTD | 1072 | Visit the site checked the generator found tripping in under voltage checked the error in DM1 found spn-5838/3 and removed the egr cleaned the butterfly valve and refixed properly clear the error code with ikonnect tool and start the generator run with load found running normal. | Closed
82 | South | 211634016 | 23-01-2025 12:22 | 58.5 | T4.8941.../2421460 | Automation issue Call By Customer Name :- Kiran Prabhu Mobile No :-9986167777 | Closed | Mr.Prashanth Narra | 3.8 | 157/14,2802/4 as per the customer complaint visit the site dg not starting.check the dg and observe the problem.the problem was pressure relief valve open fault.check the pressure relief valave connection ok.connect the tool and check dtc.it show ecu error ecu not respond.again check same problem.flash the ecu and check the dtc working.started the dg running ok.check the dg with out load and with load 20 minutes running ok.check the engine oil level ok.check the coolant level ok.check the battery destil water level ok | Closed
83 | South | 211633906 | 23-01-2025 12:04 | 45 | 3H.8951.../2421187 | MIL Lamp On Alarm | Closed | PUSHKARAM AGENCY | 99 | Customer Wants Auto Start Commissioning, DG to AMF Panel Sensing Cable Rooting Found ok, Auto Start and Battery Charger Power Connections Commissioning Done, DG Set Auto and Manual Mode Working is Good, Engine Running Performance ok, Output Voltage Normal, Safety Checking and Load on Checked ok, EB Battery Charger Working is Good. | Closed
84 | South | 211633897 | 23-01-2025 12:02 | 200 | 6H.8435.../2420063 | Abnormal Sound Problem Call by : KGD Name :Karthik Contact :7550034541 Dealer No:9442262917 | Closed | MECHO LIGHT COMPONENTS (CHENGAI) PVT LTD | 75 | Visited The above site.Radiator Belt condition found abnormal.Tight the belt, tension found ok.Engine started no abnormality found. | Closed
85 | South | 211633798 | 23-01-2025 11:45 | 30 | 3H.8902.../2421241 | AMF panel problem Call by : Customer Name :PRADEEP K M Contact :9663793637 | Task Start | PRADEEP K N | 70 | Update pending | Closed
86 | South | 211608179 | 15-01-2025 12:56 | 125.4 | 4H.8041.../2420796 | Display Issue Call By KGD Name ;- Jamuna Mob No ;- 9036094197 | Closed | Harir Yarn Industries Private Limited | 300 | visited the site carried out the daily check up and error code issue and adblue tank sensor level is low error code is 1761/14 because tripping inform the customer adblue top up required and oil service required. | Closed
87 | South | 211608042 | 15-01-2025 12:18 | 40 | 3H.8951.../2421520 | SPN 2838 FMI 1 & SPN 2791 FMI 18 | Closed | FUJI TECHNICAL SERVICES PVT. LTD. | LR | found alrm error spn 5838 FMI 1spn2791 FMI 18connect the I connect and clear the alrm , started the engine found performance ok found also oil leakage from oil filling cap found engine come without o ring pu new o ring started the engine found performance ok | Closed
88 | South | 211608020 | 15-01-2025 12:06 | 58.5 | T4.8941.../2421030 | Starting Problem Call by : Customer Name : Raju Contact : 9380955058 | Closed | KALYANI SWEETS | 68 | checked all parameters found the load issue educated to the customer about unbalanced load. | Closed
89 | South | 211607632 | 15-01-2025 10:28 | 125.4 | 4H.8042.C4../2420678 | Nox error | Closed | St. Johns Orthodox Valiyapally Vakathanam | 51 | 1761/16 Adblue level low | Closed
90 | South | 211607631 | 15-01-2025 10:27 | 40 | 3H.8951.../2420896 | Starting Problem Call by : Customer Name : Akshay Contact : 7401631554 | Closed | Axis Bank Ltd | 6 | 97/5 water in fuel alarm showing. So remove the sensor and clean the sensor after working ok. | Closed
91 | South | 211607641 | 15-01-2025 10:21 | 160 | 6H.8475.../2420063 | coolant leakage problem AND fan belt broken AND abnormal sound Call by : Customer Name :Deepak Contact :9562063263 | Closed | AYATANA HOSPITALITIES PVT LTD COORG | 437 | the engine v belt is loos so tight v belt ofter start and abnormal sound is ok and air filter clean and fitted DG running ok | Closed
92 | South | 211573274 | 2025-06-01 12:38 | 10 | GP3.8301.../2420015 | Under speed problem Call by : Customer Name : Sukumar Babu Contact : 9391035753 | Open | Mr. Sukumar | 0 | Cancelled | 0
93 | South | 211572419 | 2025-06-01 10:22 | 30 | 3H.8902.../2421321 | KRM issue | Task Start | Bhaskar associates | 0 | site visited , as per PSM and koel team instructions temporarily changed krm sim(vi). check and and found dg working parameters are krm monitoring found ok. | 0
1 | East | 211644639 | 25-01-2025 17:13 | 160 | 6H.8475.../2420151 | Starting Issue Call By Customer Name :- Prakash Sahu Mobile No :- 8128426247 | Closed | Alps Mining Services Pvt. Ltd. | 12 | SE visited site found 516166 code so cleared code by connecting Ikonnect, found no other fault code in DTC tested DG on load found ok. | CLOSED | Ujjwal Das
2 | East | 211642739 | 25-01-2025 12:16 | 30 | 3H.8902.../2420058 | Stop problem | Closed | M/s. Vasuki Nilayam. | 11 | Update Pending | CLOSED | Ujjwal Das
3 | East | 211642150 | 25-01-2025 10:32 | 20 | GP3.8601.../2420685 | Low battery voltage Alarm Issue Call By Customer Name :- Akhilesh Prasad Mobile No :-9778074795 | Closed | VEERMAN ENTERPRISES | 36 | Battery Under voltage due to battery charger loose connection after tightening the connection issue resolved. | CLOSED | Ujjwal Das
4 | East | 211641014 | 24-01-2025 19:03 | 20 | GP3.8601.../2420723 | Red Lamp On Alarm Issue Call By Customer Name - Ashish .. Number - 7477737197 | Open | Manisha Enterprise | 58 | Visit Pending | OPEN | Prosanjit saha
5 | East | 211640807 | 24-01-2025 18:00 | 58.5 | T4.8941.../2423100 | Line Rejection | Task Start | MAA BANJARI MOTORS PRIVATE LIMITED | 2 | Visit Pending | OPEN | Ujjwal Das
6 | East | 211640033 | 24-01-2025 17:24 | 5.5 | CC1.1013.../2400381 | Starting issue Call By KGD Name :- Alisha Mobile No:-9434823377 | Open | Mr. Monaj singh | 32 | Today SE will visit site | OPEN | Prosanjit saha
7 | East | 211639521 | 24-01-2025 15:54 | 625 | DV0.8501.C4../2420144 | Genset Trip | Closed | Snonwman Logistick Ltd. | 46 | DEF level was low due to which alarm popuped on display and after refilling and clearing fault code issue resolved | CLOSED | Prosanjit saha
8 | East | 211633694 | 23-01-2025 11:33 | 30 | 3H.8902.../2420172 | Starting issue Call by customer Name: Thakur . Number: 9777575588 | Task Start | Thakur Enterprises | 44 | DG was not starting showing underspeed alarm,so checked for air lock tighten all filters,adaptors and banjo bolts proper by cleanning then removed air by fuel filter and MPU connector was loose after that tighten the connector cranked DG started normally issue resolved. | CLOSED | Ujjwal Das
9 | East | 211643395 | 25-01-2025 15:10 | 10 | GP3.8301.../2420118 | Voltage Fluctuation Issue Call By OEM Name :- S.S Bharajwaj Mobile No. :- 9523150744 | Closed | Jayaswal Traders | 77 | As per complaint, Found phase to neutral voltage 215/220 then adjusted voltage and stability by AVR issue resolved. | CLOSED | Prabhakar Kumar
10 | East | 211643023 | 25-01-2025 13:17 | 125.4 | 4H.8042.C4../2420841 | Low Fuel Level Call By Customer Name :- Rajib Das Mobile No :-8638291760 | Open | National Highways Infra Projects Pvt. Ltd. | 22 | Visit Pending | OPEN | Ujjwal Das
11 | East | 211642965 | 25-01-2025 13:08 | 15 | GP3.8501.../2420815 | Coolant leakage Issue Call By Customer Name :- Chandan Kumar Mobile No :- 9334545938 | Closed | M/S RANJAN JEWELLERS | 58 | coolant leakage was due customer side mistake operator opened the radiator cap for checking coolant but was not able to close it properly so coolant was flowing out from the radiator tank. | CLOSED | Prabhakar Kumar
12 | East | 211642023 | 25-01-2025 09:53 | 125.4 | 4H.8042.C4../2420713 | FUEL LEAKAGE | Open | POOJA TRADERS | 1 | Line rejection - fuel leakage Update pendig | OPEN | Ujjwal Das
13 | East | 211640475 | 24-01-2025 17:49 | 250 | F6.8841.../2420142 | HUNTING ISSUE | Task Start | POWERLINE GREEN | 0 | Line rejection hunting issue-Engine hunting on no load condition starts after approx 1 min. rpm vairation starts from 1458 to 1515 approx. Coolant temperature-73 deg C and decreses to 71 deg C and after that RPM become stable. Exhaust outlet temperature 545 deg C and drops down to 400 deg C and variation stops. Changed ECU, Exhaust temp sensors, Boost pr sensor, Checked ITV but problem is unresolved. Taken data log and shared with Pune. No DTC found in Ikonnect | OPEN | Ujjwal Das
14 | East | 211639937 | 24-01-2025 17:09 | 40 | 3H.8951.../2421085 | AMF Panel Issue Call By KGD Name - Komkom Neha Number - 9234456624 | Open | Radheshyam Paswan. | 37 | Visit Pending | OPEN | Prabhakar Kumar
15 | East | 211639109 | 24-01-2025 14:27 | 30 | 3H.8902.../2420122 | Starting Issue. call By Customer. Name:-Dudhan Mahto Mobile No.:-9709832444 | Closed | Maria Ashram School | 100 | Mains supply was not provided to static charger and DG was not on operating condition from the last 1-2 week so battery discharged after charging the battery issue resolved | CLOSED | Prabhakar Kumar
16 | East | 211636323 | 23-01-2025 17:08 | 125.4 | 4H.8042.C4../2420957 | Tripping Issue Email By KGD Name:-rakesh koul | Closed | Vishal Mega Mart Pvt. Ltd.1 | 167 | DG fails to start showing under speed alarm so SE checked for checked electric feed pump found OK then check NRV found installed in right direction as well NRV was also OK then further check for fuel line - retighten all adapter and banjo bolt after cleaning properly then cranked issue resolved, is under observation | CLOSED | Prabhakar Kumar
17 | East | 211636314 | 23-01-2025 17:12 | 82.5 | 5H.8901.../2420065 | Starting Issue Call By KGD Name - Komkom Neha Number - 9234456624 | Open | Tathastu. | 75 | Update Pending | OPEN | Prabhakar Kumar
18 | East | 211633155 | 23-01-2025 09:12 | 320 | F6.8802.../2420204 | Trip_Genset_Low_Voltage | Cancelled | Biju Kaumbang | 560 | Cancelled- DEF level low guided on call issue resolved without site visit | OPEN | Ujjwal Das
1 | North | 211638820 | 24-01-2025 13:23 | 125.4 | 4H.8042.C4../2420426 | Leakage Issue | Task Start | Shikha Industries. . | Espiem Engines & Machines (P) Limited - Aligarh | 140 | Coolant leakage from Radiator bottom hose pipe clamp loose tightness the same issue resolve | Closed | Sudhir Awasthi
2 | North | 211638650 | 24-01-2025 12:44 | 20 | GP3.8601.../2420046 | Starting Issue Call By Customer Name :- Gulshan Mobile No :-9671641745 | Task Start | Arora Agency | Paluck Technologies Ltd. - Gurgaon |  | Cancelled-SR open on wrong ESN | Cancelled | Kapil Solanki
3 | North | 211638595 | 24-01-2025 12:31 | 20 | GP3.8604.../2420113 | INSTANCE ID:-100741907 SITE ID:- I-UE-KHJN-ENB-9045 CALL BY CUSTOMER\\ DG ISSUE:-dg issue NAME-AMIT NUMBER:-8887532065 | Task Start | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur | 400 | Load trial on 1 hour found no any alarm issue | Closed | Sudhir Awasthi
4 | North | 211638211 | 24-01-2025 11:27 | 160 | 6H.8475.../2420123 | Low Voltage Alarm Call By Customer Name - Mahender Singh No -9812314173 | Open | Hotel B. G. M. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Visit pending | open | Gourav Sharma
5 | North | 211638198 | 24-01-2025 11:26 | 58.5 | T4.8941.../2421994 | White Smoke Issue Call By Customer Name : Omveer Singh Mobile No : 9999786175 | Task Start | CHAUDHARY GENERATOR SERVICE | Paluck Technologies Ltd. - Ghaziabad | 416 | Wrong report- Engineer visit & found no any smoke From Engine | Closed | Kapil Solanki
6 | North | 211637908 | 24-01-2025 10:35 | 20 | GP3.8601.../2420707 | Urea Leakage Issue Call By Customer Name :- Rahul Sir.. Mobile No :- 9891618484 | Task Start | Rahul Sir | Vidyut Engineers - New Delhi | 7 | Wrong report SR- Engineer visit & found no any issue | Closed | Kapil Solanki
7 | North | 211637794 | 24-01-2025 10:10 | 40 | 3H.8951.../2421403 | Automation Issue Call by Customer Name : Niraj .. No : 9415005319 | Task Start | Ashish Traders | S. R Engines Sales And Service - Gorakhpur | 58 | found mains supply not proper so dg set not working properly in auto mode then connect the mains sensing wire from servo out put supply then start dg in Auto then issue resolve | Closed | Sudhir Awasthi
8 | North | 211636452 | 23-01-2025 17:32 | 30 | 3H.8902.../2420788 | Starting Issue Email By - OEM Name - Yogendra Sharma | Task Start | Jai Bajrang Seva Samiti | Espiem Engines & Machines (P) Limited - Aligarh | 2 | Air lock in fuel line remove the air then issue resolve (CC done on 02-12-2024) | Closed | Sudhir Awasthi
9 | North | 211636351 | 23-01-2025 17:17 | 125.4 | 4H.8042.C4../2420330 | Automation Issue Call By Customer Name - Priyank Asati Priyank Asati Number - 7317645299 | Open | Shri Dhanushdhari Hotels and Resorts | Espiem Engines & Machines (P) Limited - Jhansi | 4 | Synchonozation 125kva, 250kva, 380kva | Closed | Sudhir Awasthi
10 | North | 211633294 | 23-01-2025 10:04 | 20 | GP3.8601.../2420643 | Dg set not start | Closed | ICICI Bank Limited | S.S. Enterprises - Allahabad | 36 | Maintenance due alarm reset the alarm | Closed | Sudhir Awasthi
11 | North | 211644398 | 25-01-2025 16:30 | 20 | GP3.8601.../2420818 | Sound/Vibration Issue | Closed | Chola Retreat. | Espiem Engines & Machines (P) Limited - Aligarh | 80 | V-belt loose tightness the same issue resolve | Closed | Sudhir Awasthi
12 | North | 211644394 | 25-01-2025 16:27 | 30 | 3H.8902.../2420283 | Starting & Under speed Alarm Call By Customer Name - Nitesh No - 9258077178 | Open | Anand Foam and Handloom. | Paluck Technologies Ltd. - Ghaziabad |  | Visit pending | open | Kapil Solanki
13 | North | 211643942 | 25-01-2025 15:42 | 58.5 | T4.8941.../2423051 | Starting issue and error code issue Call By Customer Name :- Manoj No :- 7042353275 | Closed | KUNU EMBROIDERY MILLS | Paluck Technologies Ltd. - Ghaziabad | 46 | SPN/FMI 2791/18 Flash the file then start the DG issue resolve | Closed | Kapil Solanki
14 | North | 211643343 | 25-01-2025 14:50 | 125.4 | 4H.8041.../2420675 | Starting issue Call By Customer Name :-Akshat .. Mobile No :- 9058439345 | Closed | M/S SAMYAM INDUSTRIES | R K Engineers - Muzaffarnagar | 157 | Found Emergency button pressed condition & SPN/FMI 2802/4 after realeased the button & clear the fault code | Closed | Sudhir Awasthi
15 | North | 211643248 | 25-01-2025 14:22 | 82.5 | 5H.8901.../2420442 | Starting Issue Call By Customer Name :- Rahul Mobile No :-7233826166 | Open | Azoomi Foods. | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi
16 | North | 211642902 | 25-01-2025 12:51 | 57 | T4.8941.../2320065 | Oil Leakage issue Call By Customer Name :- V S Tripathi Mobile No :- 9560781210 | Closed | PIONEER ENGINEERING & AUTOMOTIVE CORPORATION | Paluck Technologies Ltd. - Faridabad | 794 | Lub oil leakage from Oil filling cap tightness the same issue resolve | Closed | Kapil Solanki
17 | North | 211642861 | 25-01-2025 12:40 | 25 | GP3.8702.../2421273 | MCB Tripping & Over Load Issue Call By Customer Name :- Prakash Vaishnav Mobile No :-7014763403 | Closed | Ira Retreat Pvt Ltd | BSES (I) Pvt. Ltd. - Udaipur | 144 | Customer side overload issue | Closed | Gourav Sharma
18 | North | 211642720 | 25-01-2025 12:10 | 10 | GP3.8301.../2420298 | Battery high voltage | Closed | Mr. Umesh Joshi | Deep Jyoti Electricals and Services - Haldwani | 121 | Battery voltage high set on controller 14.5V set from controller 15V | Closed | Sudhir Awasthi
19 | North | 211641900 | 25-01-2025 08:55 | 500 | DV8.8501.C4../2320051 | Trip_Genset_Low_Voltage | Closed | Sunil Healthcare Limited | Pratap Diesels Pvt. Ltd. - Alwar | 57 | Found no any issue | Closed | Gourav Sharma
20 | North | 211640765 | 24-01-2025 17:53 | 125.4 | 4H.8042.C4../2420734 | Trip_Genset_Low_Voltage | Cancelled | Hotel Subhadra | Espiem Engines & Machines (P) Limited - KANPUR |  | Cancelled-SR open by mistake | Cancelled | Sudhir Awasthi
21 | North | 211639473 | 24-01-2025 15:47 | 160 | 6H.8475.../2420004 | Auto Stopping Issue Call By Customer Name :- Nahar Singh Mobile No :- 9571560069 | Closed | Hotel Fateh Garh A Unit Of Ram Pratap Developers Pvt.Ltd. | BSES (I) Pvt. Ltd. - Udaipur | 6 | Customer side panel issue- Cool down time increase | Closed | Gourav Sharma
22 | North | 211639233 | 24-01-2025 14:55 | 30 | 3H.8902.../2320180 | Starting/Stopping Issue | Closed | Aman Warehousing Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Agra | 292 | Battery discharge, check electrolite level ok but Engineer remove the battery take to the office for checking then found leakage- Give the update | open | Sudhir Awasthi
23 | North | 211639228 | 24-01-2025 14:54 | 82.5 | 5H.8901.../2320094 | Alarm Issue Call By Customer Name - Rajeev .. Number - 8368002845 | Task Start | RAO TENT HOUSE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 407 | SPN/FMI 516166/0 reset the alarm after clear the code issue resolve | Closed | Kapil Solanki
24 | North | 211639115 | 24-01-2025 14:29 | 250 | F6.8841.../2420428 | Over heating issue Call By Customer Name :- Deepak Gupta Mobile No :- 8708530033 | Closed | Svasca Industries ( Ind) Ltd | Paluck Technologies Ltd. - Faridabad | 41 | Customer gives the over load on DG so, DG trip with alarm over load ,Engineer educatye the customer please maintain the load | Closed | Kapil Solanki
25 | North | 211644409 | 25-01-2025 16:28 | 58.5 | T4.8941.../2421264 | Starting/Stopping Issue | Closed | Chola Retreat. | Espiem Engines & Machines (P) Limited - Aligarh | 110 | Found Emergency button pressed condition realease the same issue resolve (EFSR WRONG FILL) | Closed | Sudhir Awasthi
26 | North | 211637905 | 24-01-2025 10:34 | 57 | T4.8941.../2320205 | Electrical Problems | Closed | Daiko From Here On Communication Pvt. Ltd. | Vidyut Engineers - New Delhi | 85 | Found 1C2 negative wire loose tightness the same issue resolve | Closed | Kapil Solanki
27 | North | 211637496 | 24-01-2025 08:50 | 20 | GP3.8601.../2320048 | Red Alarm Issue Call By Customer Name :- Javana Devasi Mobile No :- 7767851480 | Task Start | Beauty Impex Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 325 | Emergency alarm check & found panel back side of button wire loose tightness the same then issue resolve | Closed | Kapil Solanki
28 | North | 211644621 | 25-01-2025 17:01 | 58.5 | T4.8941.../2422836 | Starting issue Called by customer Name: Gagandeep Singh Number: 9582468392 | Closed | Honey & Dough | OVN Industries Private Limited - New Delhi | 5.1 | Found Battery voltage low, Customer battery charger not working so, Now | Closed | Kapil Solanki
29 | North | 211642410 | 25-01-2025 11:15 | 160 | 6H.8475.../2420031 | Belt Broken Call By Customer Name :- Kunal Mobile No :-9318326116 | Closed | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 2769 | V belt broken, Replace with 4k belt | Closed | Kapil Solanki
30 | North | 211639189 | 24-01-2025 14:44 | 250 | F6.8841.../2420343 | Tripping Issue. Call by Customer. Name:-Shiv .. Mobile No.:-8585932580 | Closed | DIVYA JYOTI JAGRATI SANSTHAN | OVN Industries Private Limited - New Delhi | 56 | Emergency switch wire tightness | Closed | Kapil Solanki
31 | North | 211638938 | 24-01-2025 13:50 | 500 | F6.8843.C4../2420001 & 24200001 | Fuel Tank Issue & Adblue Level Issue Call By Service Dealer Name - Rajesh Number - 9991740559 | Task Start | M. P. Institute of Medical Research | SAAN Royal Power Solutions Private Limited - Karnal | 108 | DEF Cap lock found faulty so replace the same & also Fuel level not showing correct in controller;will flash the same by Monday | Open | Ved Prakash Gupta
32 | North | 211638833 | 24-01-2025 13:27 | 400 | 6H.8439.../2420004 & 2420003 | Inspection/Maintenance | Task Start | The Pearl Petal. | SAAN Royal Power Solutions Private Limited - Rohtak | 55 | SPN/FMI-97/2 & 1761/16 ;AdBlue level found correct on site , Drain Fuel from watr separator,found ok,remove the code & run the DG,Issue resolved | Closed | Ved Prakash Gupta
33 | North | 211638412 | 24-01-2025 12:03 | 58.5 | T4.8941.../2421363 | Auto starting issue | Task Start | Shri Rama Bharti Public School | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 51 | Auto Starting Issue due to 8-pin Relay found faulty in Customer's AMF Pannel,advised to replace the same | Closed | Ved Prakash Gupta
34 | North | 211638395 | 24-01-2025 12:01 | 250 | F6.8841.../2420137 | Starting issue | Task Start | Anhad Polymers LLP. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 48 | Auto Starting issue due to 49 no. wire found loose in pannel so re-connected same & resolve the issue | Closed | Ved Prakash Gupta
35 | North | 211638307 | 24-01-2025 11:43 | 30 | 3H.8902.../2421481 | AUTOMATION ISSUE | Task Start | SANT MALHOTRA | SAAN Royal Power Solutions Private Limited - Zirakpur | 7 | Automation issue ; Customer Paanel side issue;same rectified by AMF Pannel technician | Closed | Ved Prakash Gupta
36 | North | 211638026 | 24-01-2025 10:54 | 625 | DV0.8501.C4../2420079 | ECU issue Call By Customer Name - Devendra Saini Mobile No -8053353744 | Task Start | HPL. Electric & Power Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 190.33 | SPN/FMI-660/5 ; Cylinder no.-10 injector wire found loose sotightened the same & resolve the issue | Closed | Ved Prakash Gupta
37 | North | 211637782 | 24-01-2025 10:06 | 320 | F6.8802.../2420005 | Lamp Alarm Issue Call By Customer Name :- Manish Kumar Mobile No :- 9350174697 | Task Start | Alko Plus Technosafe Private Limited | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 203.6 | Under Voltage alarm due to 2A1 fuse found faulty in controller so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
38 | North | 211637689 | 24-01-2025 09:45 | 125.4 | 4H.8042.C4../2420850 | . | Task Start | First Pure Diet Milk Products. | SAAN Royal Power Solutions Private Limited - Sonipat | 4.25(LR) | Relay card found faulty so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
39 | North | 211637680 | 24-01-2025 09:38 | 25 | GP3.8702.../2421363 | Leakage Issue | Closed | SS Engineer & Company | SAAN Royal Power Solutions Private Limited - Hisar | 38 | Coolant Leakage found on Radiator(Top-side) due to clamp found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
40 | North | 211636825 | 23-01-2025 19:12 | 20 | GP3.8601.../2420937 | Starting issue Called by customer Name: MANISH CHADHA Number: 9417372910 | Open | Super Creations. | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Under Cancellation-rectified on call | Cancelled | Ved Prakash Gupta
41 | North | 211645982 | 26-01-2025 09:47 | 25 | GP3.8702.../2420302 | Error code | Task Start | Aryadhenu Misthanshala | SAAN Royal Power Solutions Private Limited - Hisar | 25 | Cam Sensor flt. Signal error ; will flash the ECU Today due to non-availability of Nira cable | Open | Ved Prakash Gupta
42 | North | 211644735 | 25-01-2025 17:22 | 625 | DV0.8501.C4../2320017 | Inspection/Maintenance | Open | M/s. Swayut Automation | Suraj Motor Store - Jammu |  | Visit pending | Open | Ved Prakash Gupta
43 | North | 211643043 | 25-01-2025 13:21 | 100 | 4H.8041.../2320072 | Electrical Problems | Task Start | Council of Scientific and Industrial Research CSIR. Himachal Pradesh | Megatron Engineers - Amb | 97.43 | Glass fuse Cap was not available on fuse so replace the same & wire thimble on relay card found faulty so corrected the same,DG starting after cranking nearly 20 second ; pre-heater required | Open | Ved Prakash Gupta
44 | North | 211642968 | 25-01-2025 13:08 | 40 | 3H.8951.../2420736 | Starting/Stopping Issue | Closed | SHRIRAM POLYMERS | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 27 | Y-Phase under Voltage occurred , Found YG1 fuse faulty so replace the same & resolve the issue | Closed | Ved Prakash Gupta
45 | North | 211642905 | 25-01-2025 12:51 | 160 | 6H.8475.../2420060 | Amber Lamp On Alarm Call By Customer Name :- Gaurav Mobile No :-7357995380 | Closed | Chirag Industries | SAAN Royal Power Solutions Private Limited - Sonipat | 59.49 | SPN/FMI-1761/16 & 516166/0 ; Top-up the AdBlue & remove the code,issue resolved | Closed | Ved Prakash Gupta
46 | North | 211642337 | 25-01-2025 11:05 | 58.5 | T4.8941.../2421664 | Starting Issue Call By Customer Name - Zakir Hussain Number - 9797312304 | Open | Sindh Dairy Products | Suraj Moters Stores - Leh |  | Visit pending | Open | Ved Prakash Gupta
47 | North | 211642305 | 25-01-2025 10:54 | 30 | 3H.8902.../2320025 | Starting issue | Closed | Gabsons Engineers & Consultants | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 184 | Starting issue due to fuse of 2D found faulty so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
48 | North | 211642304 | 25-01-2025 10:53 | 30 | 3H.8902.../2320028 | Leakage issue | Closed | High Tech Profile Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 169 | Coolant leakage found from radiator to thermostat pipe due to clamp found loose(Bottom side) so tightened the same & resolve the issue | Closed | Ved Prakash Gupta
49 | North | 211642273 | 25-01-2025 10:50 | 58.5 | T4.8941.../2421599 | AUTOMATION issue | Closed | Durga Gold & Diamond Jewellery. | SAAN Royal Power Solutions Private Limited - Rohtak | 1.2 | Installation completed for Auto starting in Pannel | Closed | Ved Prakash Gupta
50 | North | 211642013 | 25-01-2025 09:58 | 20 | GP3.8601.../2421110 | Starting Issue Call By Customer Name - Darshan Number - 7717302590 | Closed | Gahir Agro Industry | Gen Powers - PATIALA | 2 | Emergency switch found pressed on site so release the same & educated customer about same | Closed | Ved Prakash Gupta
51 | North | 211641886 | 25-01-2025 09:07 | 82.5 | 5H.8901.../2420804 | Starting Issue Call By Customer Name :- Naveen Mobile No :-8222894142 | Closed | Dhani Power Solutions | SAAN Royal Power Solutions Private Limited - Sonipat | 214.1 | Under Speed Alarm occurred on controller & it occurred very often so disabled the same & run the DG on Load for 1 hour,no issue found | Closed | Ved Prakash Gupta | 4225/1(NOx Limit Exceeded), 3031/14, 3364/27(Def Quality), 4095/1
52 | North | 211640971 | 24-01-2025 18:32 | 20 | GP3.8601.../2421099 | Red lamp alarm issue Call By Customer Name :- Sukhpal Singh Mobile No:- 6280763897 | Task Start | M/s Abdul Aziz mir | Suraj Motor Store - Srinagar |  | Visit pending | Open | Ved Prakash Gupta
53 | North | 211640924 | 24-01-2025 18:26 | 320 | F6.8802.../2420264 | VOC- WATER LEAKAGE FROM RADIATOR HOSE CLIPS Customer Name - Manu Customer Number -7876623268 Mode- SR Generated through CDI calling. | Closed | The Royal Velvet. | SAAN Royal Power Solutions Private Limited - Rohtak | 19 | Coolant Leakage found on inlet pipe due to clamp found loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta
54 | North | 211640870 | 24-01-2025 18:06 | 250 | F6.8841.../2420243 | Trip_Genset_Low_Voltage | Closed | Divy Power Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 50 | Under Voltage alarm occurred in DG in Auto mode due to customer keep on Load via change-over even before starting the DG ;Under speed occurred due to RPM not able to get;same educated to customer | Closed | Ved Prakash Gupta
55 | North | 211639290 | 24-01-2025 15:12 | 82.5 | 5H.8901.../2320082 | AMBER LAMP ALARM | Closed | Jai Residency | SAAN Royal Power Solutions Private Limited - Rohtak | 26 | SPN/FMI-157/14 ; Check the fuel condition ,found ok , Check PRV Count & keep same to 0 & start the same,issue resolved | Closed | Ved Prakash Gupta
1 | West | 211631188 | 22-01-2025 16:10 | 58.5 | T4.8941.../2422942 | Engine not starting | Task Start | Roongta Group Builders & Developers | Dhanashree Technocrats Pvt. Ltd. - Nasik | 1 | SPN/FMI- 97/5 (Water in fuel_ self test) Checked the panel wiring found ok. According to the SD engineer, the genset is starting after overriding the controller and pressing the start button. Today the SD engineer will go to the site with the water separator filter. | Closed | Jagdeep Saini
2 | West | 211645154 | 25-01-2025 19:11 | 40 | 3H.8951.../2420333 | Starting/Stopping Issue | Closed | AIA Engineering Ltd. | Unique Techno Services Pvt Ltd. - Ahmedabad | 14.55 | DG under speed alarm Checked the fuel line found ok so reset the alarm and DG is under observation. KRM issue. | Closed | Amit sandlya
3 | West | 211644228 | 25-01-2025 15:52 | 125.4 | 4H.8042.C4../2421027 | Starting/Stopping Issue | Closed | MD INFRA INDIA PRIVATE LIMiTED | Mahalaxmi Diesels - Satara | 5 | The customer complained that the engine would start when the start button was pressed hard. So the engineer visited the spot and found that the start button was working properly | Closed | Jagdeep Saini
4 | West | 211644223 | 25-01-2025 15:51 | 30 | 3H.8902.../2420355 | Loading Issue Call By Customer Name :- Mohit Sir Mobile No :-7828410847 | Closed | MHK BUILDCON LLP | Natraj Power Tech - Dhar | 610.1 | Engine was starting but stop in 5-10minutes so SD checked the fuel line and found fuel filter chock up so replaced it and resolved the problem. | Closed | Jagdeep Saini
5 | West | 211643468 | 25-01-2025 15:21 | 35 | 3H.8902.../2422238 | FUEL LEAKAGE FILTER BODY | Task Start | ICICI Bank Limited | Unique Techno Services Pvt Ltd. - Anand | LR | During commissioning SD found that Fuel leakage from benzo bolt on filter. | Open | Amit sandlya
6 | West | 211643303 | 25-01-2025 14:37 | 160 | 6H.8475.../2420307 | Amber Lamp ON Alarm Issue Call By Customer Name - Dipak Pawar Number - 9975566453 | Closed | Khuspal Home Textile LLP. | Transcreek Engineers Pvt. Ltd. - Vasai | 15 | SPN/FMI- 516166/0,So cleared the DTC. | Closed | Jagdeep Saini
7 | West | 211643225 | 25-01-2025 14:22 | 500 | DV8.8501.C4../2420396 | Electrical Problems | Open | Shanmukha Agritec Limited. | Unique Techno Services Pvt Ltd. - Baroda | 4 | 653/3(Cylinder 3 and Injector 1),Checked the continuity from ECU to injector wiring found ok. Resistance 0.5 ohms. So refieted the pigtail connector and issue resolved. Under observation. | Open | Amit sandlya
8 | West | 211643201 | 25-01-2025 14:12 | 625 | DV0.8501.C4../2420005 | Electrical Problems | Closed | ENTREMONDE POLYCOATERS LIMITED | Dhanashree Technocrats Pvt. Ltd. - Nasik | 172 | Fuel level sensor was not working properly and fuel level was showing ++++ in the controller so programmed it and issue resolved. | Closed | Jagdeep Saini
9 | West | 211643061 | 25-01-2025 13:24 | 125.4 | 4H.8042.C4../2420595 | Starting Issue Call By Customer Name :- Surender Mobile No :-9404960020 | Closed | INDU CONSTRUCTION | Dicksons Engineering Co.Pvt.Ltd. - AMRAVATI | 62 | Low DEF level. | Closed | Jagdeep Saini
10 | West | 211642869 | 25-01-2025 12:45 | 58.5 | T4.8941.../2422973 | Error Code Issue And MIL Lamp On Alarm Call By Customer Name :- Nikhi Mobile No :-9823983099 | Task Start | OMKAR ENTERPRISES | Transcreek Engineers Pvt. Ltd. - Wadkhal | 5.22 | SPN/FMI-2791/18, therefore suggested the SD engineer to calibrate the ECU. | Open | Jagdeep Saini
11 | West | 211642528 | 25-01-2025 11:37 | 125.4 | 4H.8042.C4../2420711 | Amber Lamp Alarm issue Call By Customer Name :- Ganesh Patil Mobile No :-9049256215 | Closed | Chhabubhai Bapusaheb Chavan | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 38.58 | Low DEF level. | Closed | Jagdeep Saini
12 | West | 211642455 | 25-01-2025 11:25 | 160 | 6H.8475.../2420136 | Starting Issue Call By Customer Name :- Hitesh Mobile No :-9420143113 | Closed | Padam Kapada Bazar | Dicksons Engineering Co.Pvt.Ltd. - CHANDRAPUR | 282 | There was an abnormal sound coming from the genset, so when it was checked it was found that the belt was loose. | Closed | Jagdeep Saini
13 | West | 211642369 | 25-01-2025 11:08 | 30 | 3H.8902.../2421152 | engine change | Task Start | I P Laghu Udyog | Dhanashree Technocrats Pvt. Ltd. - Dhule | LR | There is a problem of coolant leaking from the cylinder head at 0h, so the engine was replaced | Closed | Jagdeep Saini
14 | West | 211642160 | 25-01-2025 10:31 | 750 | DV2.8501.C4../2420055 | Starting/Stopping Issue | Task Start | SHREE GANESH ENGINEERING WORKS UNIT I | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 4 | SR Sync opened for activity. | Open | Jagdeep Saini
15 | West | 211646406 | 27-01-2025 08:28 | 0 | DV8.8542.C4../2420152 | Air leakage | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi | 2 | Line between throttle valve and exhust pipe bolt found missing so fitted new bolt | Closed | Amit sandlya
16 | West | 211646193 | 26-01-2025 17:50 | 58.5 | T4.8941.../2422032 | Diesel Leakage Issue Call By Customer Name :- Sohail Diwan Mobile No :- 9662531194 | Open | Mom DJ. Sound | Unique Techno Services Pvt Ltd. - Anand | 20 | cancelled | Closed | Amit sandlya
17 | West | 211645994 | 26-01-2025 10:26 | 125.4 | 4H.8042.C4../2420808 | KRM Issue And Mobil Tank Change And Amber Lamp On Alarm Call By Customer Name- Sudip Mobile No-7507719036 | Open | Russel Britto | Mahalaxmi Diesels - Goa | 76 | cancelled | Closed | Jagdeep Saini
18 | West | 211644542 | 25-01-2025 16:47 | 58.5 | T4.8941.../2422077 | Starting/Stopping Issue | Open | Shree Marketing Devkar Poultry Farm | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati | 193.15 | cancelled | Closed | Jagdeep Saini
19 | West | 211642853 | 25-01-2025 12:42 | 20 | GP3.8601.../2420516 | dg alarm issue Email By - OEM Name - Surekha Auti | Closed | Arun Chunilal Khinvasara H. U. F. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 28 | coolant leakage from radiator bottom hose pipe clip , tight the clip issue solved. | Closed | Jagdeep Saini
20 | West | 211642583 | 25-01-2025 11:43 | 15 | GP3.8501.../2420545 | Red Lamp On Alarm Issue Call By Customer Name :-Dipankar Gautam Mobile No :-9691977970 | Open | KansaiÂ NerolacÂ Paints Ltd. | Shree Engineering Service - Jabalpur | 17 | Emergency stop was pressed so dg was not started , release the buttom issue resolved. | Closed | Vijay Patil
21 | West | 211639841 | 24-01-2025 16:40 | 400 | DV8.8542.C4../2420036 | Genset Trip | Closed | Ishvaha Enterprises Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Ahmedabad | 3.55 | Error code 516163/0(ECU Internal Failure ) disconnect ECU connector and battery supply after 10 min connect all the connector and start the dg no error code display. | Closed | Amit sandlya
22 | West | 211639570 | 24-01-2025 16:01 | 125.4 | 4H.8042.C4../2420225 | Amber lamp issue | Closed | MSLR. Private Limited | Shree Engineering Service - Satna | 1298 | Error code spn 516166 FMI op1047 connect ikonnect and clear error, issue resolved. | Closed | Vijay Patil
23 | West | 211639560 | 24-01-2025 15:59 | 58.5 | T4.8941.../2421155 | Starting/Stopping Issue | Closed | KAIZEN FITNESS AND LIFESTYLE | Shree Engineering Service - Raipur | 3.2 | 2D Fuse between distribution box to control panel +Ve supply found blown , placed new fuse issue solved. | Closed | Vijay Patil
24 | West | 211639333 | 24-01-2025 15:22 | 125.4 | 4H.8042.C4../2421028 | Engine Starting Issue Call By Service Dealer Name :- Nilesh gavande Mobile No :-9730298698 | Closed | SHRI GURUDATTA CONSTRUCTIONS | KALA Care Global LLP - Ahmednagar | 28 | Adblue level low top up adblue level. | Closed | Jagdeep Saini
25 | West | 211639265 | 24-01-2025 15:01 | 125.4 | 4H.8042.C4../2420189 | Electrical Problems | Closed | SUNRISE CONSTRUCTIONS | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 163 | adblue level is low 38% so top up adblue level is 99 % ok. | Closed | Jagdeep Saini
26 | West | 211638828 | 24-01-2025 13:25 | 20 | GP3.8601.../2420472 | Over Load Alarm issue Call By Customer Name :- Ankit Mobile No :- 8349228611 | Closed | Sai Sales & Service | Natraj Power Tech - Chhindwara | 8.52 | Customer side issue | Closed | Jagdeep Saini
27 | West | 211638651 | 24-01-2025 12:44 | 58.5 | T4.8941.../2420469 | Starting/Stopping Issue | Task Start | Satyanarayan Chouhan | Natraj Power Tech - Ujjain | 18 | Dust found in cam sensor so under speed alarm clean the sensor issue solved. | Closed | Jagdeep Saini
28 | West | 211638622 | 24-01-2025 12:38 | 125.4 | 4H.8042.C4../2420673 | error code problem | Task Start | Vihav Group | Unique Techno Services Pvt Ltd. - Baroda | 2 | Error code 520528/31 connect ikonnect and remove error code issue solved. | Closed | Amit sandlya
1 | North | 211648045 | 27-01-2025 13:55 | 40 | 3H.8951.../2420096 | Starting issue Call by customer Name: Ramjna Number: 8130797147 | Task Start | Purvanchal Projects Pvt Ltd | Vidyut Engineers - Noida | 2796 | EMS not getting ON found fuse in EMS supply line blown, just replaced the fuse, Issue resolved. | Closed | Kapil Solanki
2 | North | 211648015 | 27-01-2025 13:41 | 125.4 | 4H.8041.../2420745 | Starting/Stopping Issue | Closed | JAIN GENERATOR HIRING CO.. | OVN Industries Private Limited - New Delhi | 1457 | Low DEF level & fuel level, Educate the customer maintain the Def & fuel min. 50% | Closed | Kapil Solanki
3 | North | 211647918 | 27-01-2025 13:23 | 125.4 | 4H.8042.C4../2420693 | Abnormal sound issue And White smoke issue Call By Customer Name :- kamal panday No :- 9811408710 | Task Start | Amar Jyoti Charitable Trust | Vidyut Engineers - New Delhi |  | Today SE visit with i-konnect tool | open | Kapil Solanki
4 | North | 211647905 | 27-01-2025 13:16 | 20 | GP3.8601.../2421139 | Under Speed Alaram Issue Call By Customer Name :-Udit Sir Mobile No :-9810957005 | Task Start | TAYAL INDUSTRIES | OVN Industries Private Limited - New Delhi | 2.1 | dg set load goes to 40 amp so dg set rpm drop and dg tripping with under speed. and next test goes 25 now dg set running ok . customer moter fault advised to customer please check your motor dg is running ok | Closed | Kapil Solanki
5 | North | 211647744 | 27-01-2025 12:56 | 125.4 | 4H.8041.../2420221 | Leakage Issue | Task Start | MUKESH RANJAN CONTRACTORS | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1266 | Oil leakage from oil sump, now anabond use for leakage stop, EDO place for sump | open | Kapil Solanki
6 | North | 211647669 | 27-01-2025 12:36 | 58.5 | T4.8941.../2422800 | VOC-Genset trip issue. Customer Name - Vishal Tak Customer Number -7737789455 Mode- SR Generated through CDI calling. | Task Start | VISHAL KUMAR TAK | Rajdhani Diesels and Electricals - Jodhpur | 36 | As discussed with Customer & understood, Load not taking issue. Service engineer will visit the site today , then will share the actual issue. | open | Gourav Sharma
7 | North | 211647593 | 27-01-2025 12:29 | 30 | 3H.8902.../2420303 | Starting/Stopping Issue | Cancelled | Senani Service Station. | OVN Industries Private Limited - New Delhi |  | Cancelled-Problem solve in tele discussion | Cancelled | Kapil Solanki
8 | North | 211647295 | 27-01-2025 11:40 | 125.4 | 4H.8041.../2420345 | Starting/Stopping Issue | Completed | Secret Heart Convent School | Megatron Engineers - Amritsar | 132 | Customer raised complaint as starting issue but no such issue observed on site , neither any code found in event log | Closed | Ved Prakash Gupta
9 | North | 211647119 | 27-01-2025 11:14 | 125.4 | 4H.8041.../2320101 | Oil Leakage Issue Call By Customer Name :-Sanjay Gupta . Mobile No :- 9711360601 | Task Start | ALTOS ENGINEERS PVT LTD. | Paluck Technologies Ltd. - Gurgaon | 363 | Oil leakage from Rocker cover New packing set then oil leakage stop | Closed | Kapil Solanki
10 | North | 211647085 | 27-01-2025 11:08 | 40 | 3H.8951.../2320031 | Starting Issue & under speed Alaram Isuue Call By Customer Name :- Jogindra Mobile No :-9999930655 | Closed | Sai Lighting Components | Paluck Technologies Ltd. - Ghaziabad | 315 | Found fuel leakage from fuel leak off pipe because bolt was loose tightness the same & found main alternator duck bolt missing, Required air filter change & oil through from turbo to CAC repaired required | open | Kapil Solanki
11 | North | 211647056 | 27-01-2025 11:03 | 25 | GP3.8702.../2420099 | Leakage Issue | Task Start | Mr. Harminder Singh Samra. | Dynamic Engineering Services - Jalandhar | 6 | Fuel Leakage found from Fuel Tank Drain plug so tightened the same & check all the pipe joints of Fuel line ; DG not run since october but fuel level found low ; DG under observation for 3 days to confirm the suspect of Tank Faulty | Open | Ved Prakash Gupta
12 | North | 211647000 | 27-01-2025 11:00 | 125.4 | 4H.8042.C4../2420554 | Automation Issue Call By Sales Dealer Name :-Omveer Sharma Mobile No :-9910626566 | Closed | Mandala Construction Pvt. Ltd. | Vidyut Engineers - New Delhi | 15 | Auto connection loose tighten the same then check Auto & Manual DG run ok issue resolve | Closed | Kapil Solanki
13 | North | 211646694 | 27-01-2025 09:54 | 320 | F6.8802.../2420073 | Door Lock Issue Coolant Leakage Issue & Coolant Lid Issue Call By Customer Name :- Rishi Pal Mobile No :- 7838955880 | Open | A.G. Pipes Pvt. LTD. | Paluck Technologies Ltd. - Faridabad |  | Visit pending | open | Kapil Solanki
14 | North | 211646650 | 27-01-2025 08:30 | 125.4 | 4H.8041.../2420259 | Starting issue Call By Customer Name :- 9636320216 Mobile No :- Om Choudhary | Task Start | Cygnet Servises | Rajdhani Diesels and Electricals - Barmer |  | DG Set not Starting issue. Suggested fuel Feed pump not working. New Feed pump arranging | Task start | Gourav Sharma
15 | North | 211646324 | 26-01-2025 20:36 | 45 | 3H.8951.../2421243 | Starting issue Call By Customer Name :- Ram Charn Mobile No :-7982975198 | Closed | SETHI BUILDCON | OVN Industries Private Limited - New Delhi | 162 | Found Emergency wire removed from Switch connect the wire after tight issue resolve | Closed | Kapil Solanki
16 | North | 211646150 | 26-01-2025 15:26 | 30 | 3H.8902.../2420661 | INSTANCE ID:-100773803 SITE ID:-UP/KSB/BS/14128 CALL BY CUSTOMER// DG ISSUE :- automation faulty SILENCER ISSUE NAME:-umesh kumar triparti NUMBER:-9076556117 | Task Start | ATC Telecom Infrastructure Private Limited | S.S. Enterprises - Allahabad |  | Today SE visit | open | Sudhir Awasthi
17 | North | 211646143 | 26-01-2025 15:10 | 82.5 | 5H.8901.../2420764 | Starting Issue. Call By customer. Name:- Sriram .. Mobile No.:-8527510514 | Closed | THE NISKHAM COOPERATIVE GROUP HOUSING SOCIETY LTD | OVN Industries Private Limited - New Delhi | 7 | Found Emergency button pressed, realeased the same issue resolve | Closed | Kapil Solanki
18 | North | 211638928 | 24-01-2025 13:46 | 20 | GP3.8604.../2420102 | INSTANCE ID:-100740911 SITE ID:- I-RJ-ALWR-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- KISHAN NUMBER:- 9024467214 | Task Start | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - Alwar |  | Efsr wrong fill, Mail to ASE for fill-up the right data ( Under voltage alarm) | open | Gourav Sharma
19 | North | 211637873 | 24-01-2025 10:31 | 160 | 6H.8475.../2420022 | Electrical Problems | Task Start | Technologica Infotech Ltd. | Vidyut Engineers - New Delhi |  | Under Cancellation- | Cancelled | Kapil Solanki
20 | North | 211637614 | 24-01-2025 09:21 | 320 | F6.8802.../2320077 | Starting/Stopping Issue | Closed | Sheetal Vihar CGHS. Ltd. | OVN Industries Private Limited - New Delhi | 19 | Customer Dg not start for last 1 month After start the Dg, Dg not start in auto,When Engineer visit then he found Air in fuel line so remove the air then issue resolve | Closed | Kapil Solanki
21 | North | 211634362 | 23-01-2025 13:07 | 500 | F6.8843.C4../2420002 & 2420002 | Hour maintenance problem | Closed | Brij Healthcare & Research Centre. | Espiem Engines & Machines (P) Limited - Agra | 1289 | Last Sr. Running hours reset ,Running hours set | Closed | Sudhir Awasthi
22 | North | 211644206 | 25-01-2025 15:46 | 57 | T4.8941.../2320217 | Voltage Fluctuation | Closed | Sonu Tools | Paluck Technologies Ltd. - Faridabad | 257 | Check & found voltage proper ok but Customer one CNC machine trip so, educate customer check your CNC machine | Closed | Kapil Solanki
23 | North | 211643462 | 25-01-2025 15:21 | 58.5 | T4.8941.../2423129 | Automation Issue Call By Customer Name :- Inder Sir Mobile No :- 8953575851 | Closed | Gurjeet Singh | Vidyut Engineers - New Delhi | 4.2 | Customer side AMF panel not working | Closed | Kapil Solanki
24 | North | 211643277 | 25-01-2025 14:34 | 30 | 3H.8902.../2320065 | Starting Issue Call By Customer Name :- Kishan No :- 8595529405 | Closed | Nippi Kochhar | Vidyut Engineers - New Delhi | 42 | Engineer visit the site found no any issue in DG | Closed | Kapil Solanki
25 | North | 211643149 | 25-01-2025 13:59 | 57 | T4.8941.../2420455 | Sound/Vibration Issue | Closed | Meerut Ptfe Products Pvt. Ltd | R K Engineers - Meerut | 63 | update pending | open | Sudhir Awasthi
26 | North | 211642829 | 25-01-2025 12:33 | 200 | 6H.8435.../2420255 | Main fanbelt loose issue | Closed | DELHI RMC PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | 180 | V-belt defective so, replace the same | Closed | Kapil Solanki
27 | North | 211642711 | 25-01-2025 12:08 | 40 | 3H.8951.../2320004 | Starting Issue Call By Customer Name :- Bhavya Sir Mobile No :-7087038415 | Closed | Waves Enterprises. | Vidyut Engineers - Noida | 191 | Battery voltage low, battery charger AC supply wire break so, battery discharge connect the wire battery charge | Closed | Kapil Solanki
28 | North | 211642578 | 25-01-2025 11:45 | 20 | GP3.8601.../2421547 | SMOKE ISSUE | Closed | Arora Agency | Paluck Technologies Ltd. - Gurgaon | LR_414 | Low fuel level | Closed | Kapil Solanki
29 | North | 211642487 | 25-01-2025 11:28 | 125.4 | 4H.8042.C4../2420693 | Abnormal sound issue And White smoke issue Call By Customer Name :- kamal panday No :- 9811408710 | Closed | Amar Jyoti Charitable Trust | Vidyut Engineers - New Delhi | 9 | Found White smoke from the Engine check fuel line found ok, then check DM clean with hot water then issue resolve | Closed | Kapil Solanki
30 | North | 211642450 | 25-01-2025 11:22 | 125.4 | 4H.8041.../2420223 | Emergency Alarm Issue Call By Customer Name :- Manish Kumar Mobile No :-9711385189 | Task Start | EUROCON GLOBAL EXPORTS (P) LTD | Paluck Technologies Ltd. - Faridabad | 190 | Emergency Alarm reset the alarm the check and found Electric feed pump not working when replace the same issue resolve | Closed | Kapil Solanki
31 | North | 211642079 | 25-01-2025 10:14 | 25 | GP3.8702.../2420303 | DG automation issue | Closed | ATC Telecom Infrastructure Private Limited | OVN Industries Private Limited - New Delhi | 51 | Auto panel & Automation issue | Closed | Kapil Solanki
32 | North | 211642046 | 25-01-2025 10:01 | 125.4 | 4H.8041.../2420021 | Low Flue Alarm Issue & Error Code. Call By Customer. Name:-Bheem Singh. Mobile No.:-8053982489 | Task Start | Cotton Crafters | Paluck Technologies Ltd. - Gurgaon | 267 | Low def level alarm remove the fault code then issue resolve | Closed | Kapil Solanki
33 | North | 211641973 | 25-01-2025 09:46 | 125.4 | 4H.8042.C4../2420110 | Starting issue Call By Customer Name :- Prabhaker Pandey Mobile No :-9911105274 | Closed | SAMSONIC | Paluck Technologies Ltd. - Ghaziabad | 20.5 | Battery discharge because battery charger not connected, Done the connection of battery charger | Closed | Kapil Solanki
34 | North | 211641895 | 25-01-2025 09:18 | 40 | 3H.8951.../2420123 | Starting Issue Call By Customer Name :- Aryan Singh Mobile No :-9999008655 | Closed | Aryan Singh | Paluck Technologies Ltd. - Faridabad | 155 | Customer side panel issue- Mains line short | Closed | Kapil Solanki
35 | North | 211641122 | 24-01-2025 21:56 | 20 | GP3.8601.../2420483 | Battery Charger Issue. Call By Customer. Name:- Sanjay Raj Mobile No.- 9828406318 | Task Start | Surabhi Food Industries. | Pratap Diesels Pvt. Ltd. - BIKANER | 142 | update pending | open | Gourav Sharma
36 | North | 211639411 | 24-01-2025 15:37 | 58.5 | T4.8941.../2420723 | Oil Leakage Issue Call By Customer Name :- PAWAN GARG Mobile No :- 9891602900 | Closed | Pawan Garg | Paluck Technologies Ltd. - Faridabad | 70 | Lub oil leakage, found Filter O ring removed from Filter | Closed | Kapil Solanki
1 | East | 211648154 | 27-01-2025 14:36 | 82.5 | 5H.8901.../2420364 | Starting/Stopping Issue | Task Start | M/s. Landmark Engineering. | M T Enterprises - Bomdila | 64 | visit pending-SPN: 4363,FMI: 3 - T6 Sensor - Signal Range Check SPN: 4095,FMI: 1 - NOx limits exceeded due to Interrupted Diesel Exhaust Fluid Dosing-Low (KRM DATA) | OPEN | Ujjwal Das
2 | East | 211647813 | 27-01-2025 13:01 | 320 | F6.8802.../2420202 | SPN-636,FMI-8 POP UP WHEN START THE ENGINE | Task Start | POWERLINE GREEN | Hibreed Engineering Pvt. Ltd. - Nagaon | 0 | DG not starting showing SPN 636/8 fault code for cam sensor so checked for continuity of camsensor from the ECu found ok checked Pin of EcU found ok then replaced the cam sensor same problem further replaced the ECU but same problem, today SE will change wiring harness under observation | OPEN | Ujjwal Das
3 | East | 211646328 | 26-01-2025 20:45 | 15 | GP3.8501.../2420615 | Load Issue Call By Customer Name ;- Bittu Soni Mob No ;- 8794016784 | Open | M/S Marcofed Heningkunhlwa | Hibreed Engineering Pvt. Ltd. - Jorhat | 148 | Visit pending | OPEN | Ujjwal Das
4 | East | 211645970 | 26-01-2025 08:10 | 15 | GP3.8501.../2420777 | Red Lamp On Alarm Issue Call By Customer Name :Kamal Ch Borah No :9435011568 | Open | Kamal Ch Borah | Hibreed Engineering Pvt. Ltd. - Jorhat | 18 | Sweep stuck alarm SPN 240/7 was displayed on controller so removed the 2 pin and 3 pin connector and checked voltage found 12 V and 5V respectively, then checked rack movement found ok then reconnected connector and also tighten the connector by tie then cranked the DG issue resolved. | CLOSED | Ujjwal Das
5 | East | 211645260 | 25-01-2025 21:25 | 20 | GP3.8601.../2421368 | Trip_Genset_Low_Voltage | Open | Akuvu Powerline. | Hibreed Engineering Pvt. Ltd. - Jorhat | 2.8 | today SE will visit. | OPEN | Ujjwal Das
6 | East | 211644289 | 25-01-2025 16:07 | 5.5 | CC1.1013.../2400016 | Starting issue and Preventive Maintenance Call By Customer Name :- Shakti Kumar Mobile No :- 6294815565 | Open | East Coast Railway Andhra Pradesh | HACS Engineering and Tech Private Limited - Dhanbad |  | visit pending | OPEN | Prabhakar Kumar
7 | East | 211639073 | 24-01-2025 14:18 | 125.4 | 4H.8041.../2420412 | Genset Trip | Closed | Style Baazar Santragachi | Globalline India Services Private Limited - Darbhanga | 892 | SPN 4339 FMI 2, SPN 4095 FMI 1, SPN 4095 FMI 2, SPN 7598 FMI 7, then conected Ikonnect found same fault code in DTC then checked live parameter found relative urea pump pressure 36 - 50 hPa, so checked supply module voltage found ok and countinutity was also ok from the ECU, then also pressure not buildup so further replaced also urea filter but same problem then removed the dosing module urea connetor and given direct supply to main pump in module but motor does not work, so replaced the supply module issue resolved. | CLOSED | Prabhakar Kumar
8 | East | 211647984 | 27-01-2025 13:36 | 20 | GP3.8601.../2420716 | Low fuel level sensor issue | Task Start | Loknath Taranga Neer. | Revenus Industries Pvt. Ltd. - Contai | 43 | Visit pending | OPEN | Prosanjit saha
9 | East | 211647475 | 27-01-2025 12:15 | 15 | GP3.8501.../2421126 | Starting Issue And red lamp Alarm Issue Call by Name :Ashok . Mo No:7004216264 | Task Start | Amma engineering | Gangpur Sales and Services - BHUBANESWAR | 23 | Visit pending | OPEN | Ujjwal Das
10 | East | 211647092 | 27-01-2025 11:09 | 250 | F6.8841.../2420263 | Amber lamp alarm Call By Customer Name : Sanoj Singh No : 9816823068 | Task Start | Jai Prakash Associates Ltd. | K.C. Diesel Services - East Sikkim | 46 | Visit pending | OPEN | Prosanjit saha
11 | East | 211646163 | 26-01-2025 15:46 | 30 | 3H.8902.../2420561 | Power Supply issue Call By Customer Name - Khokan Maity Mobile No - 7908490373 | Open | ABIS Exports India Private Limited. . | Gangpur Sales and Services - Bargarh | 65 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das
12 | East | 211641014 | 24-01-2025 19:03 | 20 | GP3.8601.../2420723 | Red Lamp On Alarm Issue Call By Customer Name - Ashish .. Number - 7477737197 | Open | Manisha Enterprise | Revenus Industries Pvt. Ltd. - Howrah | 58 | Today SE will visit site | OPEN | Prosanjit saha
13 | East | 211640033 | 24-01-2025 17:24 | 5.5 | CC1.1013.../2400381 | Starting issue Call By KGD Name :- Alisha Mobile No:-9434823377 | Cancelled | Mr. Monaj singh | K.C. Diesel Services - SILIGURI | 32 | Customer required service no issue in DG | CANCELLED | Prosanjit saha
14 | East | 211643023 | 25-01-2025 13:17 | 125.4 | 4H.8042.C4../2420841 | Low Fuel Level Call By Customer Name :- Rajib Das Mobile No :-8638291760 | Cancelled | National Highways Infra Projects Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 22 | SR cancelled- created by mistake | CANCELLED | Ujjwal Das
15 | East | 211642023 | 25-01-2025 09:53 | 125.4 | 4H.8042.C4../2420713 | FUEL LEAKAGE | Open | POOJA TRADERS | M T Enterprises - Bomdila | 1 | Line rejection - fuel leakage Update pendig | OPEN | Ujjwal Das
16 | East | 211639937 | 24-01-2025 17:09 | 40 | 3H.8951.../2421085 | AMF Panel Issue Call By KGD Name - Komkom Neha Number - 9234456624 | Open | Radheshyam Paswan. | HACS Engineering and Tech Private Limited - Hazaribagh | 37 | No issue in DG running in healthy condition Mail send for cancellation | OPEN | Prabhakar Kumar
17 | East | 211636314 | 23-01-2025 17:12 | 82.5 | 5H.8901.../2420065 | Starting Issue Call By KGD Name - Komkom Neha Number - 9234456624 | Open | Tathastu. | HACS Engineering and Tech Private Limited - Hazaribagh | 75 | Visit Pending | OPEN | Prabhakar Kumar
|  | 211651703 | 28/1/2025 12:28:14 PM | 1500KVA Optiprime | DV2.8508.C4../2420002 & 2420007 | Starting isuue | Open | Anuh Pharma Limited | Transcreek Engineers Pvt. Ltd. - Boisar | LR |  | OPEN
1 | North | 211652125 | 28-01-2025 13:51 | 40 | 3H.8951.../2420045 | Leakage Issue | Task Start | Deep Automation | Paluck Technologies Ltd. - Faridabad | 106 | Check and Found Oil filter damage so oil leakage, because Fuel filter plate touch to the oil filter body due vibration filter was damage, Now remove the Plate & hole was exceed | Closed | Kapil Solanki
2 | North | 211652096 | 28-01-2025 13:47 | 250 | F6.8841.../2320026 | Tripping issue Call By Customer Name :-Sarvesh Mobile No :- 9312907425 | Task Start | Ajanta Cold Storage and General Mills | Paluck Technologies Ltd. - Ghaziabad | 118 | DG reverse phase alarm check Battery charger connection directly given (Under observation) | open | Kapil Solanki
3 | North | 211652084 | 28-01-2025 13:40 | 125.4 | 4H.8041.../2320185 | Starting Issue Call By Customer Name :- Yadav Mobile No :-8368321282 | Task Start | UNIVERSAL CHEMICAL COMPANY | Paluck Technologies Ltd. - Ghaziabad | 144 | Low def level & topup the def & clear the fault code then issue resolve | Closed | Kapil Solanki
4 | North | 211651959 | 28-01-2025 13:20 | 58.5 | T4.8941.../2421074 | Abnormal Sound issue Call By Customer Name :-Saif Mobile No :- 9695327798 | Open | Rural Development Department Uttar Pradesh. | S.S. Enterprises - Chunar - Mirzapur | 50 | Found no any issue in DG | Closed | Sudhir Awasthi
5 | North | 211651949 | 28-01-2025 13:13 | 58.5 | T4.8941.../2421885 | Under Speed Alarm Call By Customer Name - Tiwari No - 9559191222 | Open | Lucknow Generator Wala | S. R Engines Sales And Service - LUCKNOW | 29 | Controller show the under speed alarm then check Crank sensor removed & Clean After issue resolve | Closed | Sudhir Awasthi
6 | North | 211651886 | 28-01-2025 13:02 | 500 | DV8.8501.C4../2420009 | Trip_Genset_Low_Voltage | Task Start | QH. Talbros Private Limited | Paluck Technologies Ltd. - Gurgaon |  | Cancelled-Commercial issue | Cancelled | Kapil Solanki
7 | North | 211651772 | 28-01-2025 12:40 | 30 | 3H.8902.../2320014 | High coolent temperature | Task Start | PAWAN TANAY CHEM PLAST PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar | 599 | Found SPN/FMI 110/0 High coolant tem. Clear the fault code, fuel level 35%, Fan belt loose tightness the same, Exhaust pipe Very long Approx 25Fit, Educate the customer remove the extra exhaust pipe (Last CSP 22/01/2024 Required service) | Closed | Gourav Sharma
8 | North | 211651732 | 28-01-2025 12:36 | 320 | F6.8802.../2420069 | Trip_Genset_Low_Voltage | Task Start | Budhiraja Electricals | Deep Jyoti Electricals and Services - Haldwani | 15 | Jerk loan on the Dg Trial load on step by step then no issue found, Educate the customer kindly donot give suddly more load | Closed | Sudhir Awasthi
9 | North | 211651656 | 28-01-2025 12:21 | 750 | DV2.8501.C4../2420048 | Voltage Fluctuation issue Call By Customer Name :-Satendra Singh Mobile No :-9953173934 | Task Start | St. Mark's Sr. Sec. Public School, | OVN Industries Private Limited - New Delhi | 921.5 | Found radiator was chocked & Tem. Will be raise on 103 Deg. Celcius DG not trip but RPM drop approx 1300__ Service due | Closed | Kapil Solanki
10 | North | 211651585 | 28-01-2025 12:06 | 58.5 | T4.8941.../2420691 | Maintenance due alarm issue Call by customer Name: Dr. DInesh Tiwari Number: 8955049898 | Task Start | Relief Hospital. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 251 | Found maintenance due alarm in emergency on Hospital case Quatation send to the customer for Service (Last service on 4/09/2024) | Closed | Gourav Sharma
11 | North | 211651584 | 28-01-2025 12:06 | 250 | DV8.9840.../2420009 | Starting/Stopping Issue | Task Start | METAFLEX DOORS INDIA PRIVATE LIMITED. | Vidyut Engineers - Noida | 11 | Gas Engine-Found crank sensor other fault and cam sensor sync fault need to be replace the sensors | open | Kapil Solanki
12 | North | 211651487 | 28-01-2025 11:49 | 500 | DV8.8501.C4../2420374 | ECU Amber Lamp On Alarm Call By Customer Name :- BohraSingh Mobile No :- 8860077486 | Task Start | BOHRA RUBBER (P) LTD | Paluck Technologies Ltd. - Faridabad | 11 | Low def level topup the def | Closed | Kapil Solanki
13 | North | 211651424 | 28-01-2025 11:34 | 40 | 3H.8951.../2421706 | Starting/Stopping Issue | Closed | R.G. BUILD WELL ENGINEERS LTD | Paluck Technologies Ltd. - Ghaziabad | 4 | Battery charger connection done from customer end | Closed | Kapil Solanki
14 | North | 211651354 | 28-01-2025 11:21 | 15 | GP3.8501.../2320025 | Starting/Stopping Issue | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | SAM Engineering corporation - Varanasi Cantt. | 76 | Found self negative wire loose tightness the self then start the DG then issue resolve | Closed | Sudhir Awasthi
15 | North | 211651367 | 28-01-2025 11:20 | 40 | 3H.8951.../2320020 | Starting issue Call By Customer Name :- Anup Bajaj Mobile No:- 9999786017 | Task Start | BR. Containers | Paluck Technologies Ltd. - Faridabad | 659 | Battery charger connection removed Connect the charger then main fuel pipe changed required | Closed | Kapil Solanki
16 | North | 211651294 | 28-01-2025 11:08 | 250 | F6.8841.../2420015 | Automation Issue. Call By Customer. Name:- Dushant. Mobile No.:-9259609717 | Task Start | Nestle Cooprative Appartment Group Housing | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 112 | Update pending | open | Kapil Solanki
17 | North | 211651198 | 28-01-2025 11:02 | 58.5 | T4.8941.../2421836 | Automation Issue Call By Customer Name :- Ankit ... Mobile No :- 9643842292 | Task Start | Harish Sir | Vidyut Engineers - Noida | 48.56 | Found Emergency alarm Switch was pressed realease the same, reset the alarm then start the DG then issue resolve | Closed | Kapil Solanki
18 | North | 211650879 | 28-01-2025 09:57 | 125.4 | 4H.8041.../2420914 | Starting Issue Call By Customer Name :- Nawab Ji Mobile No :- 9818989516 | Closed | FINE ENGINEERS AND GENERATORS | Vidyut Engineers - Noida | 32.2 | Found air lock in fuel line, change the copper & remove the air then issue resolve | Closed | Kapil Solanki
19 | North | 211650805 | 28-01-2025 09:33 | 500 | DV8.8501.C4../2420409 | Showing ECU AMBER WARNING every time we start the generator | Task Start | BAJAJ NYLLON AND PLASTIC | Paluck Technologies Ltd. - Faridabad | 17 | Low def level Educate the customer maintain the def level | Closed | Kapil Solanki
20 | North | 211649916 | 27-01-2025 18:27 | 82.5 | 5H.8901.../2420681 | Auatomation issue Call by service dealer name : Ravindra No : 9560263917 | Closed | BEACON ELEVATOR CO PVT LTD | Vidyut Engineers - Noida | 15 | Auto wire loose from contol panel tightness the same then issue resolve | Closed | Kapil Solanki
21 | North | 211649756 | 27-01-2025 17:50 | 20 | GP3.8604.../2420195 | DG ISSUE | Open | Reliance Jio Infocomm Limited | Rajdhani Diesels and Electricals - Barmer |  | Visit pending | open | Sudhir Awasthi
22 | North | 211649258 | 27-01-2025 17:30 | 20 | GP3.8601.../2420643 | DG Not Auto Starting,Please check on urgent basis-506058 | Task Start | ICICI Bank Limited | S.S. Enterprises - Allahabad |  | Under Cancellation- | Cancelled | Sudhir Awasthi
23 | North | 211648454 | 27-01-2025 15:31 | 125.4 | 4H.8041.../2421028 | Starting/Stopping Issue | Closed | Damyaa P. J. Foods P. Ltd. | Deep Jyoti Electricals and Services - Moradabad | 144 | Battery terminal Clean with petroleam jelly & start ok | Closed | Sudhir Awasthi
24 | North | 211648324 | 27-01-2025 15:04 | 20 | GP3.8601.../2320029 | Genset Trip | Closed | Z. N. Enterprises | S.S. Enterprises - Allahabad | 12 | Battery charger connection done from customer end | Closed | Sudhir Awasthi
25 | North | 211648270 | 27-01-2025 14:57 | 30 | 3H.8902.../2420471 | Trip_Genset_Low_Voltage | Open | Shiv Kant Infratech Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Agra |  | Under Cancellation- Sr open by mistake | Cancelled | Sudhir Awasthi
26 | North | 211648231 | 27-01-2025 14:48 | 125.4 | 4H.8041.../2420182 | Starting/Stopping Issue | Closed | Sunil Generators | OVN Industries Private Limited - New Delhi | 352 | Found Distribution box XDM 1C wire loose tightness to be all then issue resolve | Closed | Kapil Solanki
27 | North | 211648057 | 27-01-2025 14:02 | 45 | 3H.8951.../2421380 | Oil leakage problem Email By - KGD Name -VIJAY KUSHWAHA | Closed | VICTOR POWER SOLUTION | Pratap Diesels Pvt. Ltd. - JAIPUR | 19.6 | Oil leakage from turbocharger nut bolt loose tightness the same then issue resolve | Closed | Gourav Sharma
28 | North | 211638659 | 24-01-2025 12:48 | 20 | GP3.8604.../2420198 | Under voltage trip issue | Task Start | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur | 158 | Under voltage now tightness the connection | Open | Sudhir Awasthi
29 | North | 211633969 | 23-01-2025 12:13 | 30 | 3H.8902.../2420633 | DG not starting,dg not working -505177 | Task Start | ICICI Bank | S. R Engines Sales And Service - LUCKNOW | 16 | Update pending | Open | Sudhir Awasthi
30 | North | 211644341 | 25-01-2025 16:13 | 20 | GP3.8601.../2420492 | Red Lamp On Alarm Call By Customer Name :- Balkeash Gurav Mobile No :- 9971176886 | Closed | Kamal Machinery Stores. | S. R Engines Sales And Service - Gorakhpur | 1001 | Update pending | Open | Sudhir Awasthi
31 | North | 211639731 | 24-01-2025 16:23 | 30 | 3H.8902.../2420439 | Starting/Stopping Issue | Closed | Sachin Kumar Gupta | S. R Engines Sales And Service - Mau | 430 | Update pending | Open | Sudhir Awasthi
32 | North | 211631323 | 22-01-2025 16:36 | 20 | GP3.1021.../2420275 | INSTANCE ID:-100777774 SITE ID:-I-UE-FZAD-ENB-0186 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-PRAKASH TIWARI NUMBER:-9696091850 | Closed | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Faizabad | 838 | Under volatge alarm flash the ECU | Closed | Sudhir Awasthi
33 | North | 211644722 | 25-01-2025 17:15 | 400 | DV8.8542.C4../2420051 | Genset Trip | Closed | A. B. E. C. O. Infrastructures Pvt. Ltd. | S.S. Enterprises - Allahabad | 13 | Update pending | open | Sudhir Awasthi
34 | North | 211643220 | 25-01-2025 14:17 | 125.4 | 4H.8041.../2420419 | Starting/Stopping Issue | Closed | Divya Jyoti Jagrati Sansthan | S.S. Enterprises - Allahabad | 289 | Amber lamp on check the panel wiring tightness to be all then found no any alarm | Closed | Sudhir Awasthi
35 | North | 211643154 | 25-01-2025 14:04 | 40 | 3H.8951.../2420728 | Leakage Issue | Closed | SUNIL KUMAR KAUSHIK | R K Engineers - Bijnor | 70 | Coolant recovery box leakage | open | Sudhir Awasthi
36 | North | 211631114 | 22-01-2025 15:48 |  | 4H.8041.../2420974 | FUEL SENSOR CHANGE | Closed | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | LR-1.1 | Update pending | open | Sudhir Awasthi
37 | North | 211642058 | 25-01-2025 10:08 |  | F6.8802.../2420308 | Charging alternator fault alarm | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | LR- | Update pending | open | Sudhir Awasthi
38 | North | 211651974 | 28-01-2025 13:19 | 15 | GP3.8501.../2420509 | AUTO STOPPING ISSUE | Closed | Cliff Computers. | Dynamic Engineering Services - Jalandhar | 63 | Customer raised complaint as Stopping issue in Auto mode but no such issue found on site | Closed | Ved Prakash Gupta
39 | North | 211651499 | 28-01-2025 11:52 | 125.4 | 4H.8041.../2420231 | Urea Issue And Automation Issue Call By Customer Name :- RAHUL ARRORA Mobile No :- 9779785649 | Task Start | Itechnolabs Software Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Zirakpur | 52.12 | SPN/FMI-1761/16 ; AdBlue Level Low,Top-up the same & resove the code,issue resolved | Closed | Ved Prakash Gupta
40 | North | 211650952 | 28-01-2025 10:17 | 40 | 3H.8951.../2420507 | DG Battery Issue,kindly arrange a visit on urgent basis- 505831 | Task Start | ICICI Bank Limited | Suraj Motor Store - Jammu | 89 | Auto Starting issue due to wire for automation in Pannel found loose so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
41 | North | 211649944 | 27-01-2025 18:37 | 125.4 | 4H.8041.../2420306 | Starting/Stopping Issue | Closed | MG BAKERS PVT LTD | Megatron Engineers - Amritsar | 155 | SPN/FMI-1761/16 ; AdBlue Level Low,Top-up the same & resove the code,issue resolved | Closed | Ved Prakash Gupta
42 | North | 211649740 | 27-01-2025 17:44 | 58.5 | T4.8941.../2422479 | Starting Issue Call By Customer Name :-Manjeet Sir Mobile No :- 8950004133 | Closed | NITIKA TEXTILE.. | SAAN Royal Power Solutions Private Limited - Ambala | 20 | Emergency Alarm activated;check the switch found 1h wire for emergency Stop loose so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
43 | North | 211649032 | 27-01-2025 17:01 | 250 | F6.8842.C4../2420013 | ABNORMAL SOUND | Task Start | Arihant Machinery Store | SAAN Royal Power Solutions Private Limited - Sonipat | 70.1 | ECU Malfunction Alarm occurred with Low Voltage ; check & DC Alternator connector found loose on site so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
44 | North | 211648437 | 27-01-2025 15:31 | 58.5 | T4.8941.../2421181 | Error code issue Call By Customer Name :- Amit Jaiswal Mobile No:- 9810141502 | Task Start | Mogh Pharma Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 173.38 | Coolant Leakage found from Radiator ; asked to share the check-sheet for the same | Open | Ved Prakash Gupta
45 | North | 211648403 | 27-01-2025 15:20 | 30 | 3H.8902.../2320174 | Starting/Stopping Issue | Closed | Mr. Raghav | Megatron Engineers - Amritsar | 2 | Starting Issue due to 2A no. wire found loose on Relay Card 12RB1 ;re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
46 | North | 211648138 | 27-01-2025 14:22 | 125.4 | 4H.8041.../2420188 | Genset Trip | Task Start | Aditi Industries | SAAN Royal Power Solutions Private Limited - Rohtak | 125 | Under speed alarm occurred with air locking due to NRV found faulty ; will replace the same by Today | Open | Ved Prakash Gupta
1 | west | 211646891 | 27-01-2025 10:39 | 30 | 3H.8902.../2422229 | DIESEL NOT COME IN PRIMING PUMP FILTER | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 0.36 | Found leakage in fuel pipe ( fuel tank to feed pump ) change the pipe and remove air , issue solved. | closed | Jagdeep saini
2 | west | 211646900 | 27-01-2025 10:38 | 15 | GP3.8501.../2421455 | Starting Issue Email By KGD Name:- Surekha Auti | Closed | Prashant Korbhan Gupta & Seema Prashant Gupta | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 17.35 | Fuel air lock issue at that time open banjo bolt on FIP & start the controller/ engine upto the air remove in fuel & then tight banjo bolt properly. | closed | Jagdeep saini
3 | west | 211646822 | 27-01-2025 10:25 | 320 | F6.8802.../2420178 | Diesel leakage issue Call by : Customer Name : Kuldeep Contact : 8668566570 | Closed | MIMSR MEDICAL COLLEGE | KALA Care Global LLP - Latur | 42 | Diesel filter ring found pinch / pressed so diesel leakage from the ring , open the filter and refitted. | closed | Jagdeep saini
4 | west | 211647526 | 27-01-2025 12:17 | 200 | 6H.8435.../2420150 | Abnormal sound issue Call By Customer Name :- Shree Raj Mobile No:- 9359590364 | Closed | Vikram Infratech Developers Private Limited | Mahalaxmi Diesels - Solapur | 199 | Belt tension found loose so tight the belt, issue solved | closed | Jagdeep saini
5 | west | 211647467 | 27-01-2025 12:13 | 25 | GP3.8702.../2421254 | Starting Issue Call By Customer Name :- Mobile No :- | Task Start | ICICI Bank Limited | Shree Engineering Service - Jabalpur | 3 | Controller not ON beacuse MCB in off condition | closed | vijay patil
6 | west | 211647459 | 27-01-2025 12:08 | 40 | 3H.8951.../2421604 | Starting Issue Call By KGD Name :- Ramish Chavahan Mobile No :-9016803464 | Closed | APPLE AAWASS | Unique Techno Services Pvt Ltd. - Ahmedabad | 10.22 | dg start in auto in presence of mains changed the Mains voltage setting in controller-180V. | closed | Amit sandlya
7 | west | 211648136 | 27-01-2025 14:16 | 25 | GP3.8702.../2422032 | ENGINE NOT START | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Starter motor found faulty need to change the starter . | Closed | Jagdeep saini
8 | west | 211648107 | 27-01-2025 14:11 | 5.5 | CC1.1013.../2400693 | starting problem | Task Start | Power Link.. | Mahalaxmi Diesels - Goa | 0 | During commiossing found oil level was low need to top up oil . | Closed | Jagdeep saini
9 | west | 211647904 | 27-01-2025 13:16 | 30 | 3H.8902.../2420716 | DG Starter Problem | Task Start | ATC Telecom Infrastructure Private Limited | Mahalaxmi Diesels - Kankavali | 70 | 2D Fuse between distribution box to control panel +Ve supply found blown , placed new fuse issue solved. | Closed | Jagdeep saini
10 | west | 211646088 | 26-01-2025 13:32 | 200 | 6H.8435.../2420057 | High Temperature issue Call By Customer Name :-Rushikesh Mobile No :-9022188163 | Cancelled | INTOFINITY PROMOTERS PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | cancelled |  | Jagdeep saini
11 | west | 211650845 | 28-01-2025 09:51 | 30 | 3H.8902.../2421448 | Starting/Stopping Issue | Task Start | GAURAV POULTRY FARM | Shree Engineering Service - Raipur | 159 | Mains phase reverse alarm shown in controller , change the phase sequence and issue resolved. | Closed | vijay patil
12 | west | 211647647 | 27-01-2025 12:38 | 750 | DV2.8501.C4../2420099 | ISSUE | Task Start | SHREE GANESH ENGINEERING WORKS UNIT I | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | DG not get sync. Checked the continuity from 615 & 620 to ECU found ok. And customer side variable voltage was receiving from terminal and ECU wiring connector. So interchanged the ECU from another engine ECU and problem solved. | closed | Jagdeep saini
13 | west | 211651088 | 28-01-2025 10:36 | 58.5 | T4.8941.../2421427 | Fule issue | Open | AMRUT COLLECTION | Mahalaxmi Diesels - Kolhapur | 96 | Fuel level not showing properly , tank 100% but still it shows 80 %. | closed | Jagdeep saini
14 | west | 211650980 | 28-01-2025 10:19 | 58.5 | T4.8941.../2421962 | abnormal sound Issue Email By - KGD Name -Umesh Saraf | Open | Tara Towers Apartments Condominium | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 3 | Canopy site issue loose bolt ion canopy , tight the bolt. | closed | Jagdeep saini
15 | west | 211650900 | 28-01-2025 10:00 | 500 | DV8.8501.C4../2420419 | Starting/Stopping Issue | Task Start | MEYER ORGANICS PVT. LTD. | Transcreek Engineers Pvt. Ltd. - Thane | 13 | SPN-3218 FMI-20, SPN-523582 FMI-0 connect ikonnoct and clear DTC . Under observation | closed | Jagdeep saini
16 | west | 211650744 | 28-01-2025 07:43 | 40 | 3H.8951.../2420446 | Sound/Vibration Issue | Task Start | SHREEKAR CONSTRUCTION | Unique Techno Services Pvt Ltd. - Hathijan | 553 | Exhaust manifold found broken and also found oil leakage on breathder pipe so fitted the pipe propetly need to change exhaust manifoled | open | Amit sandlya
17 | west | 211648161 | 27-01-2025 14:24 | 50 | T4.8941.../2422788 | OIL LEAKAGE OBSERVED FROM GALLERY TO PUMP | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | observed oil lekage from oil supply pipe benjo fitted on main gallery so removed benoj observed washer not fitted properly change the washer and take trial. | closed | Jagdeep saini
18 | west | 211651703 | 28/1/2025 12:28:14 PM | 1500KVA Optiprime | DV2.8508.C4../2420002 & 2420007 | Starting isuue | Open | Anuh Pharma Limited | Transcreek Engineers Pvt. Ltd. - Boisar | LR | Engine starting isuue. Error code-SPN:157/FMI:3 & SPN:7026/FMI:5) Continuity from IMV to ECU was checked, which was found to be OK, engineer replaced the common rail, but problem persisted. Checked and found that ECU 8 number chamber connector was not fitted properly. | OPEN | Jagdeep saini
1 | East | 211648154 | 27-01-2025 14:36 | 82.5 | 5H.8901.../2420364 | Starting/Stopping Issue | Task Start | M/s. Landmark Engineering. | M T Enterprises - Bomdila | 64 | Customer,s Adblue tank Cap key were lost so cap replaced by new one and there was low adblue level alarm so topup the adblue then cleared fault code issue resolved | CLOSED | Ujjwal Das
2 | East | 211646328 | 26-01-2025 20:45 | 15 | GP3.8501.../2420615 | Load Issue Call By Customer Name ;- Bittu Soni Mob No ;- 8794016784 | Open | M/S Marcofed Heningkunhlwa | Hibreed Engineering Pvt. Ltd. - Jorhat | 148 | Visit pending | OPEN | Ujjwal Das
3 | East | 211645260 | 25-01-2025 21:25 | 20 | GP3.8601.../2421368 | Trip_Genset_Low_Voltage | Open | Akuvu Powerline. | Hibreed Engineering Pvt. Ltd. - Jorhat | 2.8 | today SE will visit. | OPEN | Ujjwal Das
4 | East | 211644289 | 25-01-2025 16:07 | 5.5 | CC1.1013.../2400016 | Starting issue and Preventive Maintenance Call By Customer Name :- Shakti Kumar Mobile No :- 6294815565 | cancelled | East Coast Railway Andhra Pradesh | HACS Engineering and Tech Private Limited - Dhanbad |  | Problem resolved in PM visit - | CANCELLED | Prabhakar Kumar
5 | East | 211642023 | 25-01-2025 09:53 | 125.4 | 4H.8042.C4../2420713 | FUEL LEAKAGE | Open | POOJA TRADERS | M T Enterprises - Bomdila | 1 | Found coummunication failure in GCU, so checked ECU to GCU wire continuity found OK, under observation | OPEN | Ujjwal Das
6 | East | 211636314 | 23-01-2025 17:12 | 82.5 | 5H.8901.../2420065 | Starting Issue Call By KGD Name - Komkom Neha Number - 9234456624 | Open | Tathastu. | HACS Engineering and Tech Private Limited - Hazaribagh | 75 | Controller was not getting on, so checked battery voltage found ok then on further checking found DC mcb(8F1) 2B1 wire found loose after tightening issue resolved. | OPEN | Prabhakar Kumar
7 | East | 211653330 | 28-01-2025 15:56 | 125.4 | 4H.8042.C4../2420883 | Red Lamp Alarm Issue Call By Customer Name - UMESH SINGH Number - 8252327072 | Open | CIRCUIT HOUSE KATIHAR | Globalline India Services Private Limited - Purnia |  | Today SE will visit. | OPEN | Prabhakar Kumar
8 | East | 211653270 | 28-01-2025 15:45 | 15 | GP3.8501.../2420474 | Genset Trip | Open | SAVEER BIOTECH LTD.. | M T Enterprises - Bomdila | 51 | DG fail to start showing coolant temp sensor alarm, coolant temp sensor issue, need to replace as it,s continuity was OK from the ECU connector | OPEN | Ujjwal Das
9 | East | 211651646 | 28-01-2025 12:17 | 20 | GP3.8604.../2420174 | DG Air locking. | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Muzaffarpur |  | Visit pending | OPEN | Prabhakar Kumar
10 | East | 211650906 | 28-01-2025 10:03 | 250 | F6.8841.../2420332 | Leakage Issue | Task Start | Bishop Westcot School | HACS Engineering and Tech Private Limited - Ranchi |  | Today SE will visit site | OPEN | Prabhakar Kumar
11 | East | 211650860 | 28-01-2025 09:51 | 15 | GP3.8501.../2420999 | Amber lamp alarm issue Call By Customer Name :- Subhodh Kumar Mobile No:- 9798182036 | Completed | LALL CONSTRUCTION INDIA LTD | Globalline India Services Private Limited - Motihari | 45 | found 244/8 LOP open fault code so checked the LOP wire connection and found wire were losse connected on LOP so reconnected properly issue resolved. | CLOSED | Prabhakar Kumar
12 | East | 211653471 | 28-01-2025 16:25 | 15 | GP3.8501.../2421431 | Excessive Smoke | Task Start | PURBASHA SAHA | Revenus Industries Pvt. Ltd. - Nandakumar | 32 | Today SE will visit site | OPEN | Prosanjit saha
13 | East | 211653002 | 28-01-2025 15:06 | 10 | GP3.8301.../2420146 | Abnormal Sound | Task Start | ICICI Bank Limited | Revenus Industries Pvt. Ltd. - Nandakumar | 23 | Visit Pending | OPEN | Prosanjit saha
14 | East | 211651480 | 28-01-2025 11:46 | 58.5 | T4.8941.../2420564 | Maintenance Due Alarm Call By Customer Name :- Romin Rabha Mobile No :- 8974600877 | cancelled | S. G. L. Enterprise | Gangpur Sales and Services - Puri | 54 | No issue in DG SR created only for maintenance alarm, cancellation mail send to Helpdesk. | CANCELLED | Ujjwal Das
15 | East | 211651309 | 28-01-2025 11:09 | 30 | 3H.8902.../2420054 | Starting/Stopping Issue | Closed | ROY & CO | Revenus Industries Pvt. Ltd. - Barasat | 32 | Customer required service no issue in DG | CLOSED | Prosanjit saha
16 | East | 211650760 | 28-01-2025 08:34 | 30 | 3H.8902.../2420097 | Starting issue Call by customer Name: Raj Laxmi Number: 7978577106 | Task Start | Rajlaxmi Nanda | Gangpur Sales and Services - Subarnapur | 18 | Update Pending | OPEN | Ujjwal Das
17 | East | 211647475 | 27-01-2025 12:15 | 160 | 6H.8475.../2420162 | Starting problem | Open | Amma engineering | Gangpur Sales and Services - BHUBANESWAR | 41 | SE found low adblue level fault code on Ikonnect after topup cleared DTC issue resolved. | CLOSED | Ujjwal Das