## Apr 24
Sr no | Incident Id | Creation_Date | KVA Rating | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Running Hrs | Observation | Incident Status | ASM Name
1 | 210594091 | 2024-01-04 15:32 | 25 | GP3.8702.../2320018 | Starting Issue Call By Customer Name :- Navpreet Singh Mobile No :- 9811420154 | Closed | Tanu Engineering Products Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 3 | DG in stop mode, Just put in Mannual mode & Restart controller, Issue resolved. | Closed | Kapil Solanki
2 | 210593919 | 2024-01-04 14:50 | 500 | DV8.8501.C4../2320010 | Automation issue Call By: Customer Name :Ankush No :7524987246 | Closed | EA TEC ENGINEERING SOLUTION | Espiem Engines & Machines (P) Limited - KANPUR | 8 | SPN/FMI: 516166/0, reset the DTC also Dg starting in Auto mode without Auto sensing (Changed Deepsea port 49 to 50), Now DG is running is running OK. | Closed | Sudhir Awasthi
3 | 210593870 | 2024-01-04 14:47 | 160 | 6H.8475.../2420021 | ENGINE STARTING ISSUE DUE Email By - Service Dealer Name -SUNITA | Closed | S. R. V. Industries | R K Engineers - Meerut | 11 | Coolant over-flow from Reservior tank as Customer top-up itself, Educated Customer to maintain b/w L & H mark of reservior. | Closed | Sudhir Awasthi | SD logged wrong complaint
4 | 210593791 | 2024-01-04 14:00 | 25 | GP3.8702.../2320025 | Auto Starting Issue & Battery Voltage Issue Email By Service Dealer Name:-PRITI OZA | Closed | Ind Spinx Precision Limited (Unit-B) | Royal Power Solutions - Zirakpur | 15.57 | Starting issue due to Discharged Battery, battery charger functioning ok, Checked Specific gravity found Low in All Cell (11.8 to 12.2), DG up with Float Battery & Sent defective Battery to TGY team. | Open | Ved Gupta | Awaited for vendor report
5 | 210593596 | 2024-01-04 12:47 | 160 | 6H.8475.../2320012 | Under Speed Alarm Call By Customer Name:-Dharam Pal Singh Number:-9887007215 | Open | FLEXIPOL FOMAS PVT LTD | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Previous dealer has terminated so there is Men power issue. | Open | Gourav Sharma | SD visist pending
6 | 210593546 | 2024-01-04 12:35 | 320 | F6.8802.../2320080 | Self Load issue Call By Customer Name : Rahul kumar Mobile No :9593182067 | Closed | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 91.48 | Customer have two engine sets one is CPCB 4+ and second one is fire fighting, customer complaints are regarding fire fighting but SR open for CPCB 4 by mistakenly . | Closed | Kapil Solanki | Update required
7 | 210593542 | 2024-01-04 12:35 | 125.4 | 4H.8041.../2320163 | load issue call by customer name Rajeev no 8459775078 | Closed | Panchachuli Sehkari Aavak Samiti | Vidyut Engineers - Noida | 27 | Customer motor running in reverse direction, Just reconnect R Y B wire sequentially, Issue resolved. | Closed | Kapil Solanki | Update required
8 | 210593544 | 2024-01-04 12:35 | 125.4 | 4H.8041.../2420027 | Oil Leakage Issue Call By Customer Name :Manoj Mobile No :7065887070 | Task Start | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 376 | Oil leakage issue from flywheel end ,checked and found leakage from oil seal, change the same issue resolved. | Closed | Kapil Solanki | Details required
9 | 210593259 | 2024-01-04 11:16 | 125.4 | 4H.8041.../2420050 | Red Light On alarm issue Call by customer Name : Harvind Kumar Number:8076404542 | Closed | International Automotive Components | Paluck Technologies Ltd. - Faridabad | 38.16 | SPN/FMI: 516166/0 code was shown , clear the DTC issue resolved. | Closed | Kapil Solanki
10 | 210593158 | 2024-01-04 10:50 | 750 | DV2.8501.C4../2320024 | Emergency stop alarm issue Call By Service Dealer Name : Deepak Kumar Number :7027820048 | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 112.3 | Customer complaint about Emergency stop alarm issue.. Further engineer visited the site and found the canopy emergency switch on by the customer, guided the customer about the same issue resolved. After that checked DG on load but DG was tripping in 10 min. then checked the relay and found 15RB1 relay was malfunctioning , replace the relay card issue resolved.Checked DG on load(30 min ) found ok but kept under observation. | Closed | Kapil Solanki | Update requred
11 | 210591991 | 31-03-2024 17:30 | 125.4 | 4H.8041.../2320129 | Starting issue Call by Customer Name :-Manoj .. Number :-9711995052 | Open | MANOJ KUMAR | Vidyut Engineers - New Delhi |  | Emergency switch on by customer, Telephonically resolved, SR Cancelled | cancelled | Kapil Solanki
12 | 210590701 | 31-03-2024 14:01 | 125.4 | 4H.8041.../2320059 | Starting Issue Call By Customer Name:Chandrdev Number:9643819750 | Closed | Sudh Investments Private Limited | Vidyut Engineers - Noida | 165.31 | SPN/FMI: (1761/18), (1761/14), low DEF level @1% alarm was shown top up the DEF and clear the DTC issue resolved also no Fuel delivery from e-feed Pump, replaced the same, issue resolved. | Closed | Kapil Solanki
13 | 210590654 | 31-03-2024 13:38 | 57 | T4.8941.../2320278 | Voltage Issue Call By Customer Name :- Ashu ... Mobile No :- 9911289566 | Task Start | Maa Vaishno Power System. | Paluck Technologies Ltd. - Ghaziabad |  | Previous dealer has terminated so there is Men power issue. | Open | Kapil Solanki | Visit pending. Update required
14 | 210590368 | 31-03-2024 10:48 | 320 | F6.8802.../2320080 | Canopy Door Issue & Emergency Power Off Issue Call By Customer Name : Rahul kumar Mobile No :9593182067 | Closed | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 90.52 | SPN/FMI: 3031/13, 1761/16, 5461/8 code was shown clear the DTC issue resolved, Need to update Dummy file | Closed | Kapil Solanki | CAL file update
15 | 210589672 | 30-03-2024 17:46 | 500 | DV8.8501.C4../2320055 | AUTOMATION ISSUE Email By - Service Dealer Name -Madan Chhimpa | Closed | NIIT LEARNING SYSTEMS LIMITED | Paluck Technologies Ltd. - Gurgaon | 14 | SR open for synchronization.(500 & 320 KVA DG) | Closed | Kapil Solanki
16 | 210589292 | 30-03-2024 17:24 | 125.4 | 4H.8041.../2420090 | Starting Issue Call By Customer Name :- Divakur Thakur Mobile No :- 9818683289 | Closed | Metro Electric Services | Vidyut Engineers - Noida | 2.98 | DG was tripping due to Under speed alarm checked the fuel line found OK. then reprograme the GCU issue resolved.( Genset running in only override condition) | Closed | Kapil Solanki
17 | 210589064 | 30-03-2024 16:35 | 160 | 6H.8475.../2420020 | Charging Alternator Shaft Broken Email By - Customer Name - Krishan | Cancelled | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad |  | Duplicate SR on same Asset, | cancelled | Kapil Solanki
18 | 210588719 | 30-03-2024 15:56 | 100 | 4H.8041.../2320001 | Starting Issue Call by customer Name ; Manish Kumar Number ; 6239424498 | Closed | SR. Power Engineers | Vidyut Engineers - Noida | 39.37 | SPN/FMI : 1761/16 ( low DEF level) & also 516166/0 &920/5 DEF level @ 40%, Reset DTC Reset DTC, educated customer, issue resolved. | Closed | Kapil Solanki
19 | 210588617 | 30-03-2024 15:44 | 25 | GP3.8702.../2320018 | Starting Issue Call By Customer Name :-Navpreet Singh Mobile No :9811420154 | Cancelled | Tanu Engineering Products Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Customer not available at site, SR cancelled. | cancelled | Kapil Solanki | Updates required
20 | 210588161 | 30-03-2024 13:53 | 320 | F6.8802.../2320024 | Maintenance Due Alarm Issue Call By Customer Name :Kali Shankar Warma No : 9871170836 | Closed | KLK. Venture Pvt. Ltd. | Vidyut Engineers - Noida | 46.35 | Maintenace due alarm, Just reset the same. | Closed | Kapil Solanki | Updates required
21 | 210587706 | 30-03-2024 12:13 | 160 | 6H.8475.../2320030 | Belt to be Change Email By Service Dealer Name:-Shiv | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 44.3 | Charging Alternator I Bolt & mounting bolt in broken condition and also v belt broken due to I bolt broken replaced affected parts, issue resolved. | Closed | Kapil Solanki
3 | 210608335 | 2024-02-04 17:13 | 40 | 3H.8951.../2320024 | AMF panel issue. Email By Service dealer Name:-akash | Task Start | GENESIS ENTERPRISES PVT. LTD. | Espiem Engines & Machines (P) Limited - Aligarh | 144 | Repeated loose connection at XDBK connector, Panel replacement was decided, which is replaced now. | Closed | Sudhir Awasthi
4 | 210608116 | 2024-02-04 16:17 | 160 | 6H.8475.../2320035 | Preventive Maintenance Call By Customer Name :-Jyoti Mobile No :-9717281355 | Open | PUSHPANJALI HOSPITAL | OVN Industries Private Limited - New Delhi |  | SR generated by Customer for PM, Clubbed in CSP SR, Mail drop for SR cancellation. | cancelled | Kapil Solanki
5 | 210607563 | 2024-02-04 15:41 | 160 | 6H.8475.../2320014 | Abnormal Issue Call By Â Customer Name :-Ram Das Mobile No :-9012533754 | Task Start | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 74 | Customer complained about abnormal sound issue.. Further engineer visited the site and found the V belt was loose , tighten the same issue resolved. | Closed | Sudhir Awasthi | Belt replacement. Circular for field.
6 | 210607242 | 2024-02-04 13:47 | 57 | T4.8941.../2320032 | Fuel Leakage Email By - Service Dealer Name -SURESH SHARMA | Task Start | Malik Sir | Vidyut Engineers - New Delhi |  | Customer complaint about fuel leakage issue…further engineer visited the site and found the tank was overfilled.. Educated the customer about the same.. And mail dropped for SR cancellation. | cancelled | Kapil Solanki
7 | 210606288 | 2024-02-04 13:02 | 400 | DV8.8542.C4../2320007 | DG Set ECU Alarm issue eMAIL BY OEM Name Sanjay Rajyan ; | Open | BPCL Jaipur | Pratap Diesels Pvt. Ltd. - JAIPUR |  | No update received yet.. Visit pending. | Open | Gourav Sharma
8 | 210605711 | 2024-02-04 11:53 | 500 | DV8.8501.C4../2320084 | Trip_Genset_Low_Voltage | Task Start | KPH. Fabrics Pvt. Ltd | Paluck Technologies Ltd. - Faridabad | 20 | SPN/FMI :1761/15 ( low DEF level @3 & 5 % )top up the same and clear the DTC .and also (633/3) clear the DTC issue resolved. | Closed | Kapil Solanki
9 | 210605409 | 2024-02-04 11:41 | 320 | F6.8802.../2320061 | Abnormal Issue Call By Customer Name :-Sushil Mobile No :-8860089233 | Task Start | Rai Indutrial Power Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 17 | Customer complaint about abnormal issue , engineer visited site found no issue.. DG running ok. | Closed | Kapil Solanki
10 | 210604608 | 2024-02-04 09:52 | 125.4 | 4H.8041.../2420041 | Starting issue Call by Customer Name : Prashant . Number : 9911093925 | Task Start | R.K VIDYUT CONTROL | Paluck Technologies Ltd. - Gurgaon |  | SR generated on wrong Engine, SR cancelled. | Open | Kapil Solanki
S.no | 210604431 | 2024-02-04 07:30 | 125.4 | 4H.8041.../2320090 | Starting Issue Call By - Customer Name - Ritesh Kumar No. - 7042659373 | Closed | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi | 646 | Air lock issue due to Electric feed pump T socket O ring was damaged,change the same issue resolved. | Closed | Kapil Solanki
1 | 210602025 | 2024-01-04 19:21 | 125.4 | 4H.8041.../2320108 | Red Lamp Alarm Issue Call By Customer Name :-VIJAY KUMAR Mobile No :-9829973147 | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR | 35.32 | SPN/FMI: 1761/16 ( low DEF level @ 47 %) top up the same, clear the DTC issue resolved. | Closed | Gourav Sharma
3 | 210610449 | 2024-03-04 12:40 | 750 | DV2.8501.C4../2420006 | Ambar lamp on alarm issue call by Customer Name ; Sachin Kumar Number ; 9931028639 | Open | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida | 20.43 | Low DEF level @ 49%, Top up the same, Issue resolved. | Closed | Kapil Solanki
4 | 210610188 | 2024-03-04 12:10 | 750 | DV2.8501.C4../2320048 | Maintenance due Alarm Call By Customer Name :-Akash Mobile No :-8273237145 | Open | Jai Mata DI. Generator Service | Vidyut Engineers - Noida | 10.2 | Customer complaint regarding servicing of DG… | Closed | Kapil Solanki
5 | 210609839 | 2024-03-04 10:42 | 125.4 | 4H.8041.../2320039 | Starting issue Email By Service dealer Name:-Sonu Rai | Task Start | R.K VIDYUT CONTROL | Paluck Technologies Ltd. - Gurgaon | 337 | Multiple error code was shown , checked and found ECU not getting 12 volt supply due to distribution box ( XDBK2 2A1 wire) was in loose condition rectified the same issue resolved.but again 3031/14 & 5461/0 code was shown flashed the Dummy callibration file issue resolved. | Closed | Kapil Solanki
6 | 210609445 | 2024-03-04 09:19 | 125.4 | 4H.8041.../2320202 | Tripping and Heating Issue Call By Customer Name :-Narendra Kumar Mobile No :-9416351065 | Closed | Eden Garden | M/s OM Diesels Pvt. Ltd. - Rohtak | 52 | SPN/FMI: 4375/11 ( Ad blue pump flt open in DM1 )& ( 7600/4 Adblue back flow pump SCG Err in DM 2 ) was shown, checked and found supply module connector was in damaged condition, refix the same and clear the DTC issue resolved. | Closed | Kapil Solanki
S.no | 210606288 | 2024-02-04 13:02 | 400 | DV8.8542.C4../2320007 | DG Set ECU Alarm issue eMAIL BY OEM Name Sanjay Rajyan ; | Open | BPCL Jaipur | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Previous dealer has terminated so there is a man power issue. | Open | Gourav Sharma | Visit pending
1 | 210610571 | 2024-03-04 13:10 | 160 | 6H.8475.../2420006 | Amber lamp On Alarm Issue Call By Customer Name :-Ram Niwas Mobile No :-9654825512 | Task Start | India Shine Technologies | Paluck Technologies Ltd. - Faridabad | 96.2 | Multiple error codes were shown related to DEF level level checked and found 0 % DEF top up & educated the customer about the same issue resolved. | Closed | Kapil Solanki
3 | 210615763 | 2024-04-04 18:27 | 320 | F6.8802.../2320051 | Starting Issue Email By Customer Name:-Jeet Singh | Open | Sri Dwarkadheesh Polymers Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | visit pending.. | Open | Gourav Sharma | Update pending
4 | 210615313 | 2024-04-04 17:01 | 125.4 | 4H.8041.../2420124 | Starting Issue Email By - KGD Name - Ashutosh Kumar Singh | Task Start | Venus CGHS. Ltd. | OVN Industries Private Limited - New Delhi |  | DG was tripping due to Under speed alarm,checked the fuel line found OK.running in only over ride condition.today engineer on site for reprogramming the GCU.. | Open | kapil Solanki
5 | 210613874 | 2024-04-04 15:50 | 200 | 6H.8435.../2320032 | Voltage Issue Email By - Service Dealer Name -Mayur Vira | Open | Oil India Limited | Rajdhani Diesels and Electricals - Jodhpur |  | visit pending.. | Open | Gourav Sharma
6 | 210613585 | 2024-04-04 14:56 | 125.4 | 4H.8041.../2320134 | Fuel leakage issue Call By customer Name: Ramkumar . Number: 9917556807 | Open | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar |  | visit pending.. | Open | Sudhir Awasthi
7 | 210613247 | 2024-04-04 13:23 | 57 | T4.8941.../2320014 | Starting issue Call By Customer Name: Sunil No: 9811105868 | Task Start | Goel Selection | OVN Industries Private Limited - New Delhi | 2.52 | SPN/FMI:110/3 Coolant temp -14 degC showing on ikonnect ,coolent tem female connector loose ( all mention in PIR) issue resolved.kept in underobservation for two days | Open | Kapil Solanki
8 | 210613105 | 2024-04-04 12:57 | 125.4 | 4H.8041.../2420102 | DG starting complaint. Email By-Customer Name:- Ashutosh Kumar Singh | Task Start | Master Electric Store | OVN Industries Private Limited - New Delhi | 2.6 | DG was running in only override condition,reprogramme the same issue resolved. | Closed | Kapil Solanki | QS Will check and confirm by monday
9 | 210613069 | 2024-04-04 12:46 | 40 | 3H.8951.../2320059 | Diesel Leakage Issue Call By: Customer Name :Kishan Pal No :9910941459 | Task Start | Shiva Cares HP. Petrol Pump | Paluck Technologies Ltd. - Faridabad | 77 | fuel leakage due to leak off pipe lock was in open condition rectified the same issue resolved. | Closed | Kapil Solanki
10 | 210612730 | 2024-04-04 11:51 | 125.4 | 4H.8041.../2420124 | Starting Issue Call By Service Dealer Name :- Devish Mobile No :- 9958999594 | Closed | Venus CGHS. Ltd. | OVN Industries Private Limited - New Delhi | 2.35 | DG was tripping due to Under speed alarm,checked the fuel line found OK.running in only over ride condition.. | Closed | Kapil Solanki | Double entry
11 | 210612238 | 2024-04-04 10:07 | 125.4 | 4H.8041.../2320004 | Display Issue Call by Customer Name : Indersen Yadavji Number:8826817371 | Closed | ARIHANT INDUSTRIAL EQUIPMENT | Vidyut Engineers - New Delhi | 88 | Customer was not aware, how to check the fuel percentage in GCU so that SR open. Educated the customer about the same.. | Closed | Kapil Solanki
12 | 210612061 | 2024-04-04 09:13 | 500 | DV8.8501.C4../2320033 | Starting Issue And Cranking Issue Call By Customer Name : -Subhas Sharma Mobile No :-9306952708 | Closed | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 73 | Starting issue for now DV8.1234/123456_v2 file flased,as there was no any alarm in the GCU as well as event log. | Closed | Kapil Solanki
S.No | 210611826 | 2024-03-04 23:27 | 82.5 | 5H.8901.../2320004 | Starting Issue Call By Customer Name:Akash Bhatia Number:9873252550 | Closed | Klikk Pack Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 18 | Starting issue due to battery discharged,battery charger was not connected,rifited the same issue resolved. | Closed | Kapil Solanki | 4375/3- SM pressure
1 | 210611049 | 2024-03-04 15:41 | 125.4 | 4H.8041.../2320180 | Diesel Leakage Issue Call By Customer Name :-Ramesh Mobile No :-8506043972 | Closed | C. M. Infrastructure Pvt. Ltd. | Vidyut Engineers - Noida | 27.1 | SPN/FMI:516166/0 (ECU Internal fault),clear the DTC issue resolved. | Closed | Kapil Solanki
3 | 210617472 | 2024-05-04 12:38 | 750 | DV2.8501.C4../2320044 | Tripping issue & Display Issue Call By: Customer Name :Raghvendra Shukla No :9717068188 | Task Start | Paharpur Cooling Towers Ltd. | Paluck Technologies Ltd. - Ghaziabad | 72 | Fuel reading was wrong shown in GCU,due to the fuel sensor was stuck on 80 % does not reach 100 % , remove the fuel sensor,and refittied the same issue resolved. | Closed | Kapil Solanki
4 | 210617392 | 2024-05-04 12:13 | 125.4 | 4H.8041.../2320083 | Starting Problem Call by : Customer Name : Raj kumar Contact : 7760922592 | SR Status | AKASH GENERATOR SERVICES | Vidyut Engineers - New Delhi | 505 | Starting issue due to the E- feed pump NRV was dusty, clean and refitted the same issue resolved. | Closed | Kapil Solanki
5 | 210617187 | 2024-05-04 11:38 | 250 | F6.8841.../2320012 | Red Light Alarm Issue Call By Customer Name :- Pramod Kumar Mobile No :- 9311718729 | Task Start | VAISHNO INDUSTRIES PVT LTD | Paluck Technologies Ltd. - Faridabad | 26.3 | SPN/FMI 1761/16( Low DEF level @ 48%), Just topup the DEF & educated Customer about the same ,and also fuel level not showing on controller, found fuel level sensor connector was in loose condition, removed the connector and refitted the same issue resolved. | Closed | Kapil Solanki
6 | 210616865 | 2024-05-04 10:56 | 15 | GP3.8501.../2320041 | Starting issue Email By Service dealer Name:-Bharat Dixit | Task Start | Growmore Signnage LLP. | Espiem Engines & Machines (P) Limited - Agra | 20 | Earlier DG tripping with Emergency stop & Engine Crank poistion alarm, Replced Emergency switch & LOP Switch, Issue resolved. | Closed | Sudhir Awasthi | Emergency switch details.
7 | 210616847 | 2024-05-04 10:50 | 82.5 | 5H.8901.../2320084 | Automation Issue Call By Customer Name :- Nandkishor ... Mobile No :- 9310826615 | Task Start | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi | 141 | Low DEF level @ 30 %, Top up the same educated Customer also SPN/FMI 516166/0, just reset DTC & kept under observation (as Customer never done Hot shut down SD team having doubt on Canopy Emergency switch. | Closed | Kapil Solanki | check KRM data and show 516166 fault code and 1761 /14 and 16.
8 | 210616842 | 2024-05-04 10:50 | 82.5 | 5H.8901.../2320105 | Red Light Alarm Call By Customer Name: Sanjay No: 9058125516 | Task Start | ST. Francisi Hospital | R K Engineers - Muzaffarnagar | 3 | SPN/FMI:516166/0 (ECU Internal fault),clear the DTC issue resolved. | Closed | Sudhir Awasthi
9 | 210616456 | 2024-05-04 07:03 | 125.4 | 4H.8041.../2420084 | Trip_Genset_Low_Voltage | Task Start | Aggaarwal Art & Pattern Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 14 | Previously flashed 4H.681.02.0.PR File but did not set the preheat and preheat time , just set preheat output and preheat time | Closed | Kapil Solanki
10 | 210615763 | 2024-04-04 18:27 | 320 | F6.8802.../2320051 | Starting Issue Email By Customer Name:-Jeet Singh | Open | Sri Dwarkadheesh Polymers Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | As discussed with Customer , DG Voltage drops while load is given and this is due to Block load of Compressor and Sequence of Operation is already guided while DG Commissioning. | cancelled | Gourav Sharma
11 | 210615313 | 2024-04-04 17:01 | 125.4 | 4H.8041.../2420124 | Starting Issue Email By - KGD Name - Ashutosh Kumar Singh | Task Start | Venus CGHS. Ltd. | OVN Industries Private Limited - New Delhi | 2.52 | DG was starting in only override condition, change the crank start delay (0 to 3 sec ) in GCU issue resolved. | Closed | Kapil Solanki | First visit of B/D Warranty SR and before does not find any type SR
12 | 210613874 | 2024-04-04 15:50 | 200 | 6H.8435.../2320032 | Voltage Issue Email By - Service Dealer Name -Mayur Vira | Task Start | Oil India Limited | Rajdhani Diesels and Electricals - Jodhpur | 70 | SPN/FMI: 1761/16 (low DEF level @48%) ,top up the same and educated the customer about same…and also 3218/18, 516166/0 checked and found nox sensor connector loose, removed the connector and refitted the same issue resolved. | Closed | Gourav Sharma | KRM check
13 | 210613585 | 2024-04-04 14:56 | 125.4 | 4H.8041.../2320134 | Fuel leakage issue Call By customer Name: Ramkumar . Number: 9917556807 | Open | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 225.7(104.3 KRM Show hours ) | Fuel leakage from loose main fuel filter, tighten the same issue resolved. | closed | Sudhir Awasthi | cc date-12/12/2023 first csp date-11-03-2024
14 | 210619378 | 2024-05-04 18:58 | 125.4 | 4H.8041.../2420125 | Starting Issue Call By: Customer Name :Sham No :9971438718 | Open | SR. Power Engineers | Vidyut Engineers - Noida |  | Emergency stop alarm was shown,due to the canopy emergency switch pressed, guided to the customer on call issue resolved.. Mail dropped for SR cancellation. | cancelled | Kapil Solanki
S.no | 210619157 | 2024-05-04 17:46 | 160 | 6H.8475.../2420020 | Amber Lamp alarm Issue Call By: Customer Name :Sunil Khanduja No :9318463928 | Closed | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad | 29 | SPN/FMI: 1761/16 ( low DEF level @ 48 % ) top up and educate the customer about the same issue resolved. | Closed | Kapil Solanki
1 | 210618808 | 2024-05-04 17:16 | 500 | DV8.8501.C4../2320050 | Trip_Genset_Low_Voltage | Task Start | FORECH INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 79.8 | SR generated due to KRM.. Further engineer visited site and found DG was tripping due to under voltage alarm,checked and found fuel line pipe was bend correct the same also main suction fuel line bolt was loose condition, retighten with teflon tape issue resolved. | Closed | Kapil Solanki | Details to shae to Qa
3 | 210621495 | 2024-06-04 14:35 | 125.4 | 4H.8041.../2320079 | Error Code Issue Call By Service Dealer Name :- Naresh Number:-9335012037 | Task Start | XPERT POWER GENSET | OVN Industries Private Limited - New Delhi | 1385 | SPN/FMI: 7598/7 (supply module press redn err), & (5461/0) in DM 1 and also (1761/16 in DM 2 ) code was shown , clear the DTC issue resolved. | Closed | Kapil Solanki | SR history
4 | 210621429 | 2024-06-04 14:30 | 125.4 | 4H.8041.../2320105 | Error Code Issue Call By Service Dealer Name :- Naresh Number:-9335012037 | Task Start | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 853 | Engineer visited site and found DG was not starting ..checked panel connections found XDBK (2A1) connections was burnt..suspected the both connection got short and got burnt.. | Open | Kapil Solanki
5 | 210621263 | 2024-06-04 14:01 | 125.4 | 4H.8041.../2420089 | Starting issue Call by CUSTOMER Name :- LALIT PAL Number :- 7011277501 | Task Start | GS. Oberoi Structures Pvt. Ltd. | Vidyut Engineers - New Delhi | 1.6 | DG was tripping due to under speed alarm ,running in only override condition.. Programming required. | Open | Kapil Solanki
6 | 210621260 | 2024-06-04 14:01 | 125.4 | 4H.8041.../2320125 | Emeregency Lamp Alarm ON Issue Call By Customer Name :- Dilip ... Mobile No :- 9555188828 | Task Start | YUG ENTERPRISES | Paluck Technologies Ltd. - Faridabad | 251 | SPN/FMI: 5461/0 and (1761/16 in DM 2 )clear the DTC issue resolved. | Closed | Kapil Solanki | ECU Program yo be done
7 | 210621177 | 2024-06-04 13:34 | 82.5 | 5H.8901.../2320084 | Automation Issue Call By Customer Name :- Nandkishor ... Mobile No :- 9310826615 | Task Start | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi | 155 | SPN/FMI: 516166/0 code was shown , clear the DTC issue resolved. | Closed | Kapil Solanki
8 | 210621083 | 2024-06-04 13:14 | 82.5 | 5H.8901.../2320011 | Stopping issue Call by customer Name:- SANJAI AGARWAL No:- 9810016151 | Task Start | Packo Industries | Paluck Technologies Ltd. - Faridabad | 105.32 | Customer complaint regarding reducing cooling time..No issue in DG educated to the customer about the same. | Closed | Kapil Solanki
9 | 210620549 | 2024-06-04 11:40 | 320 | F6.8802.../2420018 | Trip_Genset_Low_Voltage | Task Start | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad | 7 | Sometimes Gen set was tripping due to under voltage & under frequency alarm due to jerk load on DG.. Educated to the customer for step loading issue resolved. | Closed | Kapil Solanki
10 | 210620464 | 2024-06-04 11:14 | 500 | DV8.8501.C4../2320009 | INTAKE THROTAL VALVE FAU | Task Start | Leighton India Contractors Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon
11 | 210620238 | 2024-06-04 10:33 | 125.4 | 4H.8041.../2320059 | Starting Issue Call By Customer Name : Jyoti ... Number :9795535610 | Closed | Sudh Investments Private Limited | Vidyut Engineers - Noida | 165.32 | Electric feed pump motor was not working.. Change the E-feed pump issue resolved.. | Closed | Kapil Solanki
12 | 210620142 | 2024-06-04 10:24 | 125.4 | 4H.8041.../2320169 | Starting Issue Call By Customer Name :-Pradeep Verma Number:-9582199953 | Task Start | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 26 | Battery faulty.. Battery is not holding the charge. | Closed | Kapil Solanki | TGY vendor report
S.no | 210620051 | 2024-06-04 10:02 | 125.4 | 4H.8041.../2320110 | Starting Issue Call By: Customer Name : Manoj Saini No : 9811001700 | Task Start | Oceanica Infratech LLP. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 16 | Starting issue due to Air lock in fuel line,clean the same issue resolved.. | Closed | Kapil Solanki | Update required
1 | 210619879 | 2024-06-04 09:24 | 40 | 3H.8951.../2420010 | Starting Switch to be Change | Closed | Teknodome India Pvt. Ltd. | Vidyut Engineers - Noida | 1.56 | EMS Switch was damaged, change the same issue resolvesd.. | closed | Kapil Solanki
3 | 210621495 | 2024-08-04 12:06 | 125.4 |  | Red Lamp On Alram Issue Call By Customer Name :-Nitin Patel Number:-6390227215 | Task Start | Source India | Paluck Technologies Ltd. - Faridabad | 4.12 | ECU Fault SPN/FMI : 520528/31, 4364/2 Just reset the DTC, issue resolved. | Closed | kapil Solanki | KRM does not activated
4 | 210625006 | 2024-08-04 11:26 | 125.4 | 4H.8041.../2320169 | Battery Replacement. Email By - Service Dealer Name -Saurabh Singh | Task Start | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 28 | Battery faulty.. Battery is not holding the charge. Replaced the same issue resolved. | Closed | kapil Solanki | Details to be share
5 | 210624931 | 2024-08-04 11:14 | 125.4 | 4H.8041.../2320059 | Starting Issue Call By Customer Name : Jyoti ... Number :9795535610 | Task Start | Sudh Investments Private Limited | Vidyut Engineers - Noida | 165.33 | Under warranty, e-Feed Pump replacement, SR open for part claim purpose no issue in DG.. | Closed | kapil Solanki
6 | 210624716 | 2024-08-04 10:52 | 250 | F6.8841.../2320050 | Abnormal Sound Issue Call By Customer Name :- Pradeep Yadav Mobile No :- 8368321282 | Task Start | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 30 | Abnormal sound due to loose exhaust safety guard bolt, tighten the same issue resolved. | Closed | kapil Solanki
7 | 210624196 | 2024-08-04 10:08 |  | GP3.8604.../2420104 | Fuel Leakage Problem | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | 0.1 | Line Rejection SR,Fuel leakage from 1st no Fuel Injector, due to nozzles threads are not fitted in a proper way on the engine head. | Open | Sudhir Awasthi | ESN mfg date
8 | 210624087 | 2024-08-04 09:33 | 1000 | DV8.8501.C4../2320074 & 2320086 | Starting issue | Task Start | Neelkanth Star Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 47 | Engine Starting issue due to AC Supply given to Battery Charger Output, Relay shorted, Today Team attending the issue | Open | kapil Solanki
9 | 210624029 | 2024-08-04 08:16 | 320 | F6.8802.../2320054 | Error code issue Call By: Customer Name :-Krishna Gopal Mobile No :- 7388874982 | Task Start | Newtech Vinyl | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 66 | SPN/FMI: 97/5, 3364, Just reflash the ECU, Issue resolved. | Closed | kapil Solanki
10 | 210623723 | 2024-07-04 16:26 | 125.4 | 4H.8041.../2320066 | Red lamp Alarm Call By Customer Name:Anil Kumar Number:9971230939 | Task Start | VK GENSET & POWER SOLUTION | Paluck Technologies Ltd. - Gurgaon | 1686 | SPN/FMI; 110/16 ( high coolant temp fault) checked the radiator found choked..need to clean radiator..and also ( 5461/0) flashed the latest celebration file issue resolved. | Closed | kapil Solanki
11 | 210623660 | 2024-07-04 14:39 | 40 | 3H.8951.../2320106 | Starting Issue Call By Customer Name :- Ramendra Jha Number :- 9958178702 | Open | Nuhydro | Vidyut Engineers - Noida | 13 | Starting issue due to discharged Battery as Static Charger connection not done during CC visit, Resolved Telephonically, SR initiated cancelled. | Cancelled | Kapil Solanki
12 | 210623536 | 2024-07-04 11:30 | 57 | T4.8941.../2320166 | AVR issue Call By Customer Name : Sunil Kumar No : 9887387270 | Task Start | CAPRI TRANSFORMERS PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Main Alternator connection melted 'R phase wire connection loose' just tighten the same, Plate need to be replace but not available. | Open | Gourav Sharma | Site details to be shae with qa for terminal strip arragement
13 | 210623510 | 2024-07-04 11:02 | 320 | F6.8802.../2320020 | Trip_Genset_Low_Voltage | Task Start | SSF POLYMERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 70 | KRM generated SR, Person visited but no issue found. | Closed | kapil Solanki | KRM does not activeted
14 | 210622133 | 2024-06-04 16:32 | 200 | 6H.8435.../2320026 | FUEL Indicator issue Email By - KGD Name -Kailash Pareek | Task Start | Ajanta Colors Industry | Pratap Diesels Pvt. Ltd. - JAIPUR | 33.33 | customer complaint for proper fuel level not showing in KRM , educate the customer about the same . | Closed | Gourav Sharma
S.no | 210622125 | 2024-06-04 16:29 | 320 | F6.8802.../2320055 | FUEL Indicator issue Email By Service dealer Name :-VINIT KUMAR JAIN | Task Start | AJANTA CHEMICAL INDUSTRIES | Pratap Diesels Pvt. Ltd. - JAIPUR | 33.5 | Fuel level fluctuate because of return line fuel falling on float unit ,change the direction of float issue resolved | Closed | Gourav Sharma
1 | 210622112 | 2024-06-04 16:25 | 125.4 | 4H.8041.../2320115 | Dg set not taking load Email By - KGD Name -Pooja Sharma | Task Start | Sonysales Packaging India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR | 10 | Issue in Customer Auto Panel, R & Y Phase wire interchanged, Just corrected the same, Issue resolved. | Closed | Gourav Sharma
3 | 210629313 | 2024-09-04 14:36 | 125.4 | 4H.8041.../2420132 | Error Code Issue Call By Â Service Dealer Name :-Mohit Mobile No :-7027820044 | Task Start | Gravolite India Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 3.2 | SPN/FMI:3031/14, flashed the latest celebration file issue resolved..and also DG was running in only override condition,then changed the crank start delay time (0 to 3 sec. ) | Closed | Kapil Solanki
4 | 210629194 | 2024-09-04 13:45 | 125.4 | 4H.8041.../2420089 | Starting issue Call by Customer Name :- Lalit Pal Number :- 7011277501 | Task Start | GS. Oberoi Structures Pvt. Ltd. | Vidyut Engineers - New Delhi | 6 | Air lock issue in fuel line due to loose clamps , tighten with thread..clamp will be replaced tomorrow. | Closed | Kapil Solanki | Details required
5 | 210628518 | 2024-09-04 10:34 | 82.5 | 5H.8901.../2320102 | Red lamp alarm Issue Call By: Customer Name :Anket No :9455367352 | Task Start | Vuenow Marketing Services Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 8 | Multiple error code was shown related to adblue quality & level flashed the ECU and cleared the DTC issue resolved. | Closed | Kapil Solanki | KRM does not activeted
6 | 210628404 | 2024-09-04 10:19 | 125.4 | 4H.8041.../2320055 | DES Iissue Call By: Customer Name : Mohit No : 7027820044 | Task Start | Pri Oil And Gas Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 54.55 | SPN/FMI:1761/16 (Low DEF level @ 40 %),top up and clear the DTC issue resolved. | Closed | Kapil Solanki
7 | 210628337 | 2024-09-04 09:51 | 320 | F6.8802.../2420015 | Starting Issue Call By Service Dealer Name: Mohit Number: 7027820044 | Task Start | B. N. P. Enterprises | M/s OM Diesels Pvt. Ltd. - Sonipat | 8.22 | SPN/FMI;( 4225/1),(3224/2), code was shown,Dosing module was crystallized by DEF ,then cleaned the dosing module and cleared the DTC but DTC was not cleared.. Koel team visited the site today. | open | Kapil Solanki | Details required
8 | 210628319 | 2024-09-04 09:42 | 320 | F6.8802.../2320079 | Display issue Call by customer Name: S.N Bharti Number:9911395525 | Task Start | Yogesh Engineering Works | Paluck Technologies Ltd. - Faridabad | 19 | SPN/FMI: 1761/16 ( Low DEF level ) top up the same and clear the DTC issue resolved. | Closed | Kapil Solanki
9 | 210628281 | 2024-09-04 08:43 | 500 | DV8.8501.C4../2320033 | Trip_Genset_Low_Voltage | Task Start | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 80 | KRM generated SR,engineer visited site and found DG was tripping with under voltage alarm,& DG is not starting is first crank,checked the fuel line found main fuel filter washer minor leakage,tighten with teflon tape , then flashed the latest celebration file issue resolved but kept in under observation. | open | Kapil Solanki | Fuel filter body crack observed. Part replaced
10 | 210627906 | 2024-08-04 18:34 | 125.4 | 4H.8041.../2320113 | MCB issue Call By: Customer Name :Shiv Sagar Verma No :9984986603 | Closed | Pristine Medicure Pvt Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 41 | Koel AMF panel side (MCB faulty), MCB order placed by SD team. no issue in DG. | Closed | Kapil Solanki
11 | 210627841 | 2024-08-04 18:10 | 750 | DV2.8501.C4../2320033 | Starting Issue Call By: Customer Name :Ram Mohan Gupta No :9050555117 | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 50.7 | Interface Box RL2 & RL 3 Negative wire connection loose due to Loose crimping also 30 Amp Fuse connection Push back, Corrected the same, issue resolved. | Closed | Kapil Solanki | Interface ard issue
12 | 210627677 | 2024-08-04 17:46 | 500 | DV8.8501.C4../2320015 | Trip_Genset_Low_Voltage | Open | MTI. Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Sonipat | 230 | SPN/FMI:100/1 ( minimum oil pressure err) &(156/17) short circuit of the HDEV power stage hige side (Bank error) & (658/3) short circuit of the power stage low side ( cylinder error), Today team performing Load analyses | open | Kapil Solanki | Wiring change and to be kept under observation
13 | 210627254 | 2024-08-04 17:35 | 125.4 | 4H.8041.../2420102 | VOC-: ENGINE NOT STARTING - AIR LOCK IN FUEL SYSTEM Customer Name- HimanshuCustomer Number-9026708131 Mode- SR Generated through CDI calling. | Task Start | Master Electric Store | OVN Industries Private Limited - New Delhi | 3.14 | VMR wire in break condition, corrected the same, Issue resolved. | Closed | Kapil Solanki
14 | 210627038 | 2024-08-04 16:36 | 160 | 6H.8475.../2420015 | Synchronizations Call By: Customer Name : Farib Khan No :8447581357 | Closed | PKV. Consulting Engineers Pvt. Ltd. | OVN Industries Private Limited - New Delhi |  | Customer registered SR for 160 KVA two DG Synchronization. | open | Kapil Solanki
15 | 210626855 | 2024-08-04 15:55 | 40 | 3H.8951.../2420028 | Amber Lamp Issue Call By Customer Name :-Taranpal Singh Mobile No :-9034249031 | Closed | Nirmal Charitable Trust Regd | Vishal Power Systems - Kurukshetra | 2 | Cam Sensor connector in detached condition, Connected the same, Issue resolved. | Closed | Kapil Solanki | Not checked in CC. need to confirm
16 | 210626595 | 2024-08-04 15:11 | 125.4 | 4H.8041.../2420001 | Preventive Maintenance Call By Customer Name :- Gurpreet Kaur Mobile No :- 9311523743 | Open | Kumar Generator House | Vidyut Engineers - New Delhi |  | Maintenance activity closed in CSP SR,so that mail dropped for this SR cancellation. | Cancelled | Kapil Solanki
S.no | 210626587 | 2024-08-04 15:11 | 125.4 | 4H.8041.../2320146 | Preventive Maintenance Call By Customer Name :- Gurpreet Kaur Mobile No :- 9311523743 | Open | Kumar Generator House | Vidyut Engineers - New Delhi |  | Maintenance activity close in CSP SR, so that mail dropped for this SR cancellation. | Cancelled | Kapil Solanki
1 | 210626584 | 2024-08-04 15:11 | 30 | 3H.8902.../2320040 | Preventive Maintenance Call By Customer Name :- Gurpreet Kaur Mobile No :- 9311523743 | Open | KUMAR GENERATOR HOUSE | OVN Industries Private Limited - New Delhi |  | Maintenance activity close in CSP SR,so that mail dropped for this SR cancellation. | Cancelled | Kapil Solanki
3 | 210632022 | 2024-10-04 14:59 | 320 | F6.8802.../2320026 | Trip_Genset_Low_Voltage | Open | JAYCEE CASTALLOYS (P) LTD. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 62 | High Jerk Load on DG | Closed | Kapil Solanki | KRM cpature only max 146 amp current in one phase.
4 | 210631438 | 2024-10-04 12:39 | 125.4 | 4H.8041.../2320090 | Starting Issue And preventive maintenance Call By - Customer Name - Ritesh Kumar No. - 7042659373 | Task Start | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi |  | SPN/FMI 5461/0, SD team visiting to flash the ECU. | Open | Kapil Solanki
5 | 210630673 | 2024-10-04 10:22 | 125.4 | 4H.8041.../2420062 | Starting issue Call by customer Name: Aditya Number:9350052900 | Closed | Sunita Biotech | Vidyut Engineers - Noida | 9.42 | Starting issue due to loose starting relay connector wire, remove and refitted the same issue resolved. | Closed | Kapil Solanki
6 | 210630400 | 2024-10-04 09:35 | 125.4 | 4H.8041.../2420116 | Starting Issue Call By: Customer Name :Satpal Singh No :9310666824 | Closed | Guru Harkishan Casting | Paluck Technologies Ltd. - Faridabad | 2.16 | Air lock issue in fuel line due to damaged clamp replaced the same, issue resolved. | Closed | Kapil Solanki
7 | 210630370 | 2024-10-04 09:20 | 125.4 | 4H.8041.../2320054 | Tripping Issue Call By Customer Name:- Rajesh Ram Number:- 9953102701 | Closed | THERMADYNE PVT. LTD. | Paluck Technologies Ltd. - Faridabad | 56 | SPN/FMI:1761/16 (Low DEF level) alarm clear the DTC issue resolved. | Closed | Kapil Solanki
S.no | 210629591 | 2024-09-04 16:13 | 320 | F6.8802.../2320051 | Trip_Genset_Low_Voltage | Open | Sri Dwarkadheesh Polymers Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | KRM generated SR visit pending | Open | Gourav Sharma | Genset stop time that Genset RPM is 775. so KRM SR genrate.
1 | 210629548 | 2024-09-04 16:11 | 82.5 | 5H.8901.../2320073 | Urea Issue Call By Customer Name-MP Shukla Number-9811540438 | Closed | SB. Industries | Vidyut Engineers - Noida | 39.19 | SPN/FMI : 516166/0, clear the DTC and educated the customer about the same . | Closed | Kapil Solanki
3 | 210633085 | 2024-10-04 20:01 | 125.4 | 4H.8041.../2420130 | Starting Issue Call By: Customer Name :Gurudeep Singh No :9873196290 | Open | Gurdeep Singh. | Vidyut Engineers - New Delhi |  | Canopy Emergency switch was pressed guided the customer about same on call issue resolved.. | cancelled | Kapil Solanki
4 | 210632647 | 2024-10-04 17:07 | 320 | F6.8802.../2420018 | Under Frequency Alarm Issue Call By Customer Name :- Hari Datta Mobile No :- 9958425449 | Task Start | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad | 8 | SPN/FMI: 3031/14, clear the DTC, flashing required. | Open | Kapil Solanki
5 | 210632335 | 2024-10-04 16:00 | 320 | F6.8802.../2420001 | Tripping issue Call by customer Name: Daulat Singh Number:9971998080 | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 14 | SPN/FMI: 652/5 code was shown.. Checked the injector connector found oil clean the same and also loose wiring at injector refitted the same issue resolved. | Closed | Kapil Solanki
6 | 210632056 | 2024-10-04 15:07 | 30 | 3H.8902.../2320054 | Trip_Genset_Low_Voltage | Open | Asha Sharma | Paluck Technologies Ltd. - Ghaziabad |  | KRM generated SR.. DG was tripping due to under voltage contact to the customer as per customer voice no issue in DG. | cancelled | Kapil Solanki | KRM triggered
7 | 210632032 | 2024-10-04 15:01 | 125.4 | 4H.8041.../2420113 | Air Locking Issue Email By Service Dealer Name:-Amitabh Kushwaha | Closed | Mayura Textiles | Paluck Technologies Ltd. - Faridabad | 10 | DG was running in only override condition ,change the start delay time (0 to 3 sec ) issue resolved. | Closed | Kapil Solanki | Recent cases ESN to share QA
8 | 210634351 | 2024-11-04 13:46 | 1000 | DV8.8501.C4../2320074 & 2320086 | Starting issue Call By Service Dealer:- Name :- Mohit Mobile No :-7027820044 | Open | Neelkanth Star Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat |  |  |  | Kapil Solanki | To esclate issue reg AEPG team visit
9 | 210633841 | 2024-11-04 11:23 | 500 | DV8.8501.C4../2320035 | Oil Leakage Issue Call By Customer Name :- Praveen Sharma Mobile No :- 9671565200 | Closed | Sidhi International Metal Alloys P. Ltd. | Paluck Technologies Ltd. - Faridabad | 41.4 | Oil leakage from loose oil filter, tighten the same issue resolved. | Closed | Kapil Solanki
10 | 210633606 | 2024-11-04 10:20 | 500 | DV8.8501.C4../2320029 | Coolant Leakage Issue Call By Customer Name :- Jahangir Ahmed Mobile No :- 9797750480 | Open | Sheen Agri Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar |  | Visit pending.. | Open | Ved Gupta
S.no | 210634990 | 2024-11-04 16:23 | 320 | F6.8802.../2320020 | Trip_Genset_Low_Voltage | Open | SSF POLYMERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Engineer will visited site tomorrow | Open | Kapil Solanki
1 | 210634779 | 2024-11-04 15:35 | 125.4 | 4H.8041.../2420158 | Temprature issue | Task Start | Instinct | Paluck Technologies Ltd. - Gurgaon | 2 | SPN/FMI: 171/3 ( Ambient temp flt) Koel team will visited site tomorrow. | Open | Kapil Solanki
3 | 210641127 | 2024-12-04 14:32 | 30 | 3H.8902.../2320079 | Starting issue Call By Service Dealer Name :-Ramesh Sharma Number :-9599006443 | Closed | Shivalik Hospital | Paluck Technologies Ltd. - Faridabad | 12 | SPN/FMI : 105/3 ( Intake air temp Voltage high) ( 102/3),(110/3 coolant temp high ) clear the DTC issue resolved. | Closed | Kapil Solanki | KRM data not availble KRM website
4 | 210639966 | 2024-12-04 11:41 | 62.5 | T4.8941.../2320056 | Tripping Issue Call By: Customer Name :Joganver Singh No :9911146716 | Closed | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 365.41 | Sometimes jerk load on DG ,Educated to the customer for step loading. | Closed | Kapil Solanki
5 | 210638965 | 2024-12-04 11:10 | 30 | 3H.8902.../2320008 | Starting Issue Call By: Service Dealer Name :-Bihma shenkar No :8802500270 | Cancelled | Gagan Mani | Vidyut Engineers - New Delhi |  | SD team trying to contact customer but No response from customer side. | cancelled | Kapil Solanki | KRM show wrong fault code
6 | 210638862 | 2024-12-04 10:44 | 200 | 6H.8435.../2320015 | Starting Issue Call By: Customer Name :Aakash . No :8979229856 | Closed | Indo World Space | Paluck Technologies Ltd. - Ghaziabad | 29 | SPN/FMI: 4376/3 ( reverting voltage short to ground )( 2802/3), (4375/11) ( 2802/4) code was shown, clear the DTC issue resolved. | Closed | Kapil Solanki | All fault availble in KRM data.but requriment of monitering KRM data.
7 | 210638709 | 2024-12-04 10:10 | 250 | F6.8841.../2320010 | Error Code Issue Call By Customer Name :- Ramtreet .. Number :-9813125771 | Closed | SEETA FOODS PVT LTD | Paluck Technologies Ltd. - Faridabad | 245 | SPN/FMI: 5419/1 ( Engine throttle Actuator 1-low- most severe ), checked ITV sensor and wiring harness found ok.clear the DTC issue resolved. | Closed | Kapil Solanki
8 | 210638579 | 2024-12-04 09:34 | 25 | GP3.8702.../2420004 | Starting issue Call By Customer Name :-Samar Number :-9416013877 | Closed | Shiv Urmila Bajaj Filling Station | Vishal Power Systems - PANIPAT | 60 | SR Open regarding servicing purpose. | Closed | Kapil Solanki | A CSP does not completed
9 | 210636820 | 2024-11-04 18:03 | 20 | GP3.8601.../2320053 | Black smoke issue and RPM issue Call by customer Name : Shubham Gohael No : 9929747179 | Closed | Atul Chachan | M/s OM Diesels Pvt. Ltd. - Rohtak | 34 | Unbalanced load on DG, educated to the customer about the same issue resolved. | Closed | Kapil Solanki | unbalanced load show in KRM system
10 | 210634990 | 2024-11-04 16:23 | 320 | F6.8802.../2320020 | Trip_Genset_Low_Voltage | Task Start | SSF POLYMERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 140 | KRM generated SR, Engineer visited the site and found the intake manifold gasket was damaged and need to be replaced. | Closed | Kapil Solanki | check the KRM data genset does not take jark load.
11 | 210634779 | 2024-11-04 15:35 | 125.4 | 4H.8041.../2420158 | Temprature issue | Closed | Instinct | Paluck Technologies Ltd. - Gurgaon | 2 | Line rejection SR, SPN/FMI: 171/3 ( Ambient temp. voltage high ) checked and found ECU 60 pin connector and Ambient temp sensor connector were interchanged.. Correct the same issue resolved. | Closed | Kapil Solanki
12 | 210634558 | 2024-11-04 14:48 | 57 | T4.8941.../2420052 | Starting Issue Call By Customer Name :- Ankit Agrawal Mobile No :- 9811063871 | Closed | Goyal Dal Products Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 1.14 | Engineer visited the site and found the battery charger wire break .. Reconnected the same issue resolved. | Closed | Kapil Solanki
S.no | 210634351 | 2024-11-04 13:46 | 1000 | DV8.8501.C4../2320074 & 2320086 | Starting issue Call By Service Dealer:- Name :- Mohit Mobile No :-7027820044 | Task Start | Neelkanth Star Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 58 | Earlier Air Filter Assy 'Suction Pipe' short supply with new DG, Arranged by Marketing team, Fitment done, Issue resolved. | Closed | Kapil Solanki | Commisioned
1 | 210633606 | 2024-11-04 10:20 | 500 | DV8.8501.C4../2320029 | Coolant Leakage Issue Call By Customer Name :- Jahangir Ahmed Mobile No :- 9797750480 | Task Start | Sheen Agri Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar | 61 | Coolant leakage from loose radiator hose clip tighten the same issue resolved. | Closed | Ved Gupta
3 | 210641349 | 2024-12-04 15:23 | 250 | F6.8841.../2420021 | . | Task Start | Manoj Popli | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Line rejection SR, Canopy roof was damaged. | Closed | Kapil Solanki
4 | 210642087 | 2024-12-04 18:02 | 57 | T4.8941.../2420101 | Power supply issue Call By Customer Name :- Indra Gupta Mobile No :- 9958829804 | Task Start | KSS Engineers | Vidyut Engineers - New Delhi |  | Customer panel side issue, As per customer voice DG is running OK. | Closed | Kapil Solanki
5 | 210642121 | 2024-12-04 18:12 | 40 | 3H.8951.../2320050 | Low Oil Pressure issue & Back compressor Issue Call by customer Name: Omveer Singh Number: 9999786175 | Closed | Chaudhary Generator Service | Vidyut Engineers - Noida | 644 | Customer complaint about Low oil pressure issue… engineer visited the site and found DG running ok no issue in DG. | Closed | Kapil Solanki
6 | 210643143 | 13-04-2024 10:39 |  | GP3.8604.../2420103 | Abnormal Sound Issue | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | 1.3 | Line rejection SR Abnormal sound from Engine at Fly wheel end engineer will be visit today (GOEM & ASE in contact with Bhavya Singhal) | Open | Sudhir Awasthi
7 | 210643273 | 13-04-2024 11:01 | 20 | GP3.8601.../2320059 | Starting Issue Call By Customer Name:Vipil Pathak Number:8178274977 | Closed | H. Sriwastave & Associates | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 14 | Battery was discharged ,battery charger supply was missing ,connect the battery charger supply the issue resolved | Closed | Kapil Solanki
8 | 210643308 | 13-04-2024 11:11 | 200 | 6H.8435.../2420005 | Coolant Leakage issue Call By Customer Name: Krishnanandan Number:9540678513 | Closed | Rani Electrodes Limited Unit II. | Paluck Technologies Ltd. - Faridabad | 18 | coolant over flow from recovery tank ,customer filled the coolant above H mark educated the customer about same issue resolved. | Closed | Kapil Solanki
9 | 210643604 | 13-04-2024 12:03 | 57 | T4.8941.../2320040 | Voltage Fluctuation Issue Call By Customer Name :-Umesh Dhavan Mobile No :-9213428845 | Task Start | Hariom Tools | Paluck Technologies Ltd. - Faridabad |  | DG was tripping due to under voltage alarm due to jerk load(about 15A) on DG educated the customer about same . | Closed | Kapil Solanki
10 | 210643742 | 13-04-2024 12:29 | 57 | T4.8941.../2320238 | Tripping issue Call by customer Name : Shagul No : 9899202288 | Open | Golden Sparrow Industries | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit pending | Open | Gourav Sharma
11 | 210644313 | 13-04-2024 15:04 | 57 | T4.8941.../2320155 | voltage fluctuation issue Call by customer Name : Mohit Gupta No : 9868261446 | Open | Texo Industries Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit pending | Open | Gourav Sharma
12 | 210644431 | 13-04-2024 15:29 | 125.4 | 4H.8041.../2420125 | Starting Issue Call By: Customer Name :Sham No :8448226754 | Closed | SR. Power Engineers | Vidyut Engineers - Noida | 5.5 | Starting issue due to ECU 94 pin connector was loose ,fitted the same issue resolved. | Closed | Kapil Solanki
13 | 210644478 | 13-04-2024 15:43 | 57 | T4.8941.../2320021 | Starting Issue Call By Customer Name: Alok Tiwari Number:9057686568 | Closed | CONTINENTAL DEVICE INDIA LIMITED | Vidyut Engineers - New Delhi | 12.4 | Copper washer of primary filter was cracked , Replaced the new washers , same the issue resolved | Closed | Kapil Solanki
14 | 210644509 | 13-04-2024 15:56 | 82.5 | 5H.8901.../2320102 | Display Issue Call By Customer Name :- Dinesh Kumar Number :- 7505652605 | Closed | Vuenow Marketing Services Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 9 | DEF percentage was not showing in controller, reprogrammed the GCU but issue not resolved after that change the controller..issue resolved. | Closed | Kapil Solanki
15 | 210644511 | 13-04-2024 15:56 | 15 | GP3.8501.../2320038 | Tripping issue Call by customer Name : Mahes Singh No : 9650577296 | Closed | OPTIMAS ENERGY INDIA | Vidyut Engineers - Noida | 4.2 | DG was tripping with showing over current shut down found unbalanced load, educated the customer same | Closed | Kapil Solanki
16 | 210644642 | 13-04-2024 16:10 | 57 | T4.8941.../2320196 | Load issue Call by customer Name: Aryan Sharma Number:9811852400 | Closed | PRIME ENGINEERING | Vidyut Engineers - Noida | 83.2 | Excessive Jerk Load on DG while Air Compressor Operation, Educated Customer to put step load. | Closed | Kapil Solanki
17 | 210644791 | 13-04-2024 16:55 | 62.5 | T4.8941.../2420021 | Starting Issue Call By Customer Name :- Dr Jain .. Number :- 9811276300 | Closed | Jain Hospital | Paluck Technologies Ltd. - Gurgaon | 2 | Emergency switch in depressed condition, just release the same, Issue resolved. | Closed | Kapil Solanki
18 | 210645465 | 13-04-2024 17:33 | 160 | 6H.8475.../2320011 | Tripping Issue Call By Customer Name :- Anit . Number :- 7011180879 | Open | Kashish Plastic Industries | Paluck Technologies Ltd. - Ghaziabad |  | DG trip with Emergency switch alarm, Team will attend the site | Open | Kapil Solanki
19 | 210645616 | 13-04-2024 18:12 | 500 | DV8.8501.C4../2320060 | Starting issue Call by customer Name:- Mukesh ... No:-9311324752 | Task Close | LNM. Auto Industries Private Ltd.. | Paluck Technologies Ltd. - Faridabad | 78 | 20 Amp fuse found on interface card box, Replaced with 30 A fuse issue is resolved | Closed | Kapil Solanki
Sr. No | 210645689 | 13-04-2024 19:04 | 57 | T4.8941.../2420089 | Tripping Issue Call By Customer Name :- Suresh Mobile No :- 9810964246 | Task Start | MC. Cap Industries | Paluck Technologies Ltd. - Faridabad | 2.4 | starting issue due loose connection of distribution box . Re-tighten the all distribution boxes same the resolved | Closed | Kapil Solanki
1 | 210645698 | 13-04-2024 18:49 | 200 | 6H.8435.../2320006 | KRM Issue Call By Customer Name :Shkif ... Mobile No 9419092093 | Open | Himalayan Cold Store Pvt. Ltd. | Suraj Motor Store - Srinagar | 56 | KRM Maintenance Hours update. | Closed | Ved Gupta
3 | 210646293 | 14-04-2024 07:44 | 125.4 | 4H.8041.../2320088 | Automation Issue Call By Customer Name :- Bhopal Kishan Mobile No :- 9650991118 | Shramdeep Appartments | Vidyut Engineers - Noida | 57 | Customer complained about automation issue, engineer found manual mode in DG, educated the customer about same issue resolved | Closed | Kapil Solanki
4 | 210646483 | 14-04-2024 14:32 | 125.4 | 4H.8041.../2320123 | Automation Issue Call By Customer Name :- Abhishekh . Mobile No :- 6239194836 | Sarvodya Infracon Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 35 | Issue from Customer Auto Panel (Manis sensing missing), Todau Auto Panel team visiting at site. | Closed | Kapil Solanki
5 | 210646965 | 15-04-2024 08:45 | 500 | DV8.8501.C4../2320082 | On Off switch issue Call by Customer Name :-Anand Number :- 9911319889 | PG. Electroplast Ltd. | Paluck Technologies Ltd. - Ghaziabad | 31 | DG MCCB Lever in Physically damaged condition, need to replace, EDO placed by SD team. | Open | Kapil Solanki
6 | 210647220 | 15-04-2024 10:42 | 500 | DV8.8501.C4../2320027 | Starting Issue Call By Customer Name :- Pradeep Verma Mobile No :- 9582199953 | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 48.3 | Ignition Circuit 25 Amp fuse blown-out in interface box, Replaced with 30 A fuse issue resolved. | Closed | Kapil Solanki
7 | 210647355 | 15-04-2024 11:19 | 57 | T4.8941.../2320196 | Load Issue Call By Customer Name :- Aryan Sharma Number :- 9811852400 | PRIME ENGINEERING | Vidyut Engineers - Noida | 85 | There is a maximum 20 A jerk load | Open | Kapil Solanki
8 | 210647520 | 15-04-2024 11:45 | 320 | F6.8802.../2420011 | Starting issue call by customer Name: Satish Number:8285560282 | MALIK ENTERPRISES | Paluck Technologies Ltd. - Faridabad | 12.5 | SPN/FMI -655/5 found 5 no injector connection was loose , Re tighten the same issue resolved | Closed | Kapil Solanki
Sr. No | 210647804 | 15-04-2024 12:53 | 57 | T4.8941.../2320036 | Maintenance Due Alarm Issue Call By Customer Name :-Lalit Mobile No :-9810138700 | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad |  | Visit pending | Open | Kapil Solanki
1 | 210647808 | 15-04-2024 12:53 | 82.5 | 5H.8901.../2320053 | Starting issue Call by Customer Name :-Amit Jain Number :- 9350782691 | Rock Rubber Industries | Paluck Technologies Ltd. - Ghaziabad | 26 | Emergency stop alarm showing on controller , found canopy emegency switch was opened ,tomorrow will be changed Emergency switch (NC type emergency switch) | Closed | Kapil Solanki
3 | 210652699 | 16-04-2024 11:34 | SL90 | 320 | F6.8802.../2420018 | Trip_Genset_Low_Voltage | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad | 12 | Sometime while applied load, DG was tripping with showing underspeed or undervoltage alarm , Re -tighten the fuel line, Load trial yet to perform, engineer will visit tomorrow | Open | Kapil Solanki
4 | 210652697 | 16-04-2024 11:32 | R550 | 15 | GP3.8501.../2320002 | Starting Issue Email By Service Dealer Name:-Rakesh Singh | Dr. Ajay Wadhawan | Vidyut Engineers - Noida | 11.33 | 9RB1 Relay board RL1 (2B wire was loose ) tighten the same issue resolved | Closed | Kapil Solanki
5 | 210652614 | 16-04-2024 11:18 | R1190 | 40 | 3H.8951.../2320053 | Voltage Issue Call By: Customer Name :Jaybeer Singh No :9812884055 | STRIIKER INDUSTRIES PVT LTD | Vidyut Engineers - New Delhi | 17 | Earlier Customer not responding to Phone calls later connected through GOEM Marketing team, SR initiated for cancellation, Issue will be attended in new SR. | Cancelled | Kapil Solanki
6 | 210652485 | 16-04-2024 10:47 | R1190 | 82.5 | 5H.8901.../2320103 | Diesel leakage issue Call By Customer Name :- Santosh Kumar Yadav Mobile No :- 9163433218 | Vuenow Marketing Services Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 19 | Customer complained about fuel leakage issue, water found on top of tank (engineer guess rain water) | Closed | Kapil Solanki
7 | 210652409 | 16-04-2024 10:34 | K1080 | 125.4 | 4H.8041.../2320054 | Amber Lamb alam Issue Call By Customer Name:- Rajesh Ram Number:- 9953102701 | THERMADYNE PVT. LTD. | Paluck Technologies Ltd. - Faridabad | 63 | SPN/FMI - 5461/0 Updated latest version cal file. | Closed | Kapil Solanki
8 | 210652325 | 16-04-2024 10:30 | K1080 | 125.4 | 4H.8041.../2320017 | Starting Issue Call By: Customer Name :Bharat Bhushan No :9802706060 | RAJESHWARI CHEMICALS | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | SR registered by KGD for Auto Panel connections, no Issue in DG, SR initiated for cancellation, SD team will do Chargable visit. | Closed | Kapil Solanki
9 | 210652299 | 16-04-2024 10:16 | K1080 | 125.4 | 4H.8041.../2420119 | Starting Issue Call By: Customer Name :Bharat Bhushan No :9802706060 | Masyc Projects Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | SR registered by KGD for Auto Panel connections, no Issue in DG, SR initiated for cancellation, SD team will do Chargable visit. | Closed | Kapil Solanki
10 | 210652123 | 16-04-2024 09:38 | DV | 500 | DV8.8501.C4../2320021 | Starting issue Call by customer Name: Navin Verma Number:8755023232 | SUPRA CRAFT INDIA LTD | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit pending | Open | Gourav Sharma
11 | 210652064 | 16-04-2024 08:37 | K1080 | 200 | 6H.8435.../2320002 | Starting issue Call By Customer Name :-Mhomad Shida Mobile No :-9811738726 | MM. Polyvinyls Pvt. Ltd. | Vidyut Engineers - Noida | 89.44 | SPN/FMI - 97/2, 4375/11, 920/5, 4376/3, 97/5 just clear the DTC | Closed | Kapil Solanki
12 | 210651288 | 15-04-2024 18:24 | K1080 | 125.4 | 4H.8041.../2320041 | Starting Issue Call By Customer Name :- Yogendr No :- 8447093041 | Drivewell Auto Industries. | Paluck Technologies Ltd. - Faridabad | 62 | Starting issue due to NRV of E-feed pump was internally malfunction (Fuel flow in both directions), change the same issue resolved | Closed | Kapil Solanki
13 | 210651227 | 15-04-2024 18:05 | K1080 | 125.4 | 4H.8041.../2320107 | Alarm Issue Call By: Customer Name :Dipankar No 9351764173: | Mafico Services Private Limited | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit pending | Open | Gourav Sharma
14 | 210651098 | 15-04-2024 17:43 | K1080 | 125.4 | 4H.8041.../2420125 | Starting Issue Call By: Customer Name :Sham No :9971438718 | SR. Power Engineers | Vidyut Engineers - Noida | 8.33 | Starting issue due to NRV of E-feed pump was internally malfunction (Fuel flow in both directions), change the same issue resolved or SPN/FMI - 3031/14 clear the code | Closed | Kapil Solanki
15 | 210649631 | 15-04-2024 15:12 | SL90 | 320 | F6.8802.../2420003 | Oil Â Leakage Issue Call By Customer Name :-Yadram Mobile No :-9024620248 | Rajaj Jhiriwal | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit pending | Open | Gourav Sharma
Sr. No | 210648986 | 15-04-2024 14:07 | K1080 | 125.4 | 4H.8041.../2420059 | Troubleshooting Issue Email By KGD Name:-Shamim Ahmed | Sath Guru Engineering | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit pending | Open | Gourav Sharma
1 | 210647804 | 15-04-2024 12:53 | R810 | 57 | T4.8941.../2320036 | Maintenance Due Alarm Issue Call By Customer Name :-Lalit Mobile No :-9810138700 | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad | 288 | Rental DG moved to Meerut, SR Transfer from Paluck Technologies Ltd. - Ghaziabad to RK Engineer - Meerut | Open | Kapil Solanki | Run hr and maintaince hr check in program
3 | 210652931 | 16-04-2024 12:32 | K1080 | 160 | 6H.8475.../2320029 | Fan belat issue Call by customer Name:- Rajan No:-9891915401 | Task Start | Areol Formulations Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 49 | Abnormal sound from Engine, found V belt in loose condition ,tighten the same issue resolved | Closed | Kapil Solanki
4 | 210653274 | 16-04-2024 13:55 | K1080 | 125.4 | 4H.8041.../2420092 | AIR LOCK ISSUE | Closed | Raj Engineering Works | Pratap Diesels Pvt. Ltd. - JAIPUR | 2 | Air Lock issue, replaced Fuel filer header assy. | Open | Gourav Sharma
5 | 210653574 | 16-04-2024 15:09 | R810 | 57 | T4.8941.../2320250 | Canopy Door Issue Call By Customer Name :- Sanjana . Mobile No :- 8585944939 | Closed | Shivmani Hospital | Paluck Technologies Ltd. - Faridabad | 49 | Control Panal side door was not closing properly, tighten the door lock adjusting bolt issue is resolved | Closed | Kapil Solanki
6 | 210653788 | 16-04-2024 15:51 | K1080 | 125.4 | 4H.8041.../2320134 | Starting Issue Call By: Customer Name : Kasidh Ahmad No :8445820675 | Closed | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar |  | SPN/FMI : 110/0, Checked Wiring Harness as well Sensor resistance (1400-1500 Ohm) found Ok, just reset DTC, Issue resolved, during trial no issue. | Closed | Sudhir Awasthi | Check the KRM data but does not show on dashboard .so only check the GCU data .and found it coolant temp. maximum 90 C.
7 | 210653920 | 16-04-2024 16:13 | K1080 | 125.4 | 4H.8041.../2320004 | Power supply issue Call by Customer Name : Indersen Yadavji Number:8826817371 | Closed | ARIHANT INDUSTRIAL EQUIPMENT | Vidyut Engineers - New Delhi | 88.4 | Customer complaints about power supply issue , engineer attend the site and started the engine .no issue found on DG and power supply | Closed | Kapil Solanki
8 | 210654116 | 16-04-2024 16:48 | K1080 | 125.4 | 4H.8041.../2320164 | Canopy Door Issue Call By Customer Name :- Mahendra Singh Mobile No :- 9728817611 | Open | Medipulse Aadhar Hospital & Diagnostic | Pratap Diesels Pvt. Ltd. - JAIPUR |  | visited pending | Open | Gourav Sharma
9 | 210655316 | 16-04-2024 18:22 | K1080 | 125.4 | 4H.8041.../2320062 | Alarm Issue Call By Customer Name :-Govind No :- 9315211490 | Task Start | Shiv Industries | M/s OM Diesels Pvt. Ltd. - Sonipat | 93.4 | Low DEF level @ 0%, Top up the same also educated to Customer to keep the DEF level maintained b/w 50-100 % for trouble free Operation. | Closed | Kapil Solanki
10 | 210656166 | 17-04-2024 10:51 | R1190 | 30 | 3H.8902.../2320036 | Over heating issue Call by customer Name:- Ravindra No:- 8053495659 | Task Start | Landmark Buildwell Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 625 | DG overheating due to front of radiator was choke hot air not passing between surrounding and inside the canopy, Expansion Bellow was damaged. | Open | Kapil Solanki | Below change and alingment need to check
11 | 210656428 | 17-04-2024 12:00 | K1080 | 200 | 6H.8435.../2320002 | Coolant leakage issue.. Email By-Customer Name:-Mohd Shahid | Open | MM. Polyvinyls Pvt. Ltd. | Vidyut Engineers - Noida | 90.4 | coolant overflow from the recovery tank, customer filled the coolant above H mark educated the customer about the same issue resolved. | Closed | Kapil Solanki
12 | 210657588 | 17-04-2024 14:25 | R1190 | 82.5 | 5H.8901.../2320086 | Voltage Fluctuation issue Call By Customer Name :-Gaurav Mobile No :-9911909109 | Task Start | PSG. International | Paluck Technologies Ltd. - Faridabad | 27 | As per customer voice when applied the load LED lights are flickering, engineer tested separately with 100 W bulb ,at that time there was no flickering , engineer suggest to customer check the wiring on change over panel | Closed | Kapil Solanki
S.no | 210657784 | 17-04-2024 14:44 | DV CRDi | 750 | DV2.8501.C4../2320024 | Looding issue Call by sd Name :-Deepak Kumar No :-7027820048 | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 112 | SR generated to replace CAC hose & Interface Box. | Closed | Kapil Solanki
1 | 210657818 | 17-04-2024 14:50 | DV CRDi | 750 | DV2.8501.C4../2320005 | Tripping Isue Call By Service Dearler Name- Deepak Kumar Number -7027820048 | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 135 | SR generated to replace CAC hose & Interface Box. | Closed | Kapil Solanki
3 | 210657979 | 17-04-2024 15:07 | K1080 | 125.4 | 4H.8041.../2420139 | ESU Defective | Task Start | SEAL TECH INTERNATIONAL | Paluck Technologies Ltd. - Faridabad | 2 | Staring issue ikonnect was showing ECU ERROR NO RESPONSE FROM ECU checked ECU supply voltage found 12 volt , ECU will be change | Open | Kapil Solanki | Failed part
4 | 210658735 | 17-04-2024 16:23 | R810 | 57 | T4.8941.../2320196 | Load Issue Call By Customer Name :- Aryan Sharma Number :- 9811852400 | Task Start | PRIME ENGINEERING | Vidyut Engineers - Noida | 86.29 | Customer has more load then capacity of DG, Need to analyze Load with Load analyzer. | Open | Kapil Solanki | Load study
5 | 210659758 | 17-04-2024 19:16 | DV | 500 | DV8.8501.C4../2320021 | Voltage Fluctuation & Amber Lamp Alarm Issue Call By: Customer Name :Navin Verma No :8755023232 | Open | SUPRA CRAFT INDIA LTD | Pratap Diesels Pvt. Ltd. - JAIPUR |  | DC alternator Output Voltage wire in damaged condition, Replaced Thimble, Issue resolved. | Closed | Gourav Sharma
6 | 210660011 | 18-04-2024 09:19 | K1080 | 125.4 | 4H.8041.../2320098 | Starting Issue Call By Customer Name :- Somadeep . Mobile No :-9992100991 | Task Start | Rathi Pumps Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 45 | Staring issue due to Battery was discharge , found battery charger connection supply switch was off , charging the same issue resolved | Closed | Kapil Solanki
7 | 210660014 | 18-04-2024 09:23 | DV | 500 | DV8.8501.C4../2320015 | Starting issue Call By Customer Name :Sandip Mobile No :9813216906 | Task Start | MTI. Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Sonipat | 232 | Mr. Sudip Marik Visited site. Replaced Engine Harness & Interface Box due to repeated Injector Open circuit DTC & 30 Amp Fuse blown | Open | Kapil Solanki
8 | 210660019 | 18-04-2024 09:30 | R550 | 20 | GP3.8601.../2320053 | Black smoke Email By - Service Dealer Name -KOEL CARE ROHTAK | Task Start | Atul Chachan | M/s OM Diesels Pvt. Ltd. - Rohtak | 38 | Black smoke coming from Exhaust manifold due to overload , by mistake compressor machine are connected the DG (compressor capacity more then DG capacity) Educated the customer about same issue resolved also DG commissioned in Closed Room (Vantilation issue) | Closed | Kapil Solanki
9 | 210660030 | 18-04-2024 09:47 | DV CRDi | 750 | DV2.8501.C4../2320047 | Exhaust Heat Issue Call By: Customer Name : Dipesh Garg No :8708612594 | Task Start | Merino Industries Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 5 | The Exhaust manifold is turning Hot red, Suspected Hot Air Ducting not as per recommendations. KOEL team will be visit | Open | Kapil Solanki
10 | 210660907 | 18-04-2024 12:42 | DV | 625 | DV0.8501.C4../2320001 | Fuel gauge issue Call by customer Name:- Pardeep Kumar No 9910417830 | Open | Tata Tele services | Vidyut Engineers - New Delhi | 37 | Fuel gauge not working properly and fuel tank cap are not fitted properly ,after filling 100% fuel sometimes 70%,50%,100% show on controller , found fuel gauge not traveling smoothly, fuel gauge will be change | Open | Kapil Solanki | To cpmpare 2-3 other sites. KRM data | KRM does not active in dasboard
Sr.No | 210661064 | 18-04-2024 13:26 | K1080 | 125.4 | 4H.8041.../2320201 | Starting Issue Call By Customer Name :- Sham .. Number :-9911281300 | Open | Aadrika Energy Privet Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | The Controller did not turn ON due to controller input positive supply connection was loose and found 14 RB1 (RL1 relay input wire was open tighten the same issue resolved | Closed | Kapil Solanki | Loose connection. Torque specification. Data share with location and kva
1 | 210661308 | 18-04-2024 14:40 | K1080 | 200 | 6H.8435.../2320012 | Starting Issue Call By: Customer Name :Omveer Sharma No :9910626566 | Task Start | NIEVA HOMES PVT. LTD. | Vidyut Engineers - Noida | 90.54 | Starting issue due to HP pump Fuel return line was loose , tighten the same issue resolved | Closed | Kapil Solanki
3 | 210664954 | 19-04-2024 13:51 | R550 | 25 | GP3.8702.../2320018 | Starting Issue Call By Customer Name :- Navpreet Singh Mobile No :- 9811420154 | Task Start | Tanu Engineering Products Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 11 | As per customer voice , Fuel level wrong showing on controller , controller showing @80% even after filling @100% fuel. | Closed | Kapil Solanki | Will check details
4 | 210664080 | 19-04-2024 10:23 | K1080 | 125.4 | 4H.8041.../2420049 | low fuel level issue Call By: Customer Name : Jagdish .. No : 9354437278 | Task Start | JM. Engineers | Vidyut Engineers - New Delhi | 2.7 | SD team carry out CC on 16-04-2024 (just 3 days ago) today Fuel level sensor wire faulty, sensing wire damaged, need to replace. | Closed | Kapil Solanki
5 | 210663375 | 18-04-2024 17:47 | K1080 | 125.4 | 4H.8041.../2320152 | Diesel pipe leakage Issue Email By Customer Name:-united power | Open | TEJBIR SINGH | OVN Industries Private Limited - New Delhi |  | Customer not respond to Phone calls | Cancelled | Kapil Solanki
Sr.No | 210661772 | 18-04-2024 16:07 | R810 | 62.5 | T4.8941.../2320253 | Alarm protector issue & Tripping issue Call By: Customer Name : Rehan Khan No : 8700101171 | Closed | Trade and Taxes | Deep Jyoti Electricals and Services - Moradabad | 278 | Customer filled Pooe quality Fuel, Just replaced Fuel filter, Issue resolved. | Closed | Sudhir Awasthi
1 | 210665092 | 19-04-2024 14:36 | K1080 | 125.4 | 4H.8041.../2320121 | Starting Issue Call By: Customer Name :Unmesh Bhai No :8006519930 | Task Start | XPERT POWERGEN PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | 1530 | Tripping issue with SPN/FMI - 51/0 and under speed alarm showing on controller, when applied the load engine was tripping after few minutes , checked the connector or ITV found ok , Mr. Sudip visited the site & found ITV faulty, need to be replace. | Open | Kapil Solanki | Need to check other sites run hr. Need to check working life of ITV. Trail on seeding batch
3 | 210665348 | 19-04-2024 15:27 | SL90 | 250 | F6.8841.../2320030 | Automation issue Call By Customer Name :-Yogesh Mehra Mobile No :-9783595793 | Task Start | Asian Engineering Co. | Vidyut Engineers - New Delhi | 15 | Customer complained about automation issue , but actually the customer questions about cooling down period 3 minute, educated the customer about the same issue resolved | Closed | Kapil Solanki
5 | 210665528 | 19-04-2024 15:52 | DV | 400 | DV8.8542.C4../2420012 | Starting issue Email By - Service Dealer Name -Sonu Rai | Closed | IK. Power Solutions | 420326_1 ¦ Paluck Technologies Ltd. - Gurgaon | 15 | Low DEF level @ 42 %, Just top up & educated Customer, Issue resolved. | Closed | Kapil Solanki
6 | 210665550 | 19-04-2024 16:07 | K1080 | 125.4 | 4H.8041.../2420125 | VOC-: ENGINE NOT TAKING LOAD DUE TO FAILURE OF NON RETURN VALVE IN FUEL LINE Customer Name- Gyan ChaudharyCustomer Number-9810297071 Mode- SR Generated through CDI calling. | Closed | SR. Power Engineers | Vidyut Engineers - Noida | 8.33 | Customer complained about starting issue , engine cranking but not starting, Engineer did not find any issue DG starting and stopping is ok ,on load and without load | Closed | Kapil Solanki | KRM check. Need to check controller start delay setting | KRM does not active
7 | 210665661 | 19-04-2024 16:30 | SL90 | 320 | F6.8802.../2320025 | Trip_Genset_Low_Voltage | Task Start | MANGLA APPARELS INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 41.2 | SPN/FMI - 3031/14 flashing latest version file and under voltage alarm showing on controller and NOX sensor connector was loose, fitted the same issue resolved | Closed | Kapil Solanki
8 | 210666163 | 19-04-2024 17:36 | R550 | 20 | GP3.8601.../2320048 | Red Lamp On Alarm issue Message By Customer Name: Jawana Devasi Number: 8302273537 | Task Start | Beauty Impex Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | Visit pending | Open | Kapil Solanki
10 | 210666179 | 19-04-2024 17:41 | R1190 | 82.5 | 5H.8901.../2320082 | Starting Issue Call By Customer Name :- Vinod. . Mobile No :- 8708962822 | Closed | Jai Residency | M/s OM Diesels Pvt. Ltd. - Rohtak | 17 | Staring issue with showing fuel level low alarm , found fuel level was low, educated the customer about the same issue resolved | Closed | Kapil Solanki
11 | 210666438 | 19-04-2024 19:01 | K1080 | 125.4 | 4H.8041.../2320201 | Starting Issue Call By: Customer Name :Shyam No :9720510257 | Task Start | Aadrika Energy Privet Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 5 | Staring issue due to controller not turning ON, checked the pin no 1,2 found 12 volt ,controller will be replace | Open | Kapil Solanki
12 | 210666787 | 20-04-2024 09:46 | R810 | 62.5 | T4.8941.../2320267 | Oil Leakage Issue Email By Service Dealer Name:-Rahul Sharma | Task Start | Punia Maternity and Orthopaedics Hospital | M/s OM Diesels Pvt. Ltd. - HISAR | 21 | Lub oil leakage from oil drain pipe, Banjo washer was loose, tighten the same issue resolved | Closed | Kapil Solanki
13 | 210666909 | 20-04-2024 10:20 | R810 | 57 | T4.8941.../2320007 | Starting Issue Call By Customer Name :- Puran Number :-7838362256 | Task Start | Nanak Sai Estate LLP. | Vidyut Engineers - Noida | 35.3 | Starting issue due to Emergency switch of panel is turning ON just off the Emergency switch and educated the customer about The same issue resolved | Closed | Kapil Solanki
Sr. No | 210667118 | 20-04-2024 11:00 | DV | 625 | DV0.8501.C4../2320001 | Fuel gauge issue Call by customer Name:- Pardeep Kumar No 9910417830 | Open | Tata Tele services | Vidyut Engineers - New Delhi | 37.43 | AS previously discussed (Fuel gauge not working properly and fuel tank cap are not fitted properly ,after filling 100% fuel sometimes 70%,50%,100% show on controller , found fuel gauge not traveling smoothly , fuel gauge will be change) , SR is opened for change fuel sensor or fuel cap | Closed | Kapil Solanki
1 | 210667366 | 20-04-2024 11:37 | K1080 | 160 | 6H.8475.../2420021 | Low Coolant Level Issue & Tripping Issue Email By Service Dealer Name:-Kaushik | Task Start | S. R. V. Industries | R K Engineers - Meerut | 14.57 | Engine tripping with Over load alarm also in GCU event log multiple DTC 516166 suspected Customer doing Hot shut down, educated to Customer. | Closed | Sudhir Awasth | KRM data check | Check the KRM but does not show any type of overload alarm OR does not capture the data .516166 fault code capture in KRM
3 | 210667637 | 20-04-2024 12:27 | R810 | 57 | T4.8941.../2320166 | Main Alternator Terminal Plate broken Email By-Koel P Name:-Rohit S Jangid | Closed | CAPRI TRANSFORMERS PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - JAIPUR | 31.37 | Main Alternator Terminal Plate Replaced, Issue resolved. | Closed | Gourav Sharma
4 | 210668239 | 20-04-2024 14:56 | K1080 | 125.4 | 4H.8041.../2320004 | Control Panel Issue Call By Customer Name :- Indersen Yadavji Mobile No :- 8826817371 | Closed | ARIHANT INDUSTRIAL EQUIPMENT | Vidyut Engineers - New Delhi | 88.5 | SPN/FMI : 520528/31 & 51/0, Just reset the DTC, For DG starting Changed Relay Card Port from 1 to 2 (NO to NC) | Open | Kapil Solanki | Log file required
5 | 210668412 | 20-04-2024 15:31 | K1080 | 125.4 | 4H.8041.../2320134 | Error Code Issue High Temperature Issue Call By: Customer Name : Kasidh Ahmad No :8445820675 | Closed | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 225.9 | SPN/FMI: 110/3 (Coolant temp Sensor Open Circuit), Need to replace the Sensor. | Open | Sudhir Awasthi | KRM check | KRM does not show in KRM protal.but chec k customer logine than found to the coolant Temp.touch 28 C at 9:49 AM
6 | 210668656 | 20-04-2024 15:59 | DV | 500 | DV8.8501.C4../2320050 | Trip_Genset_Low_Voltage | Task Start | FORECH INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 82.8 | SR is created by KRM , Engineer check the event log found sometime engine was tripping with showing under speed or over Current alarm educated the customer about the same issue resolved | Closed | Kapil Solanki
7 | 210669926 | 20-04-2024 19:15 | K1080 | 125.4 | 4H.8041.../2320088 | Automation Issue Call By Customer Name :- Bhopal Kishan Mobile No :- 9650991118 | Task Start | Shramdeep Appartments | Vidyut Engineers - Noida | 59.12 | Starting issue with emergency stop alarm showing on controller ,found DIG I/P 10 wire was loose, tighten the same issue resolved | Closed | Kapil Solanki | Loose contact agains population data
8 | 210670052 | 21-04-2024 08:27 | R810 | 62.5 | T4.8941.../2420018 | Starting issue Call by customer Name: Mahendra Number:9996111113 | Task Start | VICKY CHEMICALS INDUSTRIES | M/s OM Diesels Pvt. Ltd. - Rohtak |  | Customer not allow to check the DG , as per customer voice, he resolved the issue itself. | Closed | Kapil Solanki
Sr. No | 210671646 | 22-04-2024 08:28 | K1080 | 200 | 6H.8435.../2320032 | DG Set not starting Issue Email By GOEM Name:-MAYUR VIRA | Task Start | Oil India Limited | Rajdhani Diesels and Electricals - Jodhpur |  | SPN/FMI - 1761/18,520528/31,1761/14, DEF level was @0% topup the DEF and clear the fault code , educated the customer about same issue resolved | Closed | Gourav Sharma
1 | 210671776 | 22-04-2024 10:00 | R810 | 57 | T4.8941.../2320007 | Starting Issue Call By: Customer Name :Puran . No :7838362256 | Task Start | Nanak Sai Estate LLP. | Vidyut Engineers - Noida | 38.4 | DG was tripping with under speed or over voltage alarm showing on controller , found unbalance load (12A,56A,68A at that time ), educated the customer to balance the Load. | Closed | Kapil Solanki | KRM check | KRM does not availble at KRM protal
3 | 210679208 | 23-04-2024 12:49 | K1080 | 125.4 | 4H.8041.../2320006 | Adblu low level issue Call by customer Name:- Shubham Goyal No:- 9255555939 | Open | SHRI BALAJI POLYMERS | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 29.49 | DEF level not showing correctly, even filling @80 % , but DEF level was showing @38% , found DEF level float was stuck , the float was cleaned by hot water issue resolved | Closed | Kapil Solanki
4 | 210679181 | 23-04-2024 12:38 | R810 | 57 | T4.8941.../2420078 | KRM issue. Email By Service Dealer Name:-Pooja Sharma | Open | Mangalam Childrens Hospital | Pratap Diesels Pvt. Ltd. - JAIPUR | 11.51 | AVR burnt due to Output Connection R Y B wire in Loose condition at Terminal Plate, Need to Replace AVR Card. | Open | Gourav Sharma
5 | 210678988 | 23-04-2024 12:07 | K1080 | 125.4 | 4H.8041.../2420059 | Display Issue Call By Customer Name :- Rajnish Kumar Number :-9649880643 | Open | Sath Guru Engineering | Pratap Diesels Pvt. Ltd. - JAIPUR |  | MOV failure. RRA assembly arranged | Open | Gourav Sharma | KRM | That is wrong statement in drive .main observation urea Percentage does not show in contteroller.
6 | 210676583 | 23-04-2024 11:27 | SL90 | 320 | F6.8802.../2420024 | Display Ala-ram issue Call by customer Name:- Sayyed Ahled No:- 7426911331 | Open | Rosa Herbal Care India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | No Visit done | Open | Gourav Sharma
7 | 210676350 | 23-04-2024 10:46 | R1190 |  | 3H.8902.../2320176 | ENGINE JAM | Task Start | Industrial Equipment | Royal Power Solutions - Zirakpur | 0.1 | Engine not rotating, Team working at GOEM factory (in touch with QA team) | Open | Ved Gupta
8 | 210676024 | 23-04-2024 09:44 | K1080 | 125.4 | 4H.8041.../2320086 | Starting issue Call By Customer Name :-Om Prakash Mobile No :-8800312571 | Task Start | Total Construction | Paluck Technologies Ltd. - Gurgaon | 914 | DG Starting issue due to Loose Battery Terminal, Tighten the same, issue resolved. | Closed | Kapil Solanki
9 | 210675539 | 22-04-2024 19:23 | R810 | 57 | T4.8941.../2320060 | Starting Issue Email By- KGD Name- : Pooja Sharma | Task Start | Jhalani Eye Hospital | Pratap Diesels Pvt. Ltd. - JAIPUR |  | No Visit done | Open | Gourav Sharma
10 | 210675250 | 22-04-2024 17:33 | K1080 | 125.4 | 4H.8041.../2420017 | Starting issue Call By Customer Name:-Mittal No:9837122533- | Closed | Modern Process House | R K Engineers - Meerut | 23.55 | Diesel Leakage from Fuel tank due to 100 % filling, Team educated Customer to fill upto 95% only. | Closed | Sudhir Awasthi
11 | 210673822 | 22-04-2024 15:24 | K1080 |  | 4H.8041.../2320076 | ITV CHANGE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | GOEM team confirmed ITV Jam issue & replaced itself from another Engine, When SD team reached He found ITV in replaced condition. (HO Team suggested GOEM team to change the ITV) | Closed | Sudhir Awasthi
12 | 210673540 | 22-04-2024 14:00 | R1190 | 82.5 | 5H.8901.../2320104 | Mains Voltage & Emergency Shutdown Alarm Issue Call By: Customer Name :Vinod Kumar No :9812194512 | Closed | Max Power Solution | Vidyut Engineers - Noida | 14.36 | SPN/FMI : 516166/0 & 51/0, Yesterday SD team reset the DTC but Today new issue DG tripping with Under Speed alram also SPN/FMI 1761/16 (Low DEF level), Physically 80% DEF availabe in Tank, Team working at site. | Open | Kapil Solanki
13 | 210673287 | 22-04-2024 13:11 | K1080 | 160 | 6H.8475.../2320018 | Fuel Sensor Issue. Call By Customer Name :- Aashish Number :-9811170652 | Closed | ANTRAK AUTOMOTIVE COMPONENTS | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 43 | Low DEF level @ 38 %, Top up DEF also Educated Customer to tup up itself, next time such Visit will not cover under Warranty. | Closed | Kapil Solanki
14 | 210672926 | 22-04-2024 12:02 | K1080 | 125.4 | 4H.8041.../2420047 | KRM issue Call by customer Name: Vinod Kumar Number:9415477589 | Cancelled | Strategic Alliance Management Service Pvt. Ltd. | SAM Engineering corporation - Varanasi Cantt. | 1.5 | Customer unable to Log in @ KRM Mobile App, Just guided Telephononically, No Issue in DG, SR Cancelled. | Cancelled | Sudhir Awasthi
15 | 210660762 | 2024-04-18 12:04 | K1080 | 125.4 | 4H.8041.../2320070 | Engine overheating after ruuning of 1 hour on 110% load at GOEM plant | Task Start | Elmech Engineers | DIVERSE TECHNO SERVICES PRIVATE LIMITED - Ankurhati | 6 | Engine temp reaching 105 deg C after ruuning of 1 hour on 110% load at GOEM plant, replaced the exsisiting engine with another proto engine found that is also reaching 98 deg C. As per CRE team need to send back the engine to KOEL plant | Open | Prosenjit Saha
16 | 210657896 | 2024-04-17 14:58 | K1080 | 160 | 6H.8475…/2420005 | Fan hub campaigning | Completed | IID Centre, Kaliabor, Nagaon,, Assam, NAGAON, ASSAM | Rhino Industrial Equipments Pvt.Ltd., - Nagaon | 0.1 | SR is opened due to modified fan hub fitment | Open | Subhrajit Roy
Sr. No | 210657960 | 2024-04-17 14:58 | K1080 | 160 | 6H.8435…/2420010 | Fan hub campaigning | Completed | IID Centre, Kaliabor, Nagaon,, Assam, NAGAON, ASSAM | Rhino Industrial Equipments Pvt.Ltd., - Nagaon | 0.1 | SR is opened due to modified fan hub fitment | Open | Subhrajit Roy
1 | 210397964 | 2024-02-12 17:52 | K1081 | 125.1 | 4H.8041…/2320003 | Fan hub campaigning | Completed | IID Centre, Kaliabor, Nagaon,, Assam, NAGAON, ASSAM | Rhino Industrial Equipments Pvt.Ltd., - Nagaon | 1.1 | SR is opened due to modified fan hub fitment | Open | Subhrajit Roy
3 | 210682725 | 24-04-2024 10:25 | K1080 | 125.4 | 4H.8041.../2320180 | Starting issue Call By Customer Name :-Ramesh Mobile No :-8506043972 | Task Start | C. M. Infrastructure Pvt. Ltd. | Vidyut Engineers - Noida | 27.2 | Starting issue due to battery was discharged , battery charger was not working , the customer took the battery for charging ,battery charger will be change | Closed | Kapil Solanki | Need to check CC report | Check the CC efsr does not found any problem and battery charger connection is ok.
4 | 210683126 | 24-04-2024 11:41 | R1190 | 82.5 | 5H.8901.../2320014 | Automation Issue Call By Â Customer Name :-Ajitpal Singh Mobile No :-9268320772 | Open | National Diesel Works | Vidyut Engineers - Noida | 74.22 | Customer complained about automation issue engineer did not found automation related issue , found coolant was leakage from hose clamp (minor leakage ) tighten the all hose clamp issue resolved | Closed | Kapil Solanki
5 | 210683221 | 24-04-2024 11:53 | R1190 | 40 | 3H.8951.../2320026 | Shutdown Alarm issue Call By Customer Name: Sumeet Kanwar Number: 9810002039 | Open | Rosy Arts | Vidyut Engineers - Noida | 27.1 | Starting issue due to SPN/FMI - 97/2 just clear the same issue resolved | Closed | Kapil Solanki | KRM check | check the KRM data and97/2 fault code availble the customer login
6 | 210682362 | 24-04-2024 09:44 | SL90 | 320 | F6.8802.../2320006 | Trip_Genset_Low_Voltage | Open | Super Seal India Ltd. | Paluck Technologies Ltd. - Faridabad | 136 | Tripping issue with under voltage alarm, found controller genset voltage wire RG (pin 34 ) was loose, tighten the same issue resolved | Closed | Kapil Solanki
F | 210682345 | 24-04-2024 09:38 | K1080 | 125.4 | 4H.8041.../2420131 | Tripping Issue Call By Customer Name :- dienesh Chandra Number | Open | Statcon Energiaa Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 2 | starting issue due to inside the panel MCB (DC) wire was loose ,tighten the same and SPN/FMI - 3031/14 flashing the latest version file | Closed | Kapil Solanki
8 | 210682331 | 24-04-2024 09:37 | SL90 | 250 | F6.8841.../2420004 | Controller issue & Display issue Call by customer Name:- Prakash .. No:- 7428506588 | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 24 | KRM Network issue, Placed the KRM antenna Outside the Canopy & reinserted SIM Card also Low DEF level Quotation submitted by SD. | Closed | Kapil Solanki
9 | 210682306 | 24-04-2024 09:27 | R550 | 20 | GP3.8604.../2420117 | Return fuel Pipe Was Broken. | Open | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - JAIPUR |  | No Visit done | Open | Gourav Sharma | Details required
10 | 210681943 | 23-04-2024 19:02 | R810 | 57 | T4.8941.../2320239 | Starting issue Call By Customer Name:-RAJKUMAR SHARMA No:-9971635522 | Open | Motorcraft India Pvt. Ltd. | Vidyut Engineers - Noida | 15.33 | Starting issue due to Controller was not turning ON , found controller positive (2D) supply was loose , tighten the same issue resolved | Closed | Kapil Solanki
11 | 210681833 | 23-04-2024 18:15 | SL90 | 320 | F6.8802.../2320054 | Error code issue Call By: Customer Name :-Krishna Gopal Mobile No :- 7388874982 | Task Start | Newtech Vinyl | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 74 | SPN/FMI - 1761/16 DEF level was @48% top up the DEF and educated the customer about the same issue resolved | Closed | Kapil Solanki
12 | 210681045 | 23-04-2024 16:36 | SL90 | 250 | F6.9052.../2300002 | Oil Leakage Issue Call By Customer Name:rekha Rav No:7665887225 | Open | PERENNIAL TECHNOLOGY PVT LTD | Megatron Engineers - Hoshiarpur |  | Asset mapped with SD Unique Techno Services Pvt Ltd. - Jamnagar | Open | Ved Gupta | Need to check with pulse | 23 April 2024 Asset transfer to new SD - UTS Jamnager
13 | 210680670 | 23-04-2024 15:32 | K1080 | 160 | 6H.8475.../2320002 | Abnormal sound issue & Starting issue Call by customer Name:- Om Bir Singh No:- 9717279844 | Task Start | HNA. Contracting & Trading LLP. | Vidyut Engineers - Noida | 18.1 | SPN/FMI : 97/5, 520527/16 & 4365/2, Found WIF Sensor connector in detached condition, Connect the same & reset DTC, Issue resolved. | Closed | Kapil Solanki | KRM check | found it 97/5 fault code in 3 days and does not other fault code in 10 days
14 | 210680666 | 23-04-2024 15:32 | SL90 | 320 | F6.8802.../2420008 | Starting issue and Preventive Maintenance Call By Customer Name :-Keshaw Ram Yadav Mobile No :-9811063408 | Closed | Gyan Devi Sr Sec School | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2.1 | Customer (School Principal) not aware of DG starting procedure, Educated Customer, Issue resolved. | Closed | Kapil Solanki
Sr. no | 210679516 | 23-04-2024 13:37 | K1080 | 125.4 | 4H.8041.../2320201 | Controller Faulty Issue Email By Service Dealer Name:-Saurabh Singh | Closed | Aadrika Energy Privet Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 6 | GCU display blank (Firm version 640 C, Replaced GCU Unit but after Programming Fuel % issue, Need to Reproramme the same. | Open | Kapil Solanki
1 | 210679448 | 23-04-2024 13:24 | K1080 | 125.4 | 4H.8041.../2420027 | Oil Leakage Email By - Service Dealer Name - Saurabh Singh | Closed | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 763 | Oil Leakage from Flywheel side (Suspected Leakage from Oil seal), Customer given time for Tomorrow. | Open | Kapil Solanki | Details required
3 | 210683406 | 24-04-2024 12:16 | K1080 | 160 | 6H.8475.../2420016 | Amber Lamp Alarm issue Call By Customer Name :-Balram Singh Mobile No :-7983511019 | Task Start | Mahalaxmi Crafts & Tisseus Pvt. Ltd. | R K Engineers - Muzaffarnagar | 5 | SPN/FMI: 516166/0 & 3218/8 (Nox Sensor Connector), Customer practicing Hot shut down, Educated Customer. |  | Sudhir Awasthi | KRM details check | check one month KRM data but genset does not show 3218/8 and 516166/0 fault code active repet now.custmor practcing hot shut down now.
4 | 210683775 | 24-04-2024 13:26 | DV | 500 | DV8.8501.C4../2320041 | Amber Warning issue Email By Service Dealer Name:- Megatron Engineers | Task Start | Ian Macleod Distillers India Pvt. Ltd. | Megatron Engineers - Amb | 65 | SPN/FMI - 1761/16 DEF level was @ 45% top up the DEF and educated the customer about the same issue resolved | Closed | Ved Gupta
6 | 210683815 | 24-04-2024 13:34 | R1190 | 30 | 3H.8902.../2320002 | MCB Lamp On Off issue Call By Customer Name :-Praveen Mobile No :-9582297314 | Task Start | Rajeshwari Petrochem Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 34 | SPN/FMI - 2791/31, 5838/1 EGR valve connector was opened and cleaned(no any dust found). and clear the DTC issue resolved. | Closed | Kapil Solanki |  | check the KRM and found it the2791/31 and 5838 /1 in KRM protal and that fault active till 3 April.
7 | 210683884 | 24-04-2024 13:51 | K1080 | 125.4 | 4H.8041.../2320124 | Starting Issue Call By: Customer Name :Puran . No :7838362256 | Closed | Nanak Sai Estate LLP. | Vidyut Engineers - Noida | 5.12 | Engine was not starting , engineer tighten the fuel line all benjo washer , issue resolved (E-feed pump not installed ) | Closed | Kapil Solanki
8 | 210684438 | 24-04-2024 15:58 | SL90 | 320 | F6.8802.../2320017 | lockout issue Call By: Customer Name :Kuldeep Sharma No :8684002063 | Closed | MT AUTOCRAFT | M/s OM Diesels Pvt. Ltd. - Rohtak | 153.17 | DG was tripping SPN/FMI - 3364/8 (DEF quality error), 1761/16, 516166/0, 1761/17 Customer top DEF before SD reaching, just clear the DTC | Closed | Kapil Solanki
9 | 210684725 | 24-04-2024 16:54 | K1080 | 125.4 | 4H.8041.../2320086 | Starting Issue Call By: Customer Name :Om Prakash No :8800312571 | Completed | Total Construction | Paluck Technologies Ltd. - Gurgaon | 925 | DG Starting issue in morning first crank found Partially discharged (11 Volts), Static Cherger connected still issue. Connected another DG Battery, Engine started normally, Recharged Old Battery then Connected, Kept under observation. | Open | Kapil Solanki | Battery tester report found ok
10 | 210684764 | 24-04-2024 17:00 | R810 | 62.5 | T4.8941.../2420005 | Low Fuel Issue Email By-Service Dealer Name:-Madan Chhimpa | Closed | V. S. Generators Service | Paluck Technologies Ltd. - Gurgaon | 4 | fuel level was not showing on controller, found fuel level sensor connector was loose (Play in connector), fitted properly the same issue resolved | Closed | Kapil Solanki
11 | 210685566 | 24-04-2024 18:01 | R1190 | 30 | 3H.8902.../2320054 | Trip_Genset_Low_Voltage | Open | Asha Sharma | Paluck Technologies Ltd. - Ghaziabad |  | SR generated by KRM , SD team contacted customer , there is no issue SR will be cancel | Cancelled | Kapil Solanki | KRM check | check the KRM and found it genset low voltage alarm show.that resone SR genrate.
12 | 210685589 | 24-04-2024 18:12 | SL90 | 320 | F6.8802.../2420003 | Oil Â Leakage Issue Call By Customer Name :- Yadram Number :-9024620248 | Open | Rajaj Jhiriwal | Pratap Diesels Pvt. Ltd. - JAIPUR |  | visit pending | Open | Kapil Solanki
13 | 210685732 | 24-04-2024 19:28 | DV | 500 | DV8.8501.C4../2320028 | Tripping issue Call By: Customer Name :Narula ... No :9971777377 | Task Start | Neel Kamal Enterprises Private Limited | Paluck Technologies Ltd. - Faridabad | 5.46 | As per customer voice ,engine does not start when there is 30 % fuel, found fuel suction tube was short , GOEM replace the tube | Open | Kapil Solanki
14 | 210686100 | 25-04-2024 08:42 | K1080 | 200 | 6H.8435.../2320029 | Battery and Starting issue Call By Customer Name :-Vimal Kumar Mobile No :-9717984848 | Task Start | KMSP. Industries | Paluck Technologies Ltd. - Ghaziabad | 38 | Starting issue due to battery terminal was loose , tighten by Customer, guided Telephonically, SR cancelled | Cancelled | Kapil Solanki
15 | 210686105 | 25-04-2024 08:48 | SL90 | 320 | F6.8802.../2320054 | Error code issue Call By: Customer Name :-Krishna Gopal Mobile No :- 7388874982 | Open | Newtech Vinyl | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 77 | SPN/FMI - 3031/14 just flashing the latest version file. | Closed | Kapil Solanki
Sr. no | 210686211 | 25-04-2024 10:02 | SL90 | 250 | F6.8841.../2320019 | Canopy Door Issue Call By: Customer Name : Narendra Nagar No :9811818373 | Task Start | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 80.5 | Panal site door was not closing properly , tighten the door lock adjusting bolt issue is resolved | Closed | Kapil Solanki
1 | 210686348 | 25-04-2024 10:40 | K1080 | 160 | 6H.8475.../2420021 | Loding issue Call By Customer Name : -Sndip Kumar No :-9990372382 | Open | S. R. V. Industries | R K Engineers - Meerut | 15 | Yesterday AO team visited for Customer meet Customer reported Coolant Consumption issue (Two time Topped up recover Bottle always found empty) also SPN/FMI 516166/0, Team found Cool down time 30 Sec, corrected to 5 Min. Multiple Tripping with Under speed alram. Checked Harness found One relay point loose (K88) | Open | Sudhir Awasthi | KRM check
3 | 210686472 | 25-04-2024 11:05 | R810 | 62.5 | T4.8941.../2320264 | Trip_Genset_Low_Voltage | Task Start | A.P.GENERATORS | Paluck Technologies Ltd. - Gurgaon |  | SR generated by KRM, SD team contacted customer , there is no issue SR will be cancel | Closed | Kapil Solanki | KRM check | check the KRM data and found it the genset low voltage alarm .
4 | 210686526 | 25-04-2024 11:10 | K1080 | 125.4 | 4H.8041.../2420027 | Oil Leakage Issue Email By: Service Dealer Name :Saurabh Singh | Closed | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 794 | Oil leakage from flywheel side, found oil seal was damage, Replaced Oil seal, issue resolved | Closed | Kapil Solanki
5 | 210686608 | 25-04-2024 11:37 | K1080 | 125.4 | 4H.8041.../2320139 | Alarm issue Call By Customer Name : -Nitin No :-8447344441 | Closed | Vijay Lakshmi Transoltions Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 17 | SPN/FMI - 7026/5 found metering unit connector was loose, fitted the metering unit and clear the same issue resolved | Closed | Kapil Solanki | Need to check. KRM | check the KRM found 7026/5 fault code active now and that fault active 24 april till data.
6 | 210686681 | 25-04-2024 11:55 | DV | 500 | DV8.8501.C4../2320027 | Coolant leakage Issue Call By Customer Name :- Pradeep Verma Mobile No :- 9582199953 | Closed | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 54 | coolant overflow from the recovery tank, filled the coolant above H mark educated the customer about the same issue resolved. | Closed | Kapil Solanki
7 | 210686842 | 25-04-2024 12:21 | K1080 | 125.4 | 4H.8041.../2320180 | High Belwer Alarm issue Call By Customer Name :-Ramesh Mobile No :-8506043972 | Closed | C. M. Infrastructure Pvt. Ltd. | Vidyut Engineers - Noida | 27.57 | SPN/FMI - 3031/14 ,4375/11, 2802/4, just flashing the latest version file , AS previously discussed (Starting issue due to battery was discharged, no output from battery charger, Electrician visited and found battery charger main supply wire damaged, corrected the same issue resolved | Closed | Kapil Solanki
8 | 210687188 | 25-04-2024 13:31 | K1080 | 125.4 | 4H.8041.../2320134 | Error Code issue Call By Customer Name :- Kasidh Ahmad Mobile No :-8445820675 | Closed | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar |  | DTC: 110, SD team performed the Coolant Temp Sensor replacement work. | Closed | Sudhir Awasthi | Under monitoring
9 | 210687401 | 25-04-2024 14:15 | K1080 | 125.4 | 4H.8041.../2420107 | Amber Lamp On alarm issue Call By Customer Name :- Chandra Mohan Mobile No :- 9911823339 | Closed | P. V. L. Tag Factory INDIA Pvt. Ltd. | Vidyut Engineers - Noida | 4.3 | SPN/FMI - 3031/14,4375/11 just clear the DTC , the latest version Flashing need to update. | Open | Kapil Solanki
10 | 210687564 | 25-04-2024 14:52 | R1190 | 30 | 3H.8902.../2320159 | Shut Down Alarm issue Message By Customer Name: Ankur Kaushik Number: 9958177838 | Closed | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 32 | Starting issue with showing fuel level low alarm, engineer before reach the site customer top up the fuel , could not reset the alarm , engineer just reset the alarm, educated the customer about the same issue resolved | Closed | Kapil Solanki
11 | 210687580 | 25-04-2024 14:59 | R1190 | 40 | 3H.8951.../2320116 | ENGINE NOT STARTING | Task Start | B. N. P. Enterprises | Vidyut Engineers - New Delhi | 1.45 | Starting issue due to 12RB1 relay board RL2 (output wire) was loose ,tighten the same issue resolved (LINE REJECTION SR) | Closed | Kapil Solanki | GOEM issue
12 | 210687594 | 25-04-2024 15:05 | R550 | 20 | GP3.8601.../2320061 | ENGINE NOT STARTING | Task Start | LIBRA DIESEL ENGINEERS... | Vidyut Engineers - New Delhi | 35 | SR opened by OEM , tripping issue with showing emergency stop alarm after 1-2 hours of running , engineer did not found issue , (LINE REJECTION SR). | Open | Kapil Solanki | Under observation
13 | 210687960 | 25-04-2024 16:09 | R1190 | 82.5 | 5H.8901.../2320101 | Red Lamp Alarm Issue Call By: Customer Name :Sunil . No : 9899859761 | Closed | Alliance Web Solution | Vidyut Engineers - Noida | 14 | DM2 - SPN/FMI - 516166/0 just clear alarm and change the cooling down period 30 sec to 1 min, educated the customer do not stop double press stop (hot shutdown) | Open | Kapil Solanki
14 | 210688117 | 25-04-2024 16:46 | K1080 | 125.4 | 4H.8041.../2320073 | Voltage Issue Email By Service Dealer Name:-Saurabh Singh | Closed | GUPTA SAREES CENTRE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 124 | Customer having issue in 4 AC installed at 1st Floor but inssue in Building wiring also Low DEF level, Top up the same. Issue resolved. | Closed | Kapil Solanki
Sr. No | 210689470 | 25-04-2024 17:49 | SL90 | 320 | F6.8802.../2420022 | Red Lamp Alam issue Call By Customer Name:-Upander No:-9215860371 | Task Start | Karan Power System | Vishal Power Systems - Karnal | 18 | DEF level was low @42% educated the customer topup the DEF. | Closed | Kapil Solanki
1 | 210690147 | 26-04-2024 07:21 | SL90 | 250 | F6.8841.../2420004 | Amber Lamp Alarm issue Call By Customer Name:-Tej Pratap Singh No:-7428506588 | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 26 | SPN/FMI - 3031/14 ,1761/16 ,516166/0 just clear the DTC, need to update latest version file Flashing. | Open | Kapil Solanki
3 | 210690759 | 26-04-2024 11:54 | DV | 500 | DV8.8501.C4../2320027 | Error Code issue Call By Customer Name:- Pradeep Verma No:-9582199953 | Task Start | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 56 | ECU_DCU Communication error, Just Updated ECU & DCU Cal file, Issue resolved. | Closed | Kapil Solanki | Need details. KRM check
4 | 210690831 | 26-04-2024 12:17 | K1080 | 125.4 | 4H.8041.../2320113 | Emergency Alarm Issue Call By Customer Name :- Rahul . Number :- 9958415847 | Closed | Pristine Medicure Pvt Ltd. | Paluck Technologies Ltd. - Gurgaon | 47 | Starting issue with showing emergency stop alarm , emergency switch connections tighten and issue resolved | Closed | Kapil Solanki
5 | 210691157 | 26-04-2024 13:24 | K1080 | 125.4 | 4H.8041.../2420073 | Alrm issue Call By Customer Name :Ashok Kumar No : 9990178023 | Closed | Gunno Fashions Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 8 | SPN/FMI - 516166/0 just clear the same issue resolved | Closed | Kapil Solanki | DTC discription change
6 | 210691878 | 26-04-2024 16:26 | SL90 | 320 | F6.8802.../2320020 | Trip_Genset_Low_Voltage | Task Start | SSF POLYMERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | DG was tripping with under voltage alarm found Intake Manifold Gasket in damaged condition was damage, SD Team will replace the gasket today. | Open | Kapil Solanki |  | That is second case of gasket failure but asset is same.
7 | 210692989 | 27-04-2024 08:38 | K1080 | 160 | 6H.8475.../2420018 | Abnormal sound issue Call by customer Name: Vikas Saini Number:9813775086 | Open | Unicare Fire Safety India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 140 | Abnormal sound from DG as Exhaust Pipe was in loose, Tighten the same, Issue resolved. | Closed | Gourav sharma
8 | 210693529 | 27-04-2024 11:37 | R550 | 15 | GP3.8501.../2320038 | Tripping Issue Call By Customer Name :- Mahes Singh No :- 9650577296 | Closed | OPTIMAS ENERGY INDIA | Vidyut Engineers - Noida | 7.2 | DG was tripping due to unbalanced load( R,Y,B- 28A , 3A, 5A ), educated the customer about the same issue resolved | Closed | Kapil solanki | KRM check. CC checklist | cc found unblance load R-19A,Y-3A,B-5A and check the KRM data found the somthing 500% load differance between R&B Phase
10 | 210693692 | 27-04-2024 12:03 | R810 | 57 | T4.8941.../2320115 | Starting issue Call By Customer Name :SP SINGH No : 9818415169 | Closed | Anergy Instruments Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 29 | Starting issue due to battery was discharge, battery charger was not connected (CC date : 29/11/2023), connected the same issue resolved | Closed | Kapil solanki
11 | 210693880 | 27-04-2024 12:39 | K1080 | 160 | 6H.8475.../2320024 | Amber Lamp Alarm Issue Call By Â Customer Name :-Zameer Ahmed Mobile No :-9518251673 | Task Start | CHRYSO INDIA PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Engineer on site | Open | Gourav sharma | Details pending
12 | 210694360 | 27-04-2024 14:31 | K1080 | 125.4 | 4H.8041.../2320083 | Smoke Issue Email By Service Dealer Name:-Javed Khan | Closed | AKASH GENERATOR SERVICES | Vidyut Engineers - New Delhi | 594 | DEF level low @42% top up the DEF and DM2 SPN/FMI - 516166/0 JUST clear the code and educated the customer about the same issue resolved | Closed
13 | 210694589 | 27-04-2024 15:22 | SL90 | 320 | F6.8802.../2320021 | Sound issue Call By: Customer Name :Lovkush . No :8739904306 | Task Start | Marvel Ceramics Pvt Ltd | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Engineer on site | Open | Gourav sharma
14 | 210694710 | 27-04-2024 15:38 | R550 | 15 | GP3.8501.../2320041 | Maintenance Due Alarm issue Call by Customer Name :-Govind ... Number :- 8393890100 | Closed | Growmore Signnage LLP. | Espiem Engines & Machines (P) Limited - Agra | 61 | Customer registered SR for 1st Service. | Closed | Sudhir Awasthi
15 | 210695245 | 27-04-2024 17:17 | K1080 | 125.4 | 4H.8041.../2420084 | Trip_Genset_Low_Voltage | Task Start | Aggaarwal Art & Pattern Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 22.48 | KRM generated SR, engineer did not found any issue on DG, Customer confirmed DG not started in 1st Crank in Auto mode. | Closed | Kapil solanki | KRM check | Check the KRM data and found low voltage in auto mode.
16 | 210695277 | 27-04-2024 17:21 | R1190 | 82.5 | 5H.8901.../2320065 | Adblu issue & M2 ECU Fault Alarm Issue Call By Customer Name : Ravindra Kumar No: 8979304008 | Task Start | RK. Generator Services | Vidyut Engineers - Noida | 33 | DEF level not showing on controller, Need to programming on controller | Open | Kapil solanki
17 | 210695386 | 27-04-2024 17:31 | K1080 | 160 | 6H.8475.../2420006 | Display Issue Call By Customer Name :-Shubahm Kumar Mobile No :-6306784581 | Task Start | India Shine Technologies | Paluck Technologies Ltd. - Faridabad | 170 | Fuel gauge not working properly,after filling 100% fuel,showing only 30%, found fuel gauge float unit not moving smoothly , fuel gauge need to be replace. | Open | Kapil solanki | Need site details.
18 | 210697062 | 27-04-2024 23:06 | DV | 500 | DV8.8501.C4../2320050 | Trip_Genset_Low_Voltage | Open | FORECH INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 86 | In Event log Multiple Alarm related to Low Voltage/under frequency & Over Current, Suspected DG running overload, Check Fuel line also but no abnormality observed. Educated Customer to use DG @ 80 % Load for best efficiency. | Closed | Kapil Solanki | KRM data check | check the KRM Found multiple under voltage details. when Genset stop and start that fault code activeted.
19 | 210697435 | 28-04-2024 10:20 | R1190 | 82.5 | 5H.8901.../2320102 | High Voltage issue Call by customer Name: Kishan Number:7409096174 | Task Start | Vuenow Marketing Services Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 9.1 | Multiple error code (SPN/FMI: 3031/14, 1761/16, 520527/18, 3364/10, 3364/27 & 4225/1), Checked Harness for any loose connection, found OK then updated ECU Cal file afterthat taken half hour Load trial, found no such DTC appear again. | Closed | Kapil solanki |  | KRM does not activeted.
20 | 210697482 | 28-04-2024 11:07 | DV | 500 | DV8.8501.C4../2320082 | Self Starter issue & MCB Issue Call by Customer Name :-Anand Number :- 9911319889 | Open | PG. Electroplast Ltd. | Paluck Technologies Ltd. - Ghaziabad | 43 | MCCB issue, no Output Voltage in 'Y' Phase, Informed to Quality team to takeup with MCCB Vendor as it was replaced by Supplier on 17th Apr. | Open | Kapil solanki
S.no | 210697484 | 28-04-2024 11:25 | R550 | 15 | GP3.8501.../2320036 | Starting Issue Call By Customer Name :- Gaurav . Mobile No :- 9720207860 | Closed | AA. Innovators Private Limited | Paluck Technologies Ltd. - Ghaziabad | 3.7 | Customer registered Starting issue, SD team visited & found Engine starting but showing Low Voltage warning, Just reset the warning, Perform triall found no issue. | Closed | Kapil Solanki | KRM check | KRM does not sart .
1 | 210697628 | 28-04-2024 14:34 | SL90 | 250 | F6.8841.../2420019 | Starting Issue Call By Customer Name :-Naveen Mobile No :-8800806887 | Open | G.K. ENTERPRISES PVT. LTD. | Vidyut Engineers - Noida | 21 | Starting issue due to DEF level was low @0% educated the customer and top up the DEF issue resolved. | Closed | Kapil solanki
3 | 210699795 | 29-04-2024 18:52 | 200 | 6H.8435.../2320031 | Starting Issue Email By Service Dealer Name:-Bharat Singh | Task Start | Oil India Limited | Rajdhani Diesels and Electricals - Jodhpur | 174 | DG running OK, 1st CSP Serive due. | Closed | Gourav Sharma
4 | 210699398 | 29-04-2024 17:13 | 160 | 6H.8475.../2320028 | Error Code Issue Call By: Customer Name : Rabbani. No :9015201975 | Task Start | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 32.58 | SPN/FMI; (1761/16 Low DEF level @ 47 % ) top up the same and also , (920/5 Audio relay open) ( 3364/8), (97/2 Water in fuel) in DM 2 alarm was shown clear the DTC issue resolved. | Closed | Kapil Solanki | Need to check KRM | KRM does not activeted.
5 | 210699282 | 29-04-2024 16:53 | 125.4 | 4H.8041.../2420125 | Diesel Tank Issue Call By Â Customer Name :-Shyam M. Tiwari Mobile No :-9971438718 | Task Start | SR. Power Engineers | Vidyut Engineers - Noida | 14.5 | Customer complaint regarding Fuel tank Lock not getting Open. guided to the customer about the same issue resolved. | Closed | Kapil Solanki
6 | 210699049 | 29-04-2024 16:10 | 160 | 6H.8475.../2320037 | Ambarlamp Alram Issue Call By Customer Name : -Deepak . Number : -8800334321 | Closed | Sunex Precision Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 25 | SPN/FMI: (1761/16 Low DEF level @ 16 % ) top up and clear the DTC issue resolved and also educate the customer about the same. | Closed | Kapil Solanki
7 | 210699001 | 29-04-2024 16:05 | 82.5 | 5H.8901.../2320104 | Throat valve to be Change Email By Service Dealer Name:-Shiv | Closed | Max Power Solution | Vidyut Engineers - Noida | 38.6 | SPN/FMI: 51/0 (throttle valve is stuck in open position) HO Quality team visited the site and replaced the ITV. | Closed | Kapil Solanki
8 | 210698872 | 29-04-2024 15:50 | 500 | DV8.8501.C4../2320014 | Starting issue Call by customer Name:-Peeyush Kumar No:-9456043186 | Open | RPS CHEMICAL INDUSTRIES PRIVATE LIMITED | R K Engineers - Muzaffarnagar | 146 | Engine starting issue due to week Battery (One Battery Voltage drop upto 7 Volts during Cranking) seems One Battery internal Cells Week, SD team will send to TGY for further analyses, DG running with Float Battery. | Open | Sudhir Awasthi
9 | 210698842 | 29-04-2024 15:43 | 125.4 | 4H.8041.../2320123 | Automation Issue Call By Customer Name :-Akash Tawar Mobile No :-8824468473 | Task Start | Sarvodya Infracon Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 40 | DG Auto Starting issue (Non KOEL Panel), Negative Connection missing, Connected the same, Issue resolved. | Closed | Kapil Solanki
10 | 210698609 | 29-04-2024 15:08 | 320 | F6.8802.../2320034 | Battery Charger issue Call By Customer Name :- Rohit Number :-7017202883 | Task Start | Maxwel Exporters | R K Engineers - Meerut | 28 | Battery was discharged due to battery charger was not connected (CC date - 12/01/2024) connected the same issue resolved. | Closed | Sudhir Awasthi
11 | 210698450 | 29-04-2024 14:46 | 125.4 | 4H.8041.../2420160 | Error Code Issue Call By Customer Name :-Kamal Sharma Mobile No :-8262905463 | Task Start | M/s. KC. Villas Fagu | SAAN Industrial Solutions - Shimla |  | Multiple SPN/FMI : (1761/16. 1761/14, 1761/18, 100/1, 3031/15, 3031/28, 520527/18, 3364/10 & 3364/27) Pertaining to DEF Qulaity/Level, Voltage supply at DEF level sensor found low (02 Volts), on thorough Wiring inspection found 2 Amp fuse in 2A Connection faulty, Corrected the same, Issue resolved. | Closed | Ved Gupta
12 | 210698441 | 29-04-2024 14:46 | 82.5 | 5H.8901.../2320056 | Under Speed Alarm Issue Call By Customer Name : Kuldeep ... No : 9315151140 | Closed | Arise Ventures LLP. | Vidyut Engineers - Noida | 34.26 | SPN/FMI: (6595/0 Dosing chk err),( 4225/1), (3224/2) code was shown..just clear the DTC and checked DG on load (half hours) running ok. | Closed | Kapil Solanki
13 | 210698438 | 29-04-2024 14:45 | 125.4 | 4H.8041.../2320113 | Emergency Stop Issue Call By: Customer Name :Shiv Sagar Verma No :9984986603 | Task Start | Pristine Medicure Pvt Ltd. | Paluck Technologies Ltd. - Gurgaon | 50 | DG was tripping due to suddenly emergency stop alarm was showing in display..checked panel wiring and found XDBK1 (2C) connector loose retighten the same issue resolved.and checked DG on load (30 min ) running ok. | Closed | Kapil Solanki
14 | 210701251 | 30-04-2024 12:13 | 500 | DV8.8501.C4../2320052 | Tripping Issue Call By: Customer Name :Lalit Kumar No :9999286305 | Task Start | B. N. P. Enterprises | Vidyut Engineers - New Delhi | 7.2 | DG was tripping due to an emergency stop alarm was shown..checked and found the canopy emergency switch connection was loose (54 no wire) ..tighten the same issue resolved. | Closed | Kapil Solanki
15 | 210700818 | 30-04-2024 11:00 | 250 | F6.8841.../2320047 | Oil Leakage Issue Call By Customer Name :-Sushil Mobile No :-8860089233 | Task Start | TRACTEBEL ENGINEERING PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 55 | Oil leakage due to loose oil drain plug tighten the same issue resolved. | Closed | Kapil Solanki | CSP check | A check completed on 23/03/2024.after two CM SR created to the related Abnormal sound and starting issue.
| 210700471 | 30-04-2024 09:54 | 125.4 | 4H.8041.../2420032 | Power supply Issue Call By Â Customer Name :-Sanjeet . Mobile No :-8750654164 | Task Start | CRS. Realtech & Buiders | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 25 | Customer panel issue (Mains MCB tripping)..Contractor not holding.. Resolved with the vendor. | Closed | Kapil Solanki
| 210700416 | 30-04-2024 09:36 | 62.5 | T4.8941.../2420187 | Over Heating Issue Call By Â Service Dealer Name :-Vikas Mobile No :-7027820033 | Task Start | Shree Balaji Inds | M/s OM Diesels Pvt. Ltd. - Rohtak | 8.37 | Customer complaint regarding over heating issue.engineer visited site and found sometime engine start or sometime engine failed to start also ikonnect was showing ecu error no response from ecu found ignition relay input wire was loose(4 no) or dongle (C Pin ) was inside the dongle just correct the same issue resolved. | Closed | Kapil Solanki
7