## Sheet1
KVA Rating | SPN | FMI | Component / System | Priority | Possible Cause
25 - 57 | 97 | 2 | Water in fuel sensor | Moderate | Water buildup in the fuel filter
25 - 57 | 97 | 5 | Water in fuel sensor | Moderate | Sensor Supply Voltage Check
25 - 57 | 100 | 1 | Oil Pressure Sensor | Low | Oil Leakage
25 - 57 | 100 | 3 | Oil Pressure Sensor | Low | Connectors Failure at Oil Pressure sensor and ECU
25 - 57 | 100 | 4 | Oil Pressure Sensor | Low | Supply Voltage Check
25 - 57 | 102 | 3 | Engine Intake Manifold #1 Pressure | High | Connectors Failure at Boost Pressure/Temperaturee sensor and ECU
25 - 57 | 102 | 4 | Engine Intake Manifold #1 Pressure | High | Supply Voltage Check
25 - 57 | 105 | 3 | Engine Intake Manifold 1 Temperature | High | Connectors Failure at Boost Pressure/Temperaturee sensor and ECU
25 - 57 | 105 | 4 | Engine Intake Manifold 1 Temperature | High | Supply Voltage Check
25 - 57 | 110 | 0 | Coolant temperature sensor | Moderate | Air Flow Restricted
25 - 57 | 110 | 3 | Coolant temperature sensor | Moderate | Connectors Failure at Coolant temperature sensor and ECU
25 - 57 | 110 | 4 | Coolant temperature sensor | Moderate | Analog Input Line Pin Short to Ground
25 - 57 | 110 | 16 | Coolant temperature sensor | Moderate | Air Flow Restricted
25 - 57 | 156 | 14 | Injector Bank-1 (4 cylinder) | High | Injector output high side pin short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 157 | 3 | Rail pressure sensor | High | Connectors Failure at Fuel Rail Pressure sensor and ECU
25 - 57 | 157 | 4 | Rail pressure sensor | High | Supply Voltage Check
25 - 57 | 157 | 13 | Pressure relief valve | Moderate | High Pressure fuel drain line restriction
25 - 57 | 157 | 14 | Pressure relief valve | Moderate | High Pressure fuel drain line restriction
25 - 57 | 157 | 31 | Pressure relief valve | Moderate | High Pressure fuel drain line restriction
25 - 57 | 158 | 3 | Battery | Moderate | Alternator Malfunction
25 - 57 | 158 | 4 | Battery | Moderate | Wiring harness Loose connection at alternator & battery
25 - 57 | 190 | 0 | Engine Over Speed | High | Engine over speed detected
25 - 57 | 633 | 3 | Metering unit | Moderate | High Pressure fuel drain line restriction
25 - 57 | 633 | 4 | Metering unit | Moderate | High Pressure fuel drain line restriction
25 - 57 | 633 | 5 | Metering unit | Moderate | High Pressure fuel drain line restriction
25 - 57 | 636 | 5 | Cam Sensor | High | Connectors Failure at Cam Position Sensor and ECU / Supply Voltage Check / Supply Voltage line open Circuit / Supply Voltage line pin to pin short / Sensor Ground Line Open Circuit / Frequency input Line Open Circuit / Frequency input Line Pin to Pin Short / Cam Position Sensor Malfunctioning / ECU Calibration/ ECU Malfuntion
25 - 57 | 636 | 8 | Cam Sensor | High | Excess gap between Cam sensor and tonewheel / Cam Position Sensor Malfunctioning / Failure of Cam shaft Sensing mechanisim / ECU Calibration / ECU Malfunction
25 - 57 | 637 | 2 | Crank Sensor | High | Excess gap between Crank sensor and Flywheel / Crank Position Sensor Malfunctioning / Crank shaft & Flywheel failed / ECU Calibration / ECU Malfuntion
25 - 57 | 637 | 5 | Crank Sensor | High | Connectors Failure at Crank Position Sensor and ECU / Positive Frequency Input line open Circuit/ Positive Frequency Input line pin to pin short / Negative Frequency Input line open Circuit / Negative Frequency Input line pin to pin short / Sensor Ground Line Open Circuit / Sensor Ground line pin to pin short / Crank Position Sensor Malfunctioning / ECU Calibration / ECU Malfuntion
25 - 57 | 651 | 3 | Injector-1 for (4 cylinder) | High | Injector output low side pin short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 651 | 4 | Injector-1 for (4 cylinder) | High | Injector output high side pin short to Injector output side low pin
25 - 57 | 651 | 5 | Injector-1 for (4 cylinder) | High | Connectors Failure at Fuel Injector and ECU
25 - 57 | 652 | 3 | Injector-2 for (4 cylinder) | High | Injector output low side pin short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 652 | 4 | Injector-2 for (4 cylinder) | High | Injector output high side pin short to Injector output side low pin
25 - 57 | 652 | 5 | Injector-2 for (4 cylinder) | High | Connectors Failure at Fuel Injector and ECU
25 - 57 | 653 | 3 | Injector-3 for (4 cylinder) | High | Injector output low side pin short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 653 | 4 | Injector-3 for (4 cylinder) | High | Injector output high side pin short to Injector output side low pin
25 - 57 | 653 | 5 | Injector-3 for (4 cylinder) | High | Connectors Failure at Fuel Injector and ECU
25 - 57 | 654 | 3 | Injector-4 for (4 cylinder) | High | Injector output low side pin short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 654 | 4 | Injector-4 for (4 cylinder) | High | Injector output high side pin short to Injector output side low pin
25 - 57 | 654 | 5 | Injector-4 for (4 cylinder) | High | Connectors Failure at Fuel Injector and ECU
25 - 57 | 898 | 31 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 920 | 3 | Audio actuator relay | Low | Audio actuator relay PWM output line short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 920 | 4 | Audio actuator relay | Low | Audio actuator relay PWM output line short Ground
25 - 57 | 920 | 5 | Audio actuator relay | Low | Audio actuator relay PWM output line Open
25 - 57 | 920 | 12 | Audio actuator relay | Low | Audio actuator relay PWM output line short to Battery Supply voltage
25 - 57 | 1136 | 3 | ECU | High | ECU exposed to heat sources / ECU Calibration / ECU Malfuntion
25 - 57 | 1136 | 4 | ECU | High | ECU exposed to cold sources
25 - 57 | 1485 | 3 | Main relay | Low | ECM main relay Low side (ON/OFF) line short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 1485 | 4 | Main relay | Low | ECM main relay Low side (ON/OFF) line short to line short Ground
25 - 57 | 1485 | 5 | Main relay | Low | ECM main relay Low side (ON/OFF) line Open
25 - 57 | 2791 | 0 | EGR | High | EGR Valve Struck open
25 - 57 | 2791 | 1 | EGR | High | Connectors Failure at EGR Valve and ECU / Analog Input line Open / Sensor Ground line Open / Analog Input Line Pin to Pin Short / Supply voltage line Open / Malfunctioning of EGR Valve / ECU Calibration/ ECU Malfuntion
25 - 57 | 2791 | 2 | EGR | High | Supply voltage line Short to Ground / Analog Input Line Pin to Pin Short / Malfunctioning of EGR Valve / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 3 | EGR | High | EGR valve Positive PWM output line short to Battery Supply (12v)/ Malfunctioning of EGR Valve/ ECU Calibration/ ECU Malfunction
25 - 57 | 2791 | 4 | EGR | High | EGR valve Positive PWM output line short to Ground / Malfunctioning of EGR Valve / ECU Calibration/ ECU Malfunction
25 - 57 | 2791 | 5 | EGR | High | Connectors Failure at EGR Valve and ECU / EGR valve Positive PWM output line Open / EGR valve Negative PWM output line Open / Malfunctioning of EGR Valve / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 6 | EGR | High | High Return current flow from EGR to ECU / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 12 | EGR | High | EGR Positive PWM output pin or Negative PWM Output pin short to battery (12v) for longer time and High current flow to ECU / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 14 | EGR | High | Low Return current flow from EGR to ECU / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 17 | EGR | High | Malfunctioning of EGR Valve / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 18 | EGR | High | Malfunctioning of EGR Valve/ ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 22 | EGR | High | EGR Valve position mismatching with Actual command / ECU Calibration / ECU Malfuntion
25 - 57 | 2791 | 31 | EGR | High | EGR Valve Struck close / ECU Calibration / ECU Malfuntion
25 - 57 | 2802 | 3 | ECU | High | Alternator Malfuntion / ECU Calibration / ECU Malfuntion
25 - 57 | 2802 | 4 | ECU | High | Wiring harness Loose connection at alternator & battery / Alternator Malfuntion / Battery Malfuntion / ECU Calibration / ECU Malfuntion
25 - 57 | 3509 | 3 | ECU | High | Boost Pressure/Temperature, Oil Pressure sensor Supply Voltage ((5v) line Short to ground / ECU Calibration / ECU Malfuntion
25 - 57 | 3510 | 3 | ECU | High | Rail Pressure Sensor, camshaft Speed sensor Supply Voltage ((5v) line Short to ground / ECU Calibration / ECU Malfuntion
25 - 57 | 5314 | 15 | Injector | High | Fuel Injectors malfunctioning / ECU Calibration / ECU Malfuntion
25 - 57 | 5838 | 1 | Inducement | Low | Warning before Level 1 inducement.
25 - 57 | 5838 | 2 | Inducement | Low | Level 1 inducement started.
25 - 57 | 5838 | 3 | Inducement | Low | Level 2 inducement started.
25 - 57 | 5928 | 3 | EGR | High | EGR valve negative PWM output line short to Battery Supply (12v)/ Malfunctioning of EGR Valve / ECU Calibration/ ECU Malfunction
25 - 57 | 5928 | 4 | EGR | High | EGR valve negative PWM output line short to ground / Malfunctioning of EGR Valve / ECU Calibration/ ECU Malfunction
25 - 57 | 7026 | 3 | Metering unit | Moderate | Fuel Metering unit PWM output line short to Battery Supply voltage or Sensor Supply voltage
25 - 57 | 7026 | 4 | Metering unit | Moderate | Fuel Metering unit PWM output line short to Ground
25 - 57 | 7026 | 5 | Metering unit | Moderate | Connectors Failure at Fuel Metering unit and ECU
25 - 57 | 7026 | 12 | Metering unit | Moderate | Fuel Metering unit PWM output line short to Battery Supply voltage
25 - 57 | 516100 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516105 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516106 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516115 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516118 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516119 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516121 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516122 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516123 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516124 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516125 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516126 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516127 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516128 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516129 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516130 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516131 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516132 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516133 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516134 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516135 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516136 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516137 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516138 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516139 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516140 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516141 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516142 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516143 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516144 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516145 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516146 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516147 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516148 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516149 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516150 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516151 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516152 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516153 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516154 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516155 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516156 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516157 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516158 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516159 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516160 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516161 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516162 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516163 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516164 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516165 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516166 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516167 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516168 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516169 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516170 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516171 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516172 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516173 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516174 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516175 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516176 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516177 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516178 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516179 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516180 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516181 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516182 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516183 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516184 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516185 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516186 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516187 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516188 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure
25 - 57 | 516189 | 0 | ECU | High | ECU Malfunctioning / ECU Calibration issue / ECU Internal failure