## Mar 25
SL NO | Zone | Incident no | Creation Date | KVA | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Run hours | Observation | Incident Status | ASM Name | HO remark | Observation -2
1 | NORTH | 211769920 | 28-02-2025 19:45 | 160 | 6H.8475.../2420367 | Red lamp on alarm issue Called by customer Name : JAY PAL Number : 8930670797 | Closed | LALL NURSING & MATERNITY HOME | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 58 | Low def level alarm topup the def then issue resolve | Closed | Kapil Solanki
2 | NORTH | 211769799 | 28-02-2025 18:48 | 58.5 | T4.8941.../2420787 | Door lock Issue Call By Customer Name :- Ram .. Mobile No :-9968421480 | Closed | SETHI BUILDCON | Vidyut Engineers - New Delhi | 3626 | checked the problem, adjust the canopy door lock but door lock not Lock properly,so that required the canopy door lock Lhs-1 to be change, | open | Kapil Solanki
3 | NORTH | 211769654 | 28-02-2025 18:23 | 40 | 3H.8951.../2420449 | DG fault | Closed | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 12 | Found VMR relay not give the output so, need to replace & also 8 pin relay required to be change | Closed | Kapil Solanki
4 | NORTH | 211769626 | 28-02-2025 18:15 | 125.4 | 4H.8041.../2420183 | Over Heating Issue Call By Service Dealer Name :- Lucky sharma Mobile No :- 7503227320 | Closed | VRL LOGISTICS LTD. | Paluck Technologies Ltd. - Gurgaon | 780 | Low Coolant level top up the coolant | Closed | Kapil Solanki
5 | NORTH | 211768754 | 28-02-2025 15:55 | 40 | 3H.8951.../2420461 | LLOP PROBLEM | Closed | Suman Marriage Hall. | Excel Diesel Private Limited - Sultanpur | 77.6 | Found Oil sensor connector was loose so, tightness the same | Closed | Sudhir Awasthi
6 | NORTH | 211768641 | 28-02-2025 15:35 | 500 | DV8.8501.C4../2420020 | Tripping Issue Call By Customer Name :- Ajay Mobile No :-9958214785 | Closed | ESQUIRE TECH.. | Vidyut Engineers - New Delhi | 79 | Canopy Emergency stop alarm check & found wire was loose tightness the same & Connector, Low def level topup the def | Closed | Kapil Solanki
7 | NORTH | 211768568 | 28-02-2025 15:22 | 15 | GP3.8501.../2420359 | DG Complaints | Closed | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 95 | found 8 pin relay faulty after that replaced the relay | Closed | Kapil Solanki | Alert to be release
8 | NORTH | 211768439 | 28-02-2025 15:00 | 7.5 | D3.8305.../2400181 | oil leakage Issue Email By KGD Name:-Sagar Chopra | Closed | Delhi Metro Rail Corporation D. M. R. C. | OVN Industries Private Limited - New Delhi | 16.15 | Found silencer side Exhaust oil through so, bolt was loose & Customer give the load at night after said observation | Monitoring | Kapil Solanki | Need revise input
9 | NORTH | 211768391 | 28-02-2025 14:50 | 30 | 3H.8902.../2420262 | Starting issue Called by customer Name : Lal Number : 7827447526 | Closed | Mrs. Simran Pal | Vidyut Engineers - New Delhi | 13 | Found main relay output connection was loose so, tightness the same | Closed | Kapil Solanki
10 | NORTH | 211768326 | 28-02-2025 14:42 | 15 | GP3.8501.../2421609 | Red Lamp On Alarm & Preventive Maintenance Call By Customer Name :- Sudhir Shukla Mobile No :- 7985061329 | Open | Walnut Bakers | Espiem Engines & Machines (P) Limited - KANPUR |  | Visit pending | open | Sudhir Awasthi
11 | NORTH | 211768299 | 28-02-2025 14:38 | 57 | T4.8941.../2420210 | Starting Issue Call By Customer Name-Abid Number-8750155686 | Task Start | Niraj Marriage Hall | S. R Engines Sales And Service - Mau |  | Engineer visit Today on site | open | Sudhir Awasthi
12 | NORTH | 211768245 | 28-02-2025 14:31 | 82.5 | 5H.8901.../2420373 | Genset Trip | Closed | SHAKTI PACKERS INDIA PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | 26 | Low def level alarm topup the def then issue resolve | Closed | Kapil Solanki
13 | NORTH | 211768242 | 28-02-2025 14:30 | 5.5 | CC1.1013.../2400097 | Electrical Problems | Open | ARUN GEHLOT | Rajdhani Diesels and Electricals - Jodhpur |  | Visit pending | open | Gourav Sharma
14 | NORTH | 211768224 | 28-02-2025 14:28 | 125.4 | 4H.8041.../2320189 | Def tank temp issue | Closed | Rohit Industries | Paluck Technologies Ltd. - Ghaziabad | 163 | SPN/FMI 3031/14 Flash the dummy file | Closed | Kapil Solanki
15 | NORTH | 211768014 | 28-02-2025 13:39 | 125.4 | 4H.8042.C4../2420576 | Fuel sensor not working | Closed | Aravali Garden | Pratap Diesels Pvt. Ltd. - Alwar | 140 | Found XDBK-1,2,3,4 connectors wiring loose tightness the all and urea leakage from dousing module & remove the fuel sensor after refitted again then show the correct value | Closed | Gourav Sharma
16 | NORTH | 211767964 | 28-02-2025 13:32 | 40 | 3H.8951.../2420021 | DG mains contractor faulty | Closed | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Faridabad | 12 | Found mains contactor lock damage required to be change but when Engineer visit to the for change then he found relay was foulty so, relay to be change required | Closed | Kapil Solanki
17 | NORTH | 211767870 | 28-02-2025 13:24 | 58.5 | T4.8941.../2422321 | Door Lock Issue Call By Customer Name- Raju Number-9212005372 | Closed | RAJU GENERATORS | OVN Industries Private Limited - New Delhi | 436 | Canopy Door lock adjust | Closed | Kapil Solanki | Cut-off for latcher plate
18 | NORTH | 211767700 | 28-02-2025 13:07 | 20 | GP3.8601.../2421733 | Sound/Vibration Issue | Closed | S. R. Power Engineers | Vidyut Engineers - Noida | 2.4 | Customer raised the complaint for DG give the more sound so, check with DB meter found 76 to 80 so, same Educate the customer it is normal | Closed | Kapil Solanki
19 | NORTH | 211766314 | 28-02-2025 11:02 | 82.5 | 5H.8901.../2420577 | Voltage Fluctuation | Closed | MAHARAJA AGRASEN SEWA SADAN TRUST | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 3 | Check & found AC alternator not give the output voltage check AVR found foulty so, replace the same | Closed | Sudhir Awasthi
20 | NORTH | 211766044 | 28-02-2025 10:25 | 125.4 | 4H.8041.../2320058 | Under Speed Alarm Issue Call By Customer Name :- Pradeep Kumar Mobile No :- 9813091762 | Closed | PERFECT ZONE | Paluck Technologies Ltd. - Gurgaon | 490 | SPN/FMI 51/0 Clear the DTC & clean the ITV | Closed | Kapil Solanki
21 | NORTH | 211776574 | 2025-01-03 15:30 | 15 | GP3.8501.../2420507 | Trapping issue Call By Customer Name :- Monu ... Mobile No :- 7393883105 | Task Start | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW | 787 | Found radiator was chocked so, clean the radiator after trial on load Issue resolve | Closed | Sudhir Awasthi
22 | NORTH | 211776460 | 2025-01-03 15:03 | 125.4 | 4H.8042.C4../2420736 | DoorLack Issue . Call By KGD Name:-Tripathi Mobile No.:-7054802635 | Closed | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur | 42 | Conopy door lock adjust | Closed | Sudhir Awasthi
23 | NORTH | 211776287 | 2025-01-03 14:25 | 58.5 | T4.8941.../2520226 | Starting Issue Call By Customer Name :- SACHIN TYAGI Mobile No :-9971176291 | Closed | Jagdamba Generator Service | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 5 | Found DG was not starting so, check panel wiring found ok then check relay output point not contact proper after some times DG was starting proper | Closed | Kapil Solanki
24 | NORTH | 211776219 | 2025-01-03 13:59 | 125.4 | 4H.8041.../2420121 | Door Lock Problem Call By Customer Name :-mefus ali Number:- 8816065443 | Closed | D. V. M. Public School | Paluck Technologies Ltd. - Gurgaon | 175 | conopy door lock damage need to be replace | open | Kapil Solanki
25 | NORTH | 211776144 | 2025-01-03 13:36 | 58.5 | T4.8941.../2421947 | White Smoke Issue Call By Customer Name :-Pawan Kumar Mobile No :- 9811458226 | Closed | INDER GENERATOR HOUSE.. | Vidyut Engineers - New Delhi | 344 | DG set not start because fuel & load not available at site so that problem is under observation, order by customer that load will be available tomorrow | open | Kapil Solanki | Update required
26 | NORTH | 211776108 | 2025-01-03 13:30 | 30 | 3H.8902.../2320095 | Starting/Stopping Issue | Closed | Nuteck Paper Products | Paluck Technologies Ltd. - Faridabad | 97 | Found controller off automatically then check the found negative drop 1C2 & also found relay was heatup 12RB1-RL2 | open | Kapil Solanki
27 | NORTH | 211776095 | 2025-01-03 13:25 | 125.4 | 4H.8042.C4../2420059 | Tripping Issue Call By Customer Name :- Ram Prakash Mobile No :- 7678342570 | Closed | ECIL CO-OP. GROUP HOUSING SOCIETY LTD | OVN Industries Private Limited - New Delhi | 17 | Found jerk load on the DG so, sometimes light was flikring Educate customer for jerk load | Closed | Kapil Solanki
28 | NORTH | 211776047 | 2025-01-03 13:15 | 7.5 | D3.8305.../2400126 | Starting Issue & Shut Alarm Issue Call By Customer Name :- Arun Kumar Singh Mobile No :- 8860070224 | Closed | ADAMA INDIA PVT LTD | Paluck Technologies Ltd. - Ghaziabad | 38 | LLOp timble was broken, correct the same then issue resove | Closed | Kapil Solanki
29 | NORTH | 211776045 | 2025-01-03 13:14 | 58.5 | T4.8941.../2423232 | Starting Issue Call By Customer Name :- KOMAL SHARMA Mobile No :- 9811857374 | Closed | TRADE TAX OFFICER SEHKARI AWAS SAMITI LIMITED | Vidyut Engineers - Noida | 9.5 | Battery low after connected the charger then battery charging & after that DG start | Closed | Kapil Solanki
30 | NORTH | 211775940 | 2025-01-03 13:00 | 15 | GP3.8501.../2420555 | Leakage Issue | Task Start | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW | 579 | Found coolant leakage due to clamp was loose | Closed | Sudhir Awasthi
31 | NORTH | 211775825 | 2025-01-03 12:34 | 57 | T4.8941.../2320007 | Shut Down Alarm Call By Customer Name :- Puran Mobile No :- 7838362256 | Closed | Nanak Sai Estate LLP. | Vidyut Engineers - Noida | 56 | DG panel ems fail to start alarm show and DG set not start and check the DG set found the wiring of the DG has been cut by rat because of which the DG is not starting and the wiring farul have also been cut and panel wiring harness repair and probably insulation and fitted and check the DG manual start on testing ok DG oil service due | Closed | Kapil Solanki
32 | NORTH | 211775717 | 2025-01-03 12:02 | 45 | 3H.8951.../2420715 | Voltage Fluctuation | Closed | Ravi kumar | SAM Engineering corporation - Varanasi Cantt. | 72 | Check & Found Voltage in AVR 420 so, set through AVR 415 | Closed | Sudhir Awasthi
33 | NORTH | 211775640 | 2025-01-03 11:44 | 58.5 | 6H.9840.../2420007 | Under Speed Alarm and Tripping issue And Red Lamp On Alarm And Crank Reset Call By Customer Name :- M. D Afroj Mobile No:-8700479015 | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 36 | PNG pressure found ok after check events log found O2 CL LOOP Corr fuel mult on hi limit alarm show in multiple times so be adjust gas pressure in ZPR and ECU programing done after engine start normally and we record engine on load running parameters for share koel team | Closed | Kapil Solanki
34 | NORTH | 211775597 | 2025-01-03 11:38 | 20 | GP3.8601.../2420074 | Leakage Issue | Closed | J P GUPTA | R K Engineers - Bijnor | 1630 | Found Lub oil leakage so, check the rocker cover bolt found loose so tightness the same | Closed | Sudhir Awasthi
35 | NORTH | 211775486 | 2025-01-03 11:19 | 62.5 | T4.8941.../2320076 | Genset Trip | Closed | Tata Tele services | Paluck Technologies Ltd. - Ghaziabad | 307 | FIND V BELT BROKEN.REPLACED V BELT T4.438.01.0.00 | Closed | Kapil Solanki | Verify belt part number
36 | NORTH | 211775455 | 2025-01-03 11:08 | 57 | T4.8941.../2320196 | Load Issue Call By Customer Name :- Aryan Sharma Number :- 9811852400 | Closed | PRIME ENGINEERING | Vidyut Engineers - Noida | 211 | Found Over load & jerk load on the DG & Cable wire was defective so, same Educate the customer kindly change the wire | Closed | Kapil Solanki
37 | NORTH | 211775382 | 2025-01-03 10:56 | 200 | 6H.8435.../2420065 | Excessive Smoke | Closed | Leadengage LLP | Rajdhani Diesels and Electricals - Jodhpur | 58 | Found Fan belt was loose so, tightness the same & topup the coolant , Service due | Closed | Gourav Sharma
38 | NORTH | 211775326 | 2025-01-03 10:51 | 57 | T4.8941.../2320088 | Abnormal Sound Issue And Starting Issue Call By Customer Name :-Ram kumar Mobile No :- 9917556807 | Closed | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar | 271 | Found V-belt loose tightness the V-belt | Closed | Sudhir Awasthi | Verify belt part number
39 | NORTH | 211775314 | 2025-01-03 10:45 | 500 | DV8.8501.C4../2420042 | Sound/Vibration Issue | Closed | AVAADA ELECTRO PRIVATE LIMITED | Vidyut Engineers - Noida | 192 | Found No any in DG | Closed | Kapil Solanki
40 | NORTH | 211775269 | 2025-01-03 10:40 | 125.4 | 4H.8041.../2420705 | light power issue Call By Customer Name :- Sourbha ... Mobile No :-9639311451 | Closed | ZEUSIP ADVOCATES LLP | Vidyut Engineers - Noida | 113 | Low Def level topup the def & canopy light not on then check the DG panel canopy Light switch wiring(2E) connection loose to properly tight and fitting and check the canopy Light switch working ok | Closed | Kapil Solanki
41 | NORTH | 211775263 | 2025-01-03 10:37 | 200 | 6H.8435.../2320016 | Error code | Closed | AVS. Brake Linings Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 206 | Engine panel wiring proper check MCB wiring open and fit and proper tight and check Engine staing problem done all error code clear I connect tool | Closed | Kapil Solanki
42 | NORTH | 211775235 | 2025-01-03 10:24 | 15 | GP3.8501.../2421055 | Diesel Leakage Issue Call By Customer Name :- Gajendra Mittal Mobile No :-9414596502 | Closed | Jaishree Ram filling Station | Pratap Diesels Pvt. Ltd. - Kota | 27 | Found fuel level sensor bolt was loose so, tightness the same | Closed | Gourav Sharma
43 | NORTH | 211775149 | 2025-01-03 10:04 | 320 | F6.8802.../2420066 | Starting Issue And Genset Lock Out Manual Mode Issue And Display Issue Call By Customer Name :- Rishi Mobile No:-8299473600 | Closed | Bihari Lal Cold Storage. | S. R Engines Sales And Service - LUCKNOW | 40 | Low def level alarm topup the def then issue resolve | Closed | Sudhir Awasthi
44 | NORTH | 211775156 | 2025-01-03 09:57 | 320 | F6.8802.../2420179 | Genset Trip | Task Start | St. Marys Academy. | R K Engineers - Meerut | 5.2 | Charging alternator output voltage sometimes give & sometimes not give so, repaired after fitted ok but Today load trial | Closed | Sudhir Awasthi
45 | NORTH | 211775054 | 2025-01-03 09:07 | 125.4 | 4H.8041.../2420870 | Starting/Stopping Issue | Closed | St. Mark's Sr. Sec. Public School, | OVN Industries Private Limited - New Delhi | 1038 | Maintenance due alarm & Low coolant level , Service due | Closed | Kapil Solanki
46 | NORTH | 211775053 | 2025-01-03 09:04 | 125.4 | 4H.8041.../2420070 | Electrical Problems | Open | Rivah Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Visit pending | open | Gourav Sharma
47 | NORTH | 211775025 | 2025-01-03 08:38 | 250 | F6.8841.../2420127 | ECU Protect On Alarm Issue & Over Right Alarm Issue Call By Customer Name :- Shubhas Mobile No :- 8851659920 | Closed | KIDS CLINIC INDIA LTD | OVN Industries Private Limited - New Delhi | 1985 | DG not started due to indusment intrupted so found def tank filter chocked need to be replace and found dust particles in urea due to def tank cap open so clean all def line and def tank after that started the dg and found running is ok and dozing module working But engine required C CHECK oil service and all urea filter required to change | Closed | Kapil Solanki
48 | NORTH | 211775035 | 2025-01-03 08:31 | 160 | 6H.8475.../2420025 | Starting/Stopping Issue | Closed | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 2614 | found maintenance due alarm in dg set service due of dg set. Check adblue and found that adblue not spray so clean the dosing module with hot water . Start dg set and test on load dg set is running ok. | Closed | Kapil Solanki
49 | NORTH | 211769029 | 28-02-2025 16:43 | 20 | GP3.8601.../2420034 | Sound/Vibration Issue | Task Start | Mata Mohandai Oswal Public Senior Secondary School | Industrial Power Solutions - LUDHIANA | 137 | check the abnormal sound and check the engine the engine gear side abnormal sound issue so I dismantle the gear casing and found the oil pump gear damage | open | Ved Prakash Gupta
50 | NORTH | 211767162 | 28-02-2025 12:17 | 320 | F6.8802.../2420300 | Tripping Issue Call By Customer Name :- Sunil Pande Mobile No :-9812100734 | Closed | Marvel Home Fashion | SAAN Royal Power Solutions Private Limited - Panipat | 43 | Found Jerk load on the DG SO, Educate the customer please give the load with in the limits | Closed | Ved Prakash Gupta
51 | NORTH | 211766859 | 28-02-2025 12:04 | 15 | GP3.8501.../2421242 | Starting/Stopping Issue | Open | ALIF EMPORIUM | Suraj Motor Store - Srinagar |  | Visit pending | open | Ved Prakash Gupta
52 | NORTH | 211766476 | 28-02-2025 11:32 | 500 | DV8.8501.C4../2420103 | Display issue | Closed | GSB POLYMER PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 50 | Controller display not ON so, chcek the panel wiring found Ignition switch wire thimble was broken correct the same then issue resolve | Closed | Ved Prakash Gupta
53 | NORTH | 211766300 | 28-02-2025 11:04 | 82.5 | 5H.8901.../2420560 | Starting/Stopping Issue | Closed | STAR BITUMEN SOLUTIONS | SAAN Royal Power Solutions Private Limited - Hisar | 5 | Found self starter 3 no. wire was loose tightness the same | Closed | Ved Prakash Gupta
54 | NORTH | 211765964 | 28-02-2025 10:11 | 25 | GP3.8702.../2420077 | starting Issue & Tripping Issue & Preventive Maintenance Call By Customer Name :-Saroop Singh Mobile No :-9034674574 | Closed | BAWA TOTAL SOLUTION | SAAN Royal Power Solutions Private Limited - Hisar | 621 | SPN/FMI 110/0 radiator and DOC to Silencer Exhaust gas pipe protection tharmocol folty repair required | open | Ved Prakash Gupta
55 | NORTH | 211764120 | 27-02-2025 17:01 | 125.4 | 4H.8041.../2420441 | Stink issue Call By Customer Name :-Vijay Sharma Mobile No :- 9858683215 | Closed | Speedo Garments | Suraj Motor Store - Jammu | 135 | found leakage Some due to silencer nut bolt loose tightness the same then issue | Closed | Ved Prakash Gupta
56 | NORTH | 211763398 | 27-02-2025 15:42 |  | GP3.8702.../2520257 | coolant leakage issue | Closed | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - kathua | LR | found that coolant leakage from EGR pipe o ring side so remove and check EGR pipe not properly fitted check all o ring found normal condition so refitted the EGR pipe after fitting | Closed | Ved Prakash Gupta
57 | NORTH | 211763023 | 27-02-2025 14:40 | 30 | 3H.8902.../2320187 | CANOPY DOOR & LOCK ISSUE | Closed | Unicom India Pvt. Ltd. | Dynamic Engineering Services - Jalandhar | 5 | Canopy door lock alighnment wrong adjust the lock alighment | Closed | Ved Prakash Gupta
58 | NORTH | 211777175 | 2025-01-03 17:35 | 15 | GP3.8501.../2421479 | Starting/Stopping Issue | Task Start | GOVERMENT SENIOR SECONDARY SCHOOL | Dynamic Engineering Services - Jalandhar |  | Engineer visit Today on site | open | Ved Prakash Gupta
59 | NORTH | 211776196 | 2025-01-03 13:49 | 250 | F6.8841.../2420017 | Starting/Stopping Issue | Closed | Greenberry Hotels And Residency India Private Limited | SAAN Royal Power Solutions Private Limited - Shimla | 154 | Found fuel filter was chocked, Replace the fuel filter on paid basis | Closed | Ved Prakash Gupta
60 | NORTH | 211775922 | 2025-01-03 13:01 | 20 | GP3.8601.../2421388 | dg not starting 515212 | Open | ICICI Bank Limited | Megatron Engineers - Amritsar |  | Visit pending | open | Ved Prakash Gupta
61 | NORTH | 211775762 | 2025-01-03 12:17 | 125.4 | 4H.8042.C4../2420259 | Voltage Fluctuation | Closed | Ethnic Biotech | SAAN Royal Power Solutions Private Limited - Sonipat | 39 | Found Neutral wire was loose due to voltage flactuation so, sam tightness & DM2 Show the alarm SPN/FMI 516166/0 | Closed | Ved Prakash Gupta
62 | NORTH | 211775594 | 2025-01-03 11:37 | 15 | GP3.8501.../2420349 | KRM Not Working | Open | Dr. Rose Kamal Puri | Industrial Power Solutions - LUDHIANA |  | Visit pending | open | Ved Prakash Gupta
63 | NORTH | 211775262 | 2025-01-03 10:37 | 25 | GP3.8702.../2420908 | Tripping Issue Call By Customer Name :-RAM GOPAL Mobile No :-8699039603 | Closed | NITESH | SAAN Royal Power Solutions Private Limited - Shimla | 11 | Unbalance load on the DG so same Educate the Customer for maintain the load | Closed | Ved Prakash Gupta
64 | NORTH | 211775125 | 2025-01-03 09:52 | 125.4 | 4H.8042.C4../2420553 | Tripping and Amber Light Alarm issue Call By Customer Name :- Asgar Ali Mobile No:-9991098626 | Closed | RISHI LASER LTD. | SAAN Royal Power Solutions Private Limited - Sonipat | 9 | Found Emergency Switch button was pressed condition & SPN/FMI 1761/16 & 516166/0 clear the DTC | Closed | Ved Prakash Gupta
65 | NORTH | 211774985 | 2025-01-03 07:02 | 160 | 6H.8475.../2420272 | Starting Issue Call By Customer Name :- Sunil Kumar Mishra No :- 8818035075 | Closed | TOYPLUS PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Sonipat | 19 | SPN/FMI 1761/16 & 516166/0 Clear the DTC & flash the ECU | Closed | Ved Prakash Gupta
1 | East | 211769935 | 28/02/2025 20:10:38 | 35 | 3H.8902.../2422034 | Starting issue Called by customer NAME SUSHANT KUMAR: Number : 8987190471 | Closed | BANK OF BARODA | Globalline India Services Private Limited - Madhepura | 2 | Update Pending | CLOSED | Prabhakar Kumar
2 | East | 211768573 | 28/02/2025 15:25:04 | 35 | 3H.8902.../2421674 | Mobil Leakage Issue Call By Customer Name :- Abhay Mobile No :-9661377370 | Closed | Gurudev Faishon | Globalline India Services Private Limited - Bhagalpur | 57 | Lube oil leakage due to loosen oil filling cap. Previously one wet CSP has been done. Tighten the cap and issue got resolved. | CLOSED | Prabhakar Kumar
3 | East | 211768093 | 28/02/2025 13:58:01 | 25 | GP3.8702.../2421901 | Tripping Issue. Call By service dealer. Name:-Parsuram Singh Mobile No.:-9151061241 | Closed | Starline Enterprises | HACS Engineering and Tech Private Limited - Jamshedpur | 11.33 | Engine shutdown due to Unbalaced load in three phases. SE visited the site and guided the customer to balance the load. Restored the site. | CLOSED | Prabhakar Kumar
4 | East | 211765993 | 28/02/2025 10:13:25 | 20 | GP3.8601.../2421192 | Starting issue Call By Customer Name :- Chandan Kumar Mobile No:-9955042251 | Closed | SHRI RADHAKRISHNA KEDIA GIRLS H/S +2 | Globalline India Services Private Limited - Muzaffarpur | 49 | Engine shutdown due to loose contact in the NC block of emergency switch. Removed the wire and tighten the screw ofcontact block in emergency switch . Issue got resolved. | CLOSED | Prabhakar Kumar
5 | East | 211764500 | 27/02/2025 17:38:43 | 58.5 | T4.8941.../2422910 | Control panel Issue Call By Customer Name :- Sheetal Gupta Mobile No :- 6299024030 | Open | HARE RAM HARE KRISHNA ENTERPRISES | HACS Engineering and Tech Private Limited - Hazaribagh | 42 | Voltage drop. Found load cable was defective. Corrected the same and issue has been restored | CLOSED | Prabhakar Kumar
6 | East | 211766514 | 28-02-2025 11:31 | 82.5 | 5H.8901.../2320008 | Automatiom Issue Call By Customer Name-Sikta Number-9986974640 | Closed | SimpleeKare Health. | Gangpur Sales and Services - Bhubaneswar | 34 | SE start the engine then found there was a loose connection somewhere all the connections are tightening the same,Issue resolved | CLOSED | Ujjwal Das
7 | East | 211763958 | 27-02-2025 16:39 | 30 | 3H.8902.../2420601 | Starting/Stopping Issue | Closed | Shilpi Biswas. | Revenus Industries Pvt. Ltd. - Nadia | 7.4 | Update Pending | CLOSED | Prosanjit saha
8 | East | 211766226 | 28-02-2025 10:52 | 250 | F6.8842.C4../2420032 | Malfunction Alarm issue Call By Customer Name :- Sunil Kumar Das Mobile No:-8961435183 | Closed | Malabar Gold. . | Gangpur Sales and Services - Rourkela | 3.29 | DG shutdown due to 516166/0 (Inductment alram) and 3031/17 (Adblue Level low) after that topup the adblue and clear the code Issue resolved. | CLOSED | Ujjwal Das
1 | WEST | 211768305 | 28-02-2025 14:41 | 58.5 | T4.8941.../2423015 | Red Lamp On Alarm Call By Customer Name :- Akash Mahale Mobile No:-9067190032 | Closed | Mangal Hospital | Dhanashree Technocrats Pvt. Ltd. - Dhule | 8 | 5838/1 ,2791/18 , Check all the EGR valve connection , found ok connect ikonnect and clear error code. | Closed | Jagdeep Saini
2 | WEST | 211766936 | 28-02-2025 12:09 | 15 | GP3.8501.../2421274 | Tripping Issue Call By Customer Name :- Tanayya Patil Mobile No :7498870442 | Closed | Santiago Realtech Ventures | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 4 | customer side load issue. | Closed | Jagdeep Saini
3 | WEST | 211765967 | 28-02-2025 10:15 | 320 | F6.8802.../2420148 | Starting/Stopping Issue | Closed | MONGA STRAYFIELD PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 179 | Low adblue level so top up adblue. | Closed | Jagdeep Saini
4 | WEST | 211766209 | 28-02-2025 10:49 | 250 | F6.8842.C4../2420088 | Starting/Stopping Issue | Closed | Krishna Mega Projects LLP. | KALA Care Global LLP - Aurangabad | 2 | no issue found on site. | Closed | Jagdeep Saini
5 | WEST | 211766097 | 28-02-2025 10:30 | 15 | GP3.8501.../2520119 | NO OUTPUT | Task Start | SHIV SHAKTI ENGINEERING WORKS | Mahalaxmi Diesels - Kankavali |  | Main alternator issue , output not come also abnormal sound from alternator , vendor team visited , found issue in exciter so arrange the exciter assembly. | open | Jagdeep Saini
6 | WEST | 211767542 | 28-02-2025 13:02 | 30 | 3H.8902.../2420249 | Protective Lamb Problem Call by : Customer Name : Rajeshkumar Contact : 7708341090 | Task Start | Larsen & Toubro Limited, Construction | Transcreek Engineers Pvt. Ltd. - Boisar | 1149 | 520528/31,5838/2,2791/1 check wiring connection , continuty found ok, so flash the ECU . | Closed | Jagdeep Saini
7 | WEST | 211766098 | 28-02-2025 10:31 | 58.5 | T4.8941.../2422300 | Battery Voltage Issue Call By Customer Name :- Pradeep Hire Mobile No :-7066530400 | Closed | NORBAR TORQUE TOOLS INDIA PRIVATE LIMITED | Transcreek Engineers Pvt. Ltd. - Navi Mumbai | 16 | Battery charger connection found loose so battery was not charged so tight the connection. | Closed | Jagdeep Saini
8 | WEST | 211766079 | 28-02-2025 10:28 | 750 | DV2.8501.C4../2420178 | ECU error show | Closed | Sairama Realty. | Transcreek Engineers Pvt. Ltd. - Panvel | 28 | low DEF so top up DEF level | Closed | Jagdeep Saini
9 | WEST | 211748879 | 23-02-2025 13:15 | 82.5 | 5H.8901.../2420146 | Tripping Issue Call By Customer Name :- Mobile No :-9322397308 | Cancelled | Shree Krishna Homes | Transcreek Engineers Pvt. Ltd. - Ambernath |  | Cancelled | Closed | Jagdeep Saini
10 | WEST | 211759829 | 26-02-2025 15:56 | 30 | 3H.8902.../2420180 | Starting Problem & lamp Problem Call by : Customer Name :Rajesh Contact :7397336597 | Closed | L & T CONSTRUCTION. | Transcreek Engineers Pvt. Ltd. - Boisar | 405 | 520528/31, 5838/3, 2091/31 error code connect ikonnect and clear error code. | Closed | Jagdeep Saini
11 | WEST | 211760057 | 26-02-2025 16:47 | 20 | GP3.8601.../2420050 | Automation and Current issue Call By Customer Name :- Ganesh Mobile No:-9730580949 | Cancelled | Suzanne Merwanji. | Mahalaxmi Diesels - Goa |  | cancelled | Closed | Jagdeep Saini
12 | WEST | 211757712 | 26-02-2025 09:49 | 30 | 3H.8902.../2421492 | Starting/Stopping Issue | Closed | Axis Bank Ltd | Mahalaxmi Diesels - Satara | 5 | loose connection found in controller to start coil supply relay tight the wire issue solved. | Closed | Jagdeep Saini
13 | WEST | 211757937 | 26-02-2025 10:56 | 15 | GP3.8501.../2420546 | Starting problem | Closed | CUPID Limited | Dhanashree Technocrats Pvt. Ltd. - Nasik | 1597 | Swept stuck issue , change the pump. | Closed | Jagdeep Saini
14 | WEST | 211754951 | 25-02-2025 14:32 | 30 | 3H.8902.../2420710 | Electrical Problems | Closed | Babasaheb Sanap. | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | customer side unbalance load | Closed | Jagdeep Saini
15 | WEST | 211757635 | 26-02-2025 08:26 | 30 | 3H.8902.../2420565 | Preventive Maintenance Call By Customer Name :- Firoj Ahamad Mobile No :- 6263906941 | Closed | Dinshaw's Dairy Foods Pvt Ltd | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 1040 | Maintenance due alarm so reset the alarm. suggest the customer for servicing. | Closed | Jagdeep Saini
16 | WEST | 211750685 | 24-02-2025 12:50 | 20 | GP3.8601.../2421447 | Starting/Stopping Issue | Closed | Sreeja Engineering Services | Dicksons Engineering Co.Pvt.Ltd. - Yavatmal | 4 | Panel MCB found in off condition so on the mcb and educate the customer. | Closed | Jagdeep Saini
17 | WEST | 211746071 | 22-02-2025 12:51 | 58.5 | T4.8941.../2421678 | Electrical Problems | Closed | Sukhakarta Critical Care and Maternity Hospital. | Dicksons Engineering Co.Pvt.Ltd. - Yavatmal | 22 | mains mcb nutral issue connection loose contactor and lvm not working proper in auto mational | Closed | Jagdeep Saini
18 | WEST | 211746105 | 22-02-2025 12:58 | 58.5 | T4.8941.../2422819 | ERROR CODE ISSUE. | Completed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 0.17 | Emergency stop alarm shown found loose connection so tight the wire. | Closed | Jagdeep Saini
19 | WEST | 211751450 | 24-02-2025 15:35 | 40 | 3H.8951.../2520302 | Line Rejection | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | No issue with dg | Closed | Jagdeep Saini
20 | WEST | 211751439 | 24-02-2025 15:31 | 82.5 | 5H.8901.../2420929 | Line Rejection | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | No issue with dg | Closed | Jagdeep Saini
21 | WEST | 211764026 | 27-02-2025 16:48 | 25 | GP3.8702.../2420198 | Battery issue Call By Service Dealer Name :- Saurabh Mobile No :- 7385403851 | Task Start | Prapti Associates | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 18 | Loose connection from battery charger so tight the connection. | Closed | Jagdeep Saini
22 | WEST | 211757709 | 26-02-2025 10:05 | 45 | 3H.8951.../2520124 | Starting Issue Call By Customer Name :- Sudagar Nabade Mobile No :- 9623992393 | Closed | Perennial Technologies Pvt. Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 58 | Dg tripped due to unbalanced load so suggest the customer to balance the load. | Closed | Jagdeep Saini
23 | WEST | 211769137 | 28-02-2025 16:59 | 160 | 6H.8475.../2420369 | Under speed alarm issue Call by Service Dealer Name - Pankaj No - 9879000913 | Closed | Bharti Marketing | Unique Techno Services Pvt Ltd. - Vapi | 12 | Low adblue level | Closed | Amit Sandlya
24 | WEST | 211766128 | 28-02-2025 10:40 | 20 | GP3.8601.../2420983 | Starting/Stopping Issue | Closed | SHREEKAR CONSTRUCTION | Unique Techno Services Pvt Ltd. - Surendranagar | 1137 | The fuel level was low so the technician was advised to refuel. | Closed | Amit Sandlya
25 | WEST | 211764870 | 27-02-2025 19:27 | 5.5 | CC1.1013.../2400409 | Starting/Stopping Issue | Task Start | KARTIK ENTERPRISE | Unique Techno Services Pvt Ltd. - Gandhidham | 474 | Engine not starting, so replaced the fuel pump. | Closed | Amit Sandlya
26 | WEST | 211775071 | 2025-01-03 09:25 | 125.4 | 4H.8041.../2420959 | Leakage Issue | Closed | Shri Narayan Charitable Trust. | Unique Techno Services Pvt Ltd. - Ankleshwar | 84 | Oil was leaking from the oil drain pipe, so the clamp was tightened. | Closed | Amit Sandlya
27 | WEST | 211775062 | 2025-01-03 09:20 | 25 | GP3.8702.../2421701 | Emergency stop alarm issue Call By Customer Name :Atul Bhai No :7984068729 | Task Start | Lcc Projects Pvt. Ltd. . | Unique Techno Services Pvt Ltd. - Ahmedabad | 140 | Emergency Alarm was showing in the controller. So bypashed the Emergency button, engine running ok. Today engineer will visit with Emergency button. | Closed | Amit Sandlya
28 | WEST | 211737200 | 20-02-2025 11:18 | 58.5 | T4.8941.../2422857 | Air locking issue | Task Start | ARCHANA JAISWAL | Unique Techno Services Pvt Ltd. - Ahmedabad | 8 | 20-02-2024 DG only start after hand priming of the fuel. Took the bucket trail DG was not started. No any leakage found in fuel system. After one time start opened the fuel filter and found about half fuel in fuel filter. So today engineer will visit at the site with all copper washer and one NRV(For fitted in suction line). 28-02-2025 ASE visited on site with Bosch persor so found HP Pump issue & spring of the pump was damage. So changed it and issue resolved. | Closed | Amit Sandlya
29 | WEST | 211775746 | 2025-01-03 12:18 | 25 | GP3.8702.../2420202 | Coolant lekage Issue Call By Service Dealer Name :- Parmanand Sir Mobile No :- 7869079392 | Closed | Mr. Sunil Ahirwar. | Natraj Power Tech - Sagar | 445.58 | Coolant leakage from hose pipe so tightened the clamp. | Closed | Vijay Patil
30 | WEST | 211709169 | 2025-12-02 11:43 | 5.5 | CC1.1013.../2400113 | Battery Charge Issue Call By Customer Name :- Balram Mobile No :-9508252219 | Closed | Rajlaxmi Dev Build India Pvt. Ltd. | Natraj Power Tech - Bhopal | 566.11 | Replaced the battery Charger. | Closed | Vijay Patil
31 | WEST | 211762794 | 27-02-2025 13:43 | 40 | 3H.8951.../2421774 | Contractor Burn Issue Call by : Customer Name :mr.govind . Contact :9826048629 | Closed | NISARG HOSPITALITY | Mahalaxmi Diesels - Goa | 7 | Main contactor found burn , change Main contactor . | Closed | Jagdeep Saini
51 | South Zone | 211770166 | 28-02-2025 21:49 | 20 | GP3.8601.../2421416 | Inspection/Maintenance | Open | MS. Power Systems | Prasad Power Engineers - Hassan |  | cancelled | Cancelled | Mr. Anil Kumar H G
10 | South | 211769921 | 28-02-2025 19:45 | 250 | F6.8841.../2420399 | Starting/Stopping Issue | Closed | St. AUGUSTINES FORANE CHURCH | Electro Controls - Kottayam | 131 | Oil leakage from dipstick side, check and found that dipstick not fitted properly | Closed | Mr. Sanjaimon S
3 | WEST | 211776898 | 2025-01-03 16:48 | 30 | 3H.8902.../2421879 | Starting Issue Email By - KGD Name -Vishal Raut | Open | Mr. Amit Arjun Jadhav | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati |  | cancelled | Closed | Jagdeep Saini
4 | WEST | 211776901 | 2025-01-03 16:48 | 15 | GP3.8501.../2520244 | Engine Hunting | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | RPM fluctuation no issue in fuel line need to change the fuel pump. | Closed | Jagdeep Saini
5 | WEST | 211776645 | 2025-01-03 15:44 | 25 | GP3.8702.../2520260 | EGR PROBLME | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Coolant found in EGR system | Closed | Jagdeep Saini
6 | WEST | 211775997 | 2025-01-03 13:03 | 0 | T4.8941.../2520535 | WIRING HARNESS ISSUE | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | 36 pin connector wire lug found back out so need to change the wiring harness. | Closed | Jagdeep Saini
7 | WEST | 211779033 | 2025-02-03 13:40 | 200 | 6H.8435.../2420083 | Fan Belt Issue Call By Customer Name - Ajit Shinde Number - 9527397629 | Task Start | H. S. Associates. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 426 | v belt founnd loose so tight the belt. | Closed | Jagdeep Saini
9 | South | 211769886 | 28-02-2025 19:34 | 20 | GP3.8601.../2421265 | Oil leakage problem Call by : Customer Name : Sathish Contact : 9741018086 | Closed | Surya Electricals | Surya Power Services - Mysuru | 17 | Oil leakage from drain bolt, tighten the bolt, no leakage after that. | Closed | Mr. Anil Kumar H G
9 | WEST | 211776624 | 2025-01-03 15:37 | 625 | DV0.8501.C4../2320015 | Starting issue | Closed | Avante Spaces Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 58 | amber lamp alarm, error code 523576/ 0 ( inducement ), ECU malfuctioning, flash the ECU , DEF level low so top up adblue . | Closed | Jagdeep Saini
10 | WEST | 211775077 | 2025-01-03 09:30 | 500 | DV8.9312.../2300002 | Staring issue | Task Start | One Avante Condominium | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 77 | Fuel level shows in bar so need to be change the programe in percentage. | Closed | Jagdeep Saini
11 | WEST | 211775074 | 2025-01-03 09:28 | 625 | DV0.9031.../2300002 | Starting issue | Closed | Avante Spaces Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 58 | amber lamp alarm, error code 523576/ 0 ( inducement ), ECU malfuctioning, flash the ECU , DEF level low so top up adblue . | Closed | Jagdeep Saini
12 | WEST | 211775066 | 2025-01-03 09:24 | 500 | DV8.8501.C4../2320045 | Error Code issue Call By Customer Name :- Lalit Patil Mobile No:-7028289512 | Closed | One Avante Condominium | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 99 | Adblue level low so top up adblue. | Closed | Jagdeep Saini
13 | WEST | 211779212 | 2025-02-03 20:53 | 160 | 6H.8475.../2420079 | Amber lamp alarm and error code issue Call By Customer Name :- Harish Mobile No :- 8888630800 | Task Start | Vascon Engineer Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 134 | low adblue level so top up adblue level. | Closed | Jagdeep Saini
14 | WEST | 211779125 | 2025-02-03 18:16 | 35 | 3H.8902.../2422312 | Starting Issue Call By Customer Name : Pramod Jadhav Number : 7888035663 | Task Start | P. N. Gadgil & Sons Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 413 | y phase fuse burn found burn , .so change the fuse issue solved. | Closed | Jagdeep Saini
15 | WEST | 211779168 | 2025-02-03 20:13 | 125.4 | 4H.8042.C4../2420816 | Amber lamp alarm issue Call By Customer Name :- Bhaiyya kamble Mobile No :-9766262217 | Cancelled | SHRADDHA HATCHERY | KALA Care Global LLP - Aurangabad |  | cancelled | Closed | Jagdeep Saini
16 | WEST | 211776179 | 2025-01-03 13:43 | 40 | 3H.8951.../2421000 | Oil leakage Issue Call By Customer. Name:- Santosh Mobile No.:9370050004 | Task Start | Santosh Kicheegoda Ailekopal ,C/o Banglore | KALA Care Global LLP - Nanded | 62 | Oil leakage from oil sump , tighten the bolt using allen key , issue solved. | Closed | Jagdeep Saini
17 | WEST | 211776905 | 2025-01-03 16:51 | 25 | GP3.8702.../2520083 | Mil Lamp Alarm Issue Email By - KGD Name - Vishal Raut | Open | Indapur Dairy and Milk Products Ltd, | Mahalaxmi Diesels - Dharashiv |  | cancelled | Closed | Jagdeep Saini
18 | WEST | 211779225 | 2025-02-03 22:21 | 58.5 | T4.8941.../2422058 | Genset Trip | Task Start | Shetye Sales | Mahalaxmi Diesels - Goa | 62 | oil leakage from gear side so use k sealant , ignition relay coil side problem so change the relay card. | Closed | Jagdeep Saini
19 | WEST | 211775206 | 2025-01-03 10:19 | 30 | 3H.8902.../2421292 | STARTING PROBLEM | Closed | Shree Sai Enterprises. | Mahalaxmi Diesels - Goa | 1 | Unbalance load from customer side | Closed | Jagdeep Saini
27 | South Zone | 211769849 | 28-02-2025 19:24 | 20 | GP3.8601.../2420858 | Display Showing "Amber light on" Problem Call by : Customer Name :Mubarque Contact :9895575763 | Task Start | Hotel Dawaat | Electro Controls - Marthandam | 89 | 2802/4,2791/114, battery charging problem, charging alternator fuse retighten, water pulley damage, ASE visiting the site for inspection | Task Start | Mr. Sanjaimon S | Details required
21 | WEST | 211775421 | 2025-01-03 11:02 | 30 | 3H.8902.../2421732 | DG automation | Open | ATC Telecom Infrastructure Private Limited | Transcreek Engineers Pvt. Ltd. - Ambernath |  | cancelled | Closed | Jagdeep Saini
22 | WEST | 211775468 | 2025-01-03 11:14 | 40 | 3H.8951.../2420916 | DG automation... | Cancelled | ATC Telecom Infrastructure Private Limited | Transcreek Engineers Pvt. Ltd. - Bhiwandi |  | cancelled | Closed | Jagdeep Saini
23 | WEST | 211778936 | 2025-02-03 10:57 | 1500 | DV2.8508.C4../2420002 & 2420007 | Red Lamp alam issue Call by Customer Name : Mr. Ganesh contact : 9860841537 | Closed | Anuh Pharma Limited | Transcreek Engineers Pvt. Ltd. - Boisar | 23 | Found adblue level low so top up adblue. | Closed | Jagdeep Saini
12 | South Zone | 211769802 | 28-02-2025 18:53 | 30 | 3H.8902.../2420791 | Display Showing Alarm Call by : Customer Name :Prasanth Contact :9791269100 | Cancelled | Prasanth Sweets and Bakes | Bharath Diesel Sales and Service - Salem |  | cancelled | Cancelled | Mr. NandhaGopal
25 | WEST | 211776911 | 2025-01-03 16:46 | 25 | GP3.8702.../2420338 | Starting Issue Call By Customer Name :- Arun Katara Mobile No :- 8233959219 | Open | Ramesh J. Raval. | Unique Techno Services Pvt Ltd. - Ahmedabad | 92.12 | SPN/FMI- 5838/1(EGRVlv block group inducement level warning),2802/3 Checked the charging alternator connections & fuse condition found OK.Checked the continuity & cross continuity from ECU to EGR valve OK. So cleared the DTC & engine running properly. | Closed | Amit Sandlya
29 | South Zone | 211768992 | 28-02-2025 16:33 | 58.5 | T4.8941.../2421998 | COONT LOW | Task Start | Mrs. Priya B. | Surya Power Services - Bangalore | LR | Low coolant level, top-up the coolant | Task Start | Mr. Anil Kumar H G
8 | South | 211768919 | 28-02-2025 16:24 | 15 | GP3.8501.../2421920 | panel door issue | Closed | PROTECH RAIL ENGINEERS | Laxmi Diesels - Visakhapatnam | 2 | Panel door hinges not working, so replace the same | Closed | Mr. MD Saleem
26 | South Zone | 211768826 | 28-02-2025 16:04 | 58.5 | T4.8941.../2520273 | . | Task Start | KALA GENSET PVT LTD | Surya Power Services - Peenya, Bangalore | LR | engine not starting, not crancking, Other SE is visiting today | Task Start | Mr. Anil Kumar H G
7 | South | 211768724 | 28-02-2025 15:50 | 4 | CC1.4035.../2400002 | Electrical Problems | Closed | Jeyaseelan | Madurai Electro Controls - Virudhunagar | 7 | Engine is off in load. Customer eb side complaint. Idle running Genset is not problem. | Closed | Mr. NandhaGopal
28 | NORTH | 211768550 | 28-02-2025 15:17 | 125 | F6.9840.../2420019 | Controller Flashing/Programming | Closed | Jawa Pharmaceuticals INDIA. Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1 | Gas Engine CC done on 03/10/2024 alarm show in controller so flash the controller | Closed | Kapil Solanki
6 | South | 211768057 | 28-02-2025 13:50 | 125.4 | 4H.8042.C4../2420837 | Starting/Stopping Issue | Closed | MODERN MATCHES PRIVATE LIMITED | Madurai Electro Controls - Virudhunagar | 32 | door lock issue, adjust the door lock | Closed | Mr. NandhaGopal
5 | East | 211775826 | 2025-01-03 12:35 | 25 | GP3.8702.../2421592 | Starting/Stopping Issue | Closed | SAMIR MALAKAR | Revenus Industries Pvt. Ltd. - Purulia | 25 | There was coolant level is low alarm and that's why engine did not start properly. then corrected alarm After that told the customer for refilling the coolant and customer agree this thing's. Although checking all DG parameters. But no problem found. Still now engine running normal. Engine start stop ok. Starting problem solved. | CLOSED | Prosanjit saha
9 | South zone | 211767984 | 28-02-2025 13:33 | 58.5 | T4.8941.../2420457 | Starting issue Call By Customer Name :- Chitra Ramakrishna Mobile No:-9941007888 | Closed | Chitra Ramakrishna. | Madhu Engineering Sales & Service - Teynampet,Chennai | 16 | Air lock due to low fuel level | closed | Mr. NandhaGopal
8 | South zone | 211767441 | 28-02-2025 12:55 | 20 | GP3.8601.../2421325 | Tripping Issue Call By Customer Name :- Murthy Mobile No:-9941293514 | Closed | Manoj Vaibhav Gems N. Jewellers Ltd. | Laxmi Diesels - Visakhapatnam | 20.18 | customer was using DG on over load due to which DG trip R phase 22 Amps y phase 33 Amps and B phase 45 Amps, advice customer to use DG in | closed | Mr. MD Saleem
29 | NORTH | 211767357 | 28-02-2025 12:43 | 750 | DV2.8501.C4../2420077 | Coolant Leakage Issue Call By Customer Name :- Rakesh Kumar Mobile No :- 9812743315 | Closed | Indian Oil Corpotation Ltd. | Paluck Technologies Ltd. - Gurgaon | 16 | found coolant minor leakage from A bank 5 and 6 number had need to be head torque otherwise had gasket replace required | Closed | Kapil Solanki
5 | South | 211766900 | 28-02-2025 12:06 | 20 | GP3.8601.../2421977 | Starting/Stopping Issue | Closed | Shimjith.M | G-Care Diesels Private Limited - Calicut | 20.25 | Visited the site, no issue observed | Closed | Mr. Sanjaimon S
13 | South Zone | 211766733 | 28-02-2025 12:01 | 20 | GP3.8601.../2421598 | Emergency stop alarm Issue Call By Customer name : Suresk Kumar No :9843066944 | Closed | Engine protective services | Bharath Diesel Sales and Service - Salem | 21 | Emergency button H1 wire loose, tighten the wire | Closed | Mr. NandhaGopal
44 | South Zone | 211766607 | 28-02-2025 11:49 | 58.5 | T4.8941.../2422015 | Oil Leakage Issue Call By Customer Name Krishnaukmar . Mobile No :- 9940071334 | Closed | Krishnaraj foods | Net Work Diesels - Potheri | 36 | INSPECT THE ENGINE FOUND ENGINE DIESEL LEAKAGE FROM NON RETURN VALVE AREA. DUE TO COPPER WASHER WAS DAMAGED, SO REPLACED NEW COPPER WASHER. STARTED AND TESTED THE ENGINE NO LOAD FOUND DG SET RUNNING PERFORMANCE IS SATISFACTORY, (COPPER WASHER IS CUSTOMER STORK) ( NO OIL LEAKAGE) | Closed | Mr. NandhaGopal
60 | South Zone | 211766610 | 28-02-2025 11:49 | 15 | GP3.8501.../2421967 | BATTERY OVERCHARGING ALARM ISSUE | Task Start | Mr. Arun Kumar S.R. | Surya Power Services - Bommasandra, Bangalore |  | Chargining alternator failure, sent for repairing | Task Start | Mr. Anil Kumar H G
22 | South Zone | 211766463 | 28-02-2025 11:29 | 200 | 6H.8435.../2420044 | Fuel Variation | Closed | CANARA BANK | G-Care Diesels Private Limited - Calicut | 98 | Attend the and fuel float checked fuel float alignment issue after fuel float removed and alignment corrected. work stating time fuel level 50% after fuel float alighment corrected 93% tank fuel full condition problem solved .adblue level low condition, coolant level low informed customer need to fillted adblue and coolent | Closed | Mr. Sanjaimon S
61 | South Zone | 211766378 | 28-02-2025 11:15 | 160 | 6H.8475.../2420165 | Alaram sound &Oil leakage &Adublue Temparature Problem Call by : Customer Name : Hari Contact : 9206608669 | Closed | M/s. Nithyaa Sai Metal Technics LLP. | Ultimate Power Source - Chittoor | 21 | Adblue level too low. Coolant lekage. | Closed | Mr. NandhaGopal
17 | South Zone | 211766297 | 28-02-2025 11:03 | 58.5 | T4.8941.../2420179 | Starting Issue Call By Customer Name :- Sakthibel . Mobile No :-7066652739 | Closed | OIL AND NATURAL GAS CORPORATION LIMITED | Bharath Diesel Sales and Service - Thiruvarur | 652 | Check the engine side crank rest so checking wiring connection controller unit self motor wiring 3/ wiring loose contact connections problem reconneting the wiring fitting found okay start the engine testing running found ok | Closed | Mr. NandhaGopal
19 | South zone | 211766145 | 28-02-2025 10:38 | 30 | 3H.8902.../2421934 | Voltage Fluctuation Issue Call By KGD Name :- Jamuna Mobile No :-9036094197 | Closed | JAYARAMAREDDY | Surya Power Services - Chikkaballapur | 37 | check the voltage and R=239,Y=239,B=238 and dg side is no issue and customer side and panel sides issue and inform the customer customer side issue. | closed | Mr. Anil Kumar H G
14 | South Zone | 211766139 | 28-02-2025 10:36 | 15 | GP3.8501.../2421796 | Voltage Fluctuation | Closed | AMBAL DYERS | Bharath Diesel Sales and Service - Salem | 10 | Inspect the engine off load check the output cable and MCCB netural line ,R 121AVR line and F1 and F2 voltage check start engine voltage + or - 3V different and fluctuation problem, output voltage not stable adjusted V port the AVR but still problem not solved replaced the new R120 AVR ,the start engine voltage 240 stable condition, load on DG not fluctuation,1 hrs. load voltage ok problem solved | Closed | Mr. NandhaGopal
4 | South | 211766042 | 28-02-2025 10:25 | 125.4 | 4H.8042.C4../2420501 | Starting/Stopping Issue | Closed | Baba Electrical Works | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 6.39 | DG not starting check and found battery voltage low, also leakage from fuel suction line, fitted the pipe properly, | Closed | Mr. NandhaGopal
4 | South Zone | 211766029 | 28-02-2025 10:24 | 82.5 | 5H.8901.../2520034 | LEAK OFF PIPE DAMAGE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | inspect the dg set ,noticed the leak off pipe damaged and replaced the leak off pipe and checked the all parameters and start the dg set run for few mins checked the leakage if any no leakage found | Closed | Mr. NandhaGopal
40 | South Zone | 211765972 | 28-02-2025 10:02 | 15 | GP3.8501.../2420903 | Starting/Stopping Issue | Open | M/S HUTTI GOLD MINES COMPANY LIMITED | KALA Care Global LLP - Hospet |  | visit pending | Open | Mr. Anil Kumar H G
17 | South zone | 211765809 | 28-02-2025 08:40 | 15 | GP3.8501.../2420928 | Call by : Customer Name :HARISH V Contact : 9980107172 | Closed | GEETHANJALI HARISH | Surya Power Services - Kalyan Nagar | 22.13 | auto eb connection done for auto start | closed | Mr. Anil Kumar H G
2 | South Zone | 211765807 | 28-02-2025 08:06 | 625 | DV0.8501.C4../2420137 | Starting Issue Call By Customer Name :- Divakar Mobile No :-7867901851 | Closed | S.S.Murali, | Bharath Diesel Sales and Service - Karappakkam | 65 | Start Relay wire loose, connection, tighten the wire | Closed | Mr. NandhaGopal
32 | South Zone | 211653916 | 28-01-2025 17:49 | 10 | GP3.8301.../2420509 | CHARGING ALTERNATOR HIGH VOLTAGE | Task Start | ANANTHAPUR RAILWAY STATION | Ultimate Power Source - Ananthapuramu | LR | visit pending | Task Start | Mr. NandhaGopal
20 | South Zone | 211653709 | 28-01-2025 17:06 | 30 | 3H.8902.../2421321 | network issue | Closed | Bhaskar associates | G-Care Diesels Private Limited - Calicut | 282.98 | Replaced KRM simcard then start the engine half and hours trial run found everything is normal | Closed | Mr. Sanjaimon S
3 | South | 211764728 | 27-02-2025 18:22 | 7.5 | D3.8305.../2400190 | Display Showing "Low Oil Pressure" And Genset Turned Off Call by : Customer Name :Dr. FAVAZ Contact :9037887135 | Closed | Dr FAVAZ | G-Care Diesels Private Limited - Thrissur | 3 | Llop faulty. Replace llop switch. Dg running with load | Closed | Mr. Sanjaimon S
18 | South Zone | 211764647 | 27-02-2025 18:04 | 15 | GP3.8501.../2420616 | Starting Problem Call by : Customer Name :SHAKKEER KAKKERI Contact :7034992122 | Closed | Amble Apartment. | G-Care Diesels Private Limited - Calicut | 49.45 | (96/0) High fuel level issue, not resolved after flashing, also check the fuel level sensor , found OK, but issue persist So replace the ECU. After replacing the ECU, issue resolved | Closed | Mr. Sanjaimon S | Cases to be share
2 | South | 211763960 | 27-02-2025 16:40 | 58.5 | T4.8941.../2421238 | Door lock Issue | Closed | Periyar Residency | G-Care Diesels Private Limited - Ernakulam | 59 | Door lock issue, fix the door lock | Closed | Mr. Sanjaimon S
47 | South Zone | 211763785 | 27-02-2025 16:11 | 400 | DV8.8542.C4../2420060 | Starting issue Call By KGD Name :- Prakash Mobile No :- 9448476151 | Task Start | P. S. K. Pharma Private Ltd. | Prasad Power Engineers - Davangere | 4 | MCCB breaker burn, replace the MCCB due to loose connection. | Task Start | Mr. Anil Kumar H G
21 | South zone | 211763592 | 27-02-2025 16:03 | 0 | GP3.8601.../2520275 | . | Closed | KALA GENSET PVT LTD | Surya Power Services - Peenya, Bangalore | LR | Airlock issue in HP | closed | Mr. Anil Kumar H G
22 | South zone | 211763460 | 27-02-2025 15:56 | 0 | GP3.8501.../2520271 | . | Closed | Kala Genset Pvt. Ltd. | Surya Power Services - Peenya, Bangalore | LR | tart the engine not 3 seconds engine rest, check the MPU is not working check the ohms , in multimeter,is showing 1ohms,and check the voltage is 9.53voltes is coming then suspected MPU is not working , change new one | closed | Mr. Anil Kumar H G
5 | South Zone | 211763410 | 27-02-2025 15:46 | 0 | DV0.8501.C4../2420073 | OIL HOSE MISSING | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the dg noticed the hose for block to centrifugal pump conneting hose missing, goem side start the engine oil are leak, | Closed | Mr. NandhaGopal
38 | South Zone | 211763399 | 27-02-2025 15:44 | 10 | GP3.8301.../2420560 | Starting Problem Call by : Customer Name : Naresh kumar Contact : 9886324445 | Open | BELLARY NIRMITI KENDRA | KALA Care Global LLP - Ballari |  | visit pending | Open | Mr. Anil Kumar H G
46 | South Zone | 211763361 | 27-02-2025 15:37 | 5.5 | CC1.1013.../2400027 | Oil Leakage Issue Call By Customer Name-Leena Number-8762664450 | Closed | MARIYA KUTTY | Prasad Power Engineers - Chikmagalore | 87 | ENGINE OIL LEAKAGE FROM INLET MANIFOLD SO WE HAVE TO REMOVE THE INLET MANIGOLD AND CLEAN IT AND CHECK THE NOZZLE AND CLEAN IT BY HAND AND WE HAVE | Closed | Mr. Anil Kumar H G
54 | South Zone | 211763111 | 27-02-2025 14:56 | 58.5 | T4.8941.../2421377 | Earthing no done | Task Start | Seva Bharathi | Prasad Power Engineers - Mangalore | LR | proper earthing is given properly, checked found 1body eathing given informe to the customer required one more body earthing pit | Task Start | Mr. Anil Kumar H G
52 | South Zone | 211762811 | 27-02-2025 13:48 | 20 | GP3.8601.../2421416 | Trip_Genset_Low_Voltage | Open | MS. Power Systems | Prasad Power Engineers - Hassan | NA | load issue, visiting the site with load analyzer | Open | Mr. Anil Kumar H G | KRM data
58 | South Zone | 211762798 | 27-02-2025 13:44 | 320 | F6.8802.../2420118 | Abnormal Sound Issue Call By Customer Name :- Devaraj G Mobile No :-7022982424 | Task Start | AVIGIRI URETHANE & RUBBER INDUSTRIES PVT LTD | Prasad Power Engineers - Tumkur | NA | abnormal sound from alternator, visit pending with nidec team | Task Start | Mr. Anil Kumar H G | Details required
31 | South Zone | 211762686 | 27-02-2025 13:27 | 125.4 | 4H.8042.C4../2420125 | Starting/Stopping Issue | Closed | NEW ALANKAR HYPER MARKET | Electro Controls - Kottayam | 62 | Adblue level low, top-up the adblue, clear the DTC | Closed | Mr. Sanjaimon S
15 | South Zone | 211762359 | 27-02-2025 12:54 | 125.4 | 4H.8042.C4../2420482 | Leakage Issue | Closed | Kayes Enterprises | Bharath Diesel Sales and Service - Salem | 4.2 | leakage from radiator bottom hose side so retightned the hose clip | Closed | Mr. NandhaGopal
25 | South Zone | 211762281 | 27-02-2025 12:50 | 35 | 3H.8902.../2422082 | Starting Problem Call by : Customer Name :Suresh Contact :9488361201 | Open | Gokulam Textiles And Readymades | Electro Controls - Marthandam | 55 | error code issue,5838/1,2791/18, connected to Diagnostic tool ECU Flashing,as per koel PSE Guidance,now alarm cleared, | Open | Mr. Sanjaimon S
10 | South zone | 211762132 | 27-02-2025 12:22 | 250 | F6.8842.C4../2420101 | Automation Issue Call By Customer Name :- Ganesh Sir Mobile No :- 9930041244 | Closed | Appidi Usha Kiran | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 9.54 | engine not starting in auto mode so we check the controller mains was enabled | closed | Mr. MD Saleem
63 | South Zone | 211762047 | 27-02-2025 12:10 | 58.5 | T4.8941.../2421495 | Preventive Maintenance Call by : Customer Name :Govardhan Contact :7092500019 | Cancelled | Goodspace Infrastructure Development LLP | Ultimate Power Source - Nellore |  | cancelled | Cancelled | Mr. NandhaGopal
36 | South Zone | 211761789 | 27-02-2025 11:35 | 20 | GP3.8601.../2420298 | Battery voltage problem Call by : Customer Name : Mihraj Contact : 8330080117 | Closed | THARAYIL FUELS | G-Care Diesels Private Limited - Thrissur | 149 | battery voltage low. Control -ve connection loose . Tight the wire. Problem clear. Dg running with load all parameters are checking dg performance is good | Closed | Mr. Sanjaimon S
24 | South Zone | 211761778 | 27-02-2025 11:31 | 5.5 | CC1.1013.../2400076 | Voltage Fluctuation | Closed | Glob Mart | Electro Controls - Mavalikara | 8 | Attended the site and checked the dg. Found the no speed signal Alarm show in controller. Checked and cleaned magnetic pick up unit and its connector. Then dg start to take full load. Presently dg is all good. | Closed | Mr. Sanjaimon S
33 | South Zone | 211761723 | 27-02-2025 11:18 | 58.5 | T4.8941.../2423009 | Starting/Stopping Issue | Closed | Pallassana Pazhayakavu Bhagavathy Devaswom Trust | Electro Controls - Palakkad |  | Visited the site, checked everything systemwise found engine is stopping is due to emergency stop alarm indicating, so checked the emergency stop found normal , found connector no 1H & 1 missing continuos negetive supply , indicating emergency stop some times . So corrected the same and started the engine with load 1 hr found no alarms , performance ok | Closed | Mr. Sanjaimon S
62 | South Zone | 211761486 | 27-02-2025 10:34 | 15 | GP3.8501.../2421693 | Trip_Genset_Low_Voltage | Closed | Elite Engineers | Ultimate Power Source - Kurnool | 258 | visit the site, but no issue found | Closed | Mr. NandhaGopal
42 | South Zone | 211761433 | 27-02-2025 10:29 | 15 | GP3.8501.../2421011 | Flickering | Closed | Arjun Builders | Laxmi Diesels - Vizianagaram | 20 | As per attend the site dg started but automatically Stop because of under voltage alarm B phase fuse problem so replace the new fuse and natural wire loose tight the wire and started the dg running condition found ok | Closed | Mr. MD Saleem
17 | East | 211758338 | 26-02-2025 12:09 | 5 | CP1.1003.../2400192 | STARTING KEY NOT WORKING | Task Start | North East Powerline Equipment Pvt.Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 49 | Low oil pressure due to low oil level. Topped up the oil and problem got resolved | CLOSED | Ujjwal Das
4 | East | 211750262 | 24-02-2025 11:34 | 2.8 | AP1.7003.../2400155 | Starting Issue Email by KGD Name - PRADAN | Open | PRADAN | Gangpur Sales and Services - BHUBANESWAR |  | Cancelled the SR | CANCELLED | Ujjwal Das
1 | East | 211848800 | 23-03-2025 13:08 | 5.5 | CC1.1013.../2400798 | LUBE OIL NOT AVAILABLE | Task Start | Vijay Lakshmi Construction | Gangpur Sales and Services - BHUBANESWAR |  | Today SE Will visit site | OPEN | Ujjwal Das
2 | East | 211851409 | 23-03-2025 12:55 | 20 | GP3.8601.../2420360 | Starting/Stopping Issue | Closed | Bhambra Auto Centre | Revenus Industries Pvt. Ltd. - Howrah | 51 | SE found starting problem for air locked in fuel line , after that release the air in fuel line issue resolved. | CLOSED | Prosanjit saha
3 | East | 211851223 | 23-03-2025 07:12 | 250 | F6.8842.C4../2420041 | Starting Issue Call By Customer Name - Abdul Rahim Number - 9851012211 | Open | N. S. R. R. K. Cold Storage Pvt. Ltd. | Revenus Industries Pvt. Ltd. - Malda |  | Visit Pending | OPEN | Prosanjit saha
1 | North | 211850508 | 22-03-2025 19:46 | 20 | GP3.8601.../2420506 | Display issue And Starting issue Call By customer Name:Archit Tripathi Number:8756663993 | Closed | Mr. Archit Tripathi | S. R Engines Sales And Service - Gorakhpur | 601 | Controller display brightness low, so increase the brightness then DG set on the Auto mode after start the DG then issue resolve | Closed | Sudhir Awasthi
2 | North | 211850488 | 22-03-2025 18:51 | 58.5 | T4.8941.../2423172 | MOBILE OIL LEAKAGE CALL BY CUSTOMER NAME-RAM BALAK NUMBER-9818426852 | Closed | SHIVAM DIESEL POWER | Paluck Technologies Ltd. - Gurgaon | 2.9 | Coustomer appointment for the Next working day | open | Kapil Solanki
3 | North | 211850230 | 22-03-2025 17:39 | 4 | CC1.4035.../2400022 | Inspection/Maintenance | Task Start | KNIP-SIPL (JV) | S.S. Enterprises - Sonbhadra | 396 | SR open for Maintenance | Closed | Sudhir Awasthi
4 | North | 211850210 | 22-03-2025 17:37 | 4 | CC1.4035.../2400027 | Inspection/Maintenance | Task Start | KNIP-SIPL (JV) | S.S. Enterprises - Sonbhadra | 197 | SR open for Maintenance | Closed | Sudhir Awasthi
4 | East | 211850199 | 22-03-2025 17:35 | 40 | 3H.8951.../2421571 | Starting/Stopping Issue | Closed | SHYAM POWER SOLUTION | Gangpur Sales and Services - Bhubaneswar | 45 | No Issue in DG, Customer side unbalance load | CLOSED | Ujjwal Das
5 | East | 211850043 | 22-03-2025 17:10 | 58.5 | T4.8941.../2422906 | Electrical Problems | Closed | M/s. Nawah Corporate Pvt. Ltd. | Gangpur Sales and Services - Bhubaneswar | 37 | SE found emergency switch alarm so tighten all connection related the emergency switch but not resolved so he provided direct negative connection from battery,Issue resolved. | CLOSED | Ujjwal Das | Resolve issue with proper way
5 | North | 211850038 | 22-03-2025 17:09 | 15 | GP3.8501.../2420074 | Genset Trip | Closed | Ashirwad Hospital. | Pratap Diesels Pvt. Ltd. - Bharatpur | 24 | Battery voltage low, Battery charger connection not connected | Closed | Gourav Sharma
1 | WEST | 211849928 | 22-03-2025 16:50 | 200 | 6H.8435.../2420073 | Umber Lamp on Alarm Issue. Call By Customer Name :- Vivek Mobile No :-9511897002 | Closed | CIP. Farm Private Limited | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 116 | Adblue level low so top up adblue level | Closed | Jagdeep saini
2 | WEST | 211849509 | 22-03-2025 15:38 | 25 | GP3.8702.../2420925 | Starting Issue Email By - KGD Name -Vishal Raut | Closed | Keys Reality | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 98 | Air lock isssue remove air lock | Closed | Jagdeep saini
6 | North | 211849420 | 22-03-2025 15:22 | 62.5 | T4.8941.../2320076 | Battery problem Call by : Customer Name : Ajay Kumar Contact : 8851779755 | Task Start | Tata Tele services | Paluck Technologies Ltd. - Ghaziabad | 318 | Modified v-belt change (T4.438.02.0.PR) STRECH FIT BELT (5PK1148) FOR 4R810 ENGINE | Closed | Kapil Solanki | Discuss with ASE what work on this issue.
6 | East | 211849334 | 22-03-2025 15:07 | 58.5 | T4.8941.../2420312 | Starting/Stopping Issue | Closed | Kabita Maternity and Nurshing Home. | Revenus Industries Pvt. Ltd. - Berhampore | 130 | SE found that Mains senseing Fuse Burn out so Fuse changeing from customer stock then check Lube oil Level and coolant Level found ok, issue resolved | CLOSED | Prosanjit saha
7 | North | 211849309 | 22-03-2025 15:01 | 250 | F6.8842.C4../2420054 | Coolant low | Closed | Siddhartha Constructions | Espiem Engines & Machines (P) Limited - KANPUR | 28 | SPN/FMI 1761/16 low def level alarm topup the def then issue resolve | Closed | Sudhir Awasthi
8 | North | 211849142 | 22-03-2025 14:28 | 82.5 | 5H.8901.../2420750 | Code issuo | Closed | KALYAN JEWELLERS INDIA LTD | Deep Jyoti Electricals and Services - Shahjahanpur | 64 | SPN/FMI 1761/16 low def level alarm topup the def then issue resolve | Closed | Sudhir Awasthi
9 | North | 211849060 | 22-03-2025 14:04 | 20 | GP3.1021.../2420369 | INSTANCE ID :-100779503 SITE ID :-I-UE-SANS-ENB-G001 CALL BY CUSTOMER// DG ISSUE :- STARTTING PROBLEM NAME :- Adarsh Pandey NUMBER :-9559883130 | Closed | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Raebareli | 590 | Check engine penal wiring and found fuse blown, so change th fuse and start the dg then issue was resolve | Closed | Sudhir Awasthi
3 | WEST | 211849024 | 22-03-2025 13:56 | 58.5 | T4.8941.../2422608 | Genset Trip | Closed | Sunil Rohokale | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 3 | Customer donot know how to start the dg so educate the customer. | Closed | Jagdeep saini
10 | North | 211848969 | 22-03-2025 13:47 | 125.4 | 4H.8042.C4../2420073 | Starting/Stopping Issue | Closed | SHAKUNTLA SINGH | Deep Jyoti Electricals and Services - Bareilly | 372 | Starting issue check the battery voltage found ok then remove the ECU connector after that reconnect & topup the def then issue resolve | Closed | Sudhir Awasthi
11 | North | 211848953 | 22-03-2025 13:43 | 58.5 | T4.8941.../2520498 | Load Issue Call By Customer Name :-Sarvesh Kumar Mobile No :- Sarvesh Kumar | Closed | ADARSH AUTO INDUSTRIES | Paluck Technologies Ltd. - Ghaziabad | 2 | Jerk load on the DG Educate the customer for load | Closed | Kapil Solanki
7 | East | 211848530 | 22-03-2025 12:19 | 30 | 3H.8902.../2421425 | Auto not working | Closed | LAXMI PRADHAN | Gangpur Sales and Services - Berhampur | 6 | Update Pending | CLOSED | Ujjwal Das
12 | North | 211848417 | 22-03-2025 12:00 | 58.5 | T4.8941.../2422461 | Tripping issue Call By Customer Name :- Piyush Sharma Number :- 9024022020 | Closed | KHANDELWAL ENTERPRISES | Pratap Diesels Pvt. Ltd. - JAIPUR | 302 | SPN/FMI 2791/1 found in DM 2 it clear and dc supply MCB CONNECTION check and loose found it retight the same after that issue resolve | Closed | Gourav Sharma
8 | East | 211848046 | 22-03-2025 10:55 | 20 | GP3.8601.../2520165 | Leakage Issue | Task Start | Sai Bhawani Service Station | Revenus Industries Pvt. Ltd. - Md. Bazar |  | Visit Pending | OPEN | Prosanjit saha
13 | North | 211847761 | 22-03-2025 09:57 | 200 | 6H.8435.../2420171 | Starting/Stopping Issue | Closed | H.SAQLAINI COLD STORE | Deep Jyoti Electricals and Services - Bareilly | 80 | SPN/FMI 1761/15, 516166/0 after that reset the alarm & topup the Def then issue was resolve | Closed | Sudhir Awasthi
14 | North | 211847736 | 22-03-2025 09:49 | 58.5 | T4.8941.../2422818 | Starting issue Call by Customer Name - Rahul Garg Number - 9759445599 | Closed | DD MOTORS | Paluck Technologies Ltd. - Ghaziabad | 47 | Airlock in fuel line remove the air then issue was resolve | Closed | Kapil Solanki
15 | North | 211847734 | 22-03-2025 09:48 | 30 | 3H.8902.../2420937 | Inspection/Maintenance | Cancelled | LAXMI ENTERPRISES | Rajdhani Diesels and Electricals - Jodhpur |  | Cancelled- Problem solve in pm visit | Cancelled | Gourav Sharma
16 | North | 211847652 | 22-03-2025 09:17 | 125.4 | 4H.8042.C4../2420431 | Starting Issue Email By - Customer Name -Suryanarayanan.s | Closed | AARTHI SCANS PVT LTD | Paluck Technologies Ltd. - Faridabad | 47 | Emergency Switch on pressed condition realeased the same issue resolve | Closed | Kapil Solanki
17 | North | 211847617 | 22-03-2025 08:08 | 58.5 | T4.8941.../2423162 | Starting Issue Call By Customer Name :- Navin .. Mobile No :- 7014415043 | Closed | Bharat Packaging | Pratap Diesels Pvt. Ltd. - Bhiwadi | 22 | Water in fuel alarm then cleaning the Tank & change the Filter and collect the Fuel sample | Closed | Gourav Sharma
15 | East | 211745776 | 22-02-2025 11:56 | 5.5 | CC1.1013.../2400016 | Starting Issue Call By Customer Name :- Shakti Kumar Mobile No :- 6294815565 | Open | East Coast Railway Andhra Pradesh | HACS Engineering and Tech Private Limited - Dhanbad | 65 | PM required. Need to cancel | CANCELLED | Prabhakar Kumar
18 | North | 211847117 | 21-03-2025 23:01 | 58.5 | T4.8941.../2520344 | Battery Issue Call By Customer Name:-MAYANK No8949552031 | Closed | NEHA KAUSHIK C/O HOTEL JAIPUR INN | Espiem Engines & Machines (P) Limited - Agra | 3 | Battery voltage low, Battery charger connection not connected from customer end, Educate the customer please always give the continue supply (230V AC) | Closed | Sudhir Awasthi
19 | North | 211845933 | 21-03-2025 16:44 | 58.5 | T4.8941.../2422818 | Starting issue Call by Customer Name - Rahul Garg Number - 9759445599 | Closed | DD MOTORS | Paluck Technologies Ltd. - Ghaziabad | 4 | Airlock in fuel line remove the air then issue was resolve | Closed | Kapil Solanki
20 | North | 211845904 | 21-03-2025 16:43 | 20 | GP3.8601.../2520129 | Automation Issue Call By Customer Name :Bijin David Number 8447314401 | Cancelled | Modern Constructions | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Cancelled- Problem solve in tele. Discustion | Cancelled | Kapil Solanki
7 | WEST | 211845751 | 21-03-2025 16:20 | 200 | 6H.8438.C4../2420025 | Genset Trip | Closed | Faith Automation System & Tooling Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 88 | charging alternator I bolt found broken , belt found broken , replace the belt and ibolt. | Closed | Jagdeep saini
8 | WEST | 211845672 | 21-03-2025 16:09 | 30 | 3H.8902.../2420202 | Starting/Stopping Issue | Closed | Prof. J. P. Trivedi Memorial Trust. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 86 | Dg automatically stop due to R phase fuse found burn so change the fuse , issue solved | Closed | Jagdeep saini | KRM data
21 | North | 211845656 | 21-03-2025 16:04 | 125.4 | 4H.8042.C4../2421139 | ALARAM ISSUE CALL BY CUSTOMER NAME-Deepak NUMBER-9899929145 | Cancelled | Sheetla Aluminium "&" Fiber Glass Co | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Cancelled - No any issue | Cancelled | Kapil Solanki
22 | North | 211845511 | 21-03-2025 15:40 | 20 | GP3.8604.../2420179 | INSTANCE ID:-100742002 SITE ID:- I-RJ-OSNN-ENB-G002 CALL BY CUSTOMER// DG ISSUE:- DG fuel abnormal issue NAME:- derandar singh NUMBER:- 9982247536 | Open | Reliance Jio Infocomm Limited | Rajdhani Diesels and Electricals - Jodhpur |  | Visit pending | open | Gourav Sharma
14 | WEST | 211845417 | 21-03-2025 15:23 | 40 | 3H.8951.../2421368 | Starting Issue Call By Customer Name :- Omkar Mobile No :- 8551031443 | Closed | Blinkit. . | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 69 | 2791,5- Engine Exhaust Gas Recirculation 1 Valve 1 Control 1-Current Below Normal alarm so connect ikonnect tool and clear error code. | Closed | Jagdeep saini
12 | WEST | 211845227 | 21-03-2025 14:50 | 125.4 | 4H.8042.C4../2420577 | DIESEL LEAKAGE PROBLEM. | Completed | Suresh Dharmavat & Associate | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 9 | Fuel leakage NRV valve adaptor return line , tight the same issue solved. | Closed | Jagdeep saini
9 | East | 211845221 | 21-03-2025 14:49 | 10 | GP3.8301.../2420013 | Voltage Fluctuation | Closed | INDIAN BANK | Gangpur Sales and Services - BHUBANESWAR | 29 | Update Pending | CLOSED | Ujjwal Das
23 | North | 211845164 | 21-03-2025 14:36 | 200 | 6H.8435.../2320034 | Service | Cancelled | UPPAL CHADHA HI-TECH DEVELOPERS [P] LTD | Paluck Technologies Ltd. - Ghaziabad |  | Cancelled - Problem solve in PM visit | Cancelled | Kapil Solanki
10 | East | 211845102 | 21-03-2025 14:14 | 500 | DV8.8501.C4../2420180 | Leakage Issue | Closed | Amunra Infratech Private Limited | K.C. Diesel Services - East Sikkim | 68 | There was coolant leakage at thermostat outlet hose due to clamp loose after tightening the clamp issue resolved | CLOSED | Prosanjit saha
24 | North | 211844887 | 21-03-2025 13:37 | 57 | T4.8941.../2320155 | Genset Trip | Closed | Texo Industries Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 353 | Coolant tem. High alarm then check & found Raditor was chocked after educate the customer kindly clean the radiator | Closed | Gourav Sharma
13 | WEST | 211844895 | 21-03-2025 13:35 | 30 | 3H.8902.../2421745 | Automation and Under Speed Alarm issue Call By Customer Name:- Dilip lokhande No:-8850290508 | Closed | DILIPO MACHCHHINDRA LOKHANDE | KALA Care Global LLP - Babhleshwar | 115 | Air lock isssue remove air lock | Closed | Jagdeep saini
25 | North | 211844398 | 21-03-2025 12:22 | 45 | 3H.8951.../2421398 | Starting issue Call By Customer Name:- Sachin Kumar Singh No:-8840737025 | Closed | KSM Bashir Mohd. & Sons | R K Engineers - Meerut | 378 | Found 2B wire loose in Starting relay after tightness the wire then issue was resolve | Closed | Sudhir Awasthi
11 | East | 211844356 | 21-03-2025 12:15 | 30 | 3H.8902.../2420195 | Trip_Genset_Low_Voltage | Cancelled | JHULAN MEHER | Gangpur Sales and Services - Subarnapur |  | SR Created by customer mistake, so cancel the SR | CANCELLED | Ujjwal Das
26 | North | 211844166 | 21-03-2025 11:39 | 500 | DV8.8501.C4../2420048 | URIA ISSUE Call By Customer Name :- Call By Customer Name :- Rajkumar Mobile No :- 9467425910 | Task Start | Shahi Dyeing Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | Today again Engineer visit | open | Kapil Solanki
27 | North | 211843970 | 21-03-2025 11:07 | 58.5 | T4.8941.../2423013 | Leakage Issue | Closed | SIA BUILDERS | OVN Industries Private Limited - New Delhi | 4 | found coolant top up and battery water top up and all connection ok fuel filter loose then tight the fuel filter ok and engine start and stop ok | Closed | Kapil Solanki
28 | North | 211843947 | 21-03-2025 11:07 | 125.4 | 4H.8042.C4../2420330 | Maintenance Due Alarm Issue Call By Customer Name :- Rajiv . Mobile No :- 7054050413 | Closed | Shri Dhanushdhari Hotels and Resorts | Espiem Engines & Machines (P) Limited - Jhansi | 263 | maintence due alarm so, reset the alarm after that issue resolve | Closed | Sudhir Awasthi
29 | North | 211843951 | 21-03-2025 11:04 | 20 | GP3.8601.../2420170 | Starting Issue Call By Customer Name :- Devendra singh Sodi Mobile No :- 9996728387 | Closed | Devendra Singh Sodi | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 16 | All switch off condition on the switch after that issue resolve No issue found in DG | Closed | Kapil Solanki
18 | WEST | 211843906 | 21-03-2025 11:00 | 625 | DV0.8501.C4../2420032 | Leakage Issue | Task Start | TRANSGREEN AGRO AND LOGIX PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Baroda | 33.17 | Abnormal sound received from the main alternator so found the main stator winding burnt & lube oil leakage from rear oil seal. | OPEN | Amit sandlya | Mail for this
30 | North | 211843660 | 21-03-2025 10:15 | 750 | DV2.8501.C4../2320032 | ECU Amber Alarm Issue Call By Customer Name -Vijay . No -9412021709 | Closed | INDIAN POTASH LIMITED | R K Engineers - Muzaffarnagar | 14 | SPN/FMI 1761/15 523584/15 516166/0 Clear the DTC & topup the def after that issue was resolve | Closed | Sudhir Awasthi
31 | North | 211843457 | 21-03-2025 09:25 | 500 | DV8.8501.C4../2320028 | Low Coolant Level Alarm Issue Call By Customer Name :- Atul Kumar Mobile No :- 9953698074 | Closed | Neel Kamal Enterprises Private Limited | Paluck Technologies Ltd. - Faridabad | 554 | Found Coolant low level alarm, then check & found Coolant level ok, but alarm show continuous then check the Coolant level switch found faulty after replace the same then issue resolve | Closed | Kapil Solanki
32 | North | 211842387 | 20-03-2025 18:51 | 250 | F6.8842.C4../2420062 | Load Issue Email By - OEM Name -Shamim Ahmed | Closed | The Savoy And Holidays Resorts | Pratap Diesels Pvt. Ltd. - Alwar | 73 | found SPN 3031/14, 156/14 flash file and dummy file F6_D1.1234 after that remove all tappet cover and found cyl no 3 injectors H wire insulation minor damage and touch with rocker body apply taflon sleeve on cut properly re fitted all tappet cover with k.sealent after that issue resolve | Closed | Gourav Sharma
33 | North | 211841167 | 20-03-2025 17:00 |  | 6H.8475.../2520060 | LINE REJECTION | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-1 | Charging alternator not given the proper output voltage show in the multimeter only, 12.5 VDC | open | Gourav Sharma
12 | East | 211840989 | 20-03-2025 16:38 | 40 | 3H.8951.../2420658 | Expansion bellow faulty | Closed | Raja Soft Coke | Revenus Industries Pvt. Ltd. - Asansol | 139 | exhaust bend pipe of DOC found broken. So, replaced with new one which is provided by Elmech Engineers. Then exhaust pipe properly fitted. Then started the Genset on auto and manual mode found running performance normal and DG out put voltage found normal. | CLOSED | Prosanjit saha
10 | WEST | 211840751 | 20-03-2025 15:56 | 25 | GP3.8702.../2420338 | Electrical Problems | Open | Ramesh J. Raval. | Unique Techno Services Pvt Ltd. - Ahmedabad | 93.29 | SPN/FMI- 157/14 & 2802/3 Panel wiring checked, all found to be ok. PRV count was 45 then 0. Engineer will visit today today. | open | Amit shandilya
19 | WEST | 211840751 | 20-03-2025 15:56 | 25 | GP3.8702.../2420338 | Electrical Problems | Closed | Ramesh J. Raval. | Unique Techno Services Pvt Ltd. - Ahmedabad | 93.29 | SPN/FMI-157/14, 2802/3 Checked the all panel connection found OK. Used the cable tie on the panel & engine wiring connector, DG running smoothly. | Closed | Amit sandlya
34 | North | 211840558 | 20-03-2025 15:15 | 125.4 | 4H.8041.../2420878 | Door Lock Issue Call by Customer Name :Yogendra Sir No:8178271899 | Closed | SHRI SHAKTI GENERATOR SERVICE | Paluck Technologies Ltd. - Ghaziabad | 38 | Attend to site check door lock issue and found rain gard out and Jackson team visit required check door lock adjust the lock | Closed | Kapil Solanki
1 | North | 211840359 | 20-03-2025 14:25 | 58.5 | T4.8941.../2422288 | Fuel Leakage from DG,kindly resolve-521181 | Task Start | ICICI Bank Limited | SAAN Royal Power Solutions Private Limited - Mandi |  | Visit Pending | open | Ved Prakash Gupta
2 | North | 211840246 | 20-03-2025 13:54 | 125.4 | 4H.8041.../2420293 | Sound/Vibration Issue | Open | SHAKTI PULLEY MANUFACTURING COMPANY | SAAN Royal Power Solutions Private Limited - Rohtak | 250 | Abnormal sound due toBelt found in loose condition of Charging alternator ; tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
40 | North | 211840185 | 20-03-2025 13:39 | 625 | DV0.8501.C4../2420040 | Tripping Issue Call By Customer Name :-Shivam Kumar Mobile No :- 9099934992 | Closed | National Hotels Limited. | Rajdhani Diesels and Electricals - Jodhpur | 208 | Wiring loose in panel tightness to be all after that issue was resolve | Closed | Gourav Sharma
9 | North | 211840208 | 20-03-2025 13:37 | 250 | F6.8842.C4../2520007 | Automation Issue Call by customer Name : Naseem Sir Number : 9654086525 | Closed | MAA LAXMI NAMKEEN | Paluck Technologies Ltd. - Ghaziabad | 15.5 | Automation issue due to Customer's AMF pannel ; same communicated to customer | Closed | Kapil Solanki
10 | North | 211840124 | 20-03-2025 13:19 | 400 | DV8.8542.C4../2420140 | Electrical Problems | Closed | Apollo Hospitals (Indraprastha Medical Corporation Ltd.) | Vidyut Engineers - Noida | 31.3 | SPN/FMI-1761/16 ; Amber lamp on ,DEF not available on site so same communicated to customer | Closed | Kapil Solanki
41 | North | 211839989 | 20-03-2025 12:51 | 25 | GP3.8702.../2520242 | Load Issue And Tripping Issue Call By Customer Name :-Navneet Mobile No:-9794242560 | Open | OSS. Construction Pvt. Ltd. | Excel Diesel Private Limited - Faizabad | 323 | Customer gives the Suddenly jerk load 32Ampere on the DG so, Dg trip with under speed alarm RPM (1250) so, Engineer controller set the Under speed alarm(3 to 7 second) & Educate the customer for the jerk load | Closed | Sudhir Awasthi
42 | North | 211839852 | 20-03-2025 12:22 | 15 | GP3.8501.../2420835 | Tripping Issue. Call By Customer Name :- Ajay .. Mobile No :-7704834099 | Task Start | R & C INFRA ENGINEER'S PVT LTD | S. R Engines Sales And Service - LUCKNOW | 2515 | Controller show the High tem. Alarm, radiator was chocked, Air filter was chocked, service due last service on (1500 hours on paid Basis) | Closed | Sudhir Awasthi
3 | North | 211839809 | 20-03-2025 12:14 | 30 | 3H.8902.../2421539 | Genset is not working it reflecting the error PROTECT LAMP ON. | Open | Axis Bank Ltd | Gen Powers - PATIALA |  | Visit Pending | open | Ved Prakash Gupta
11 | North | 211839748 | 20-03-2025 12:03 | 82.5 | 5H.8901.../2320021 | Electrical Problems | Task Start | CRMK Select | Vidyut Engineers - Noida | 236.37 | Abnormal sound found from engine side ; Unusual smell observed by dealer engineer from lube oil ; Radiator fan movement also with abnormal sound ; Mechanical engineer will attend site Today | open | Kapil Solanki
12 | North | 211839751 | 20-03-2025 12:00 | 500 | DV8.8501.C4../2420020 | Tripping Issue Call By Customer Name :- Ajay Mobile No :-9958214785 | Task Start | ESQUIRE TECH.. | Vidyut Engineers - New Delhi |  | Visit Pending | open | Kapil Solanki
43 | North | 211839677 | 20-03-2025 11:42 | 25 | GP3.8702.../2520255 | Under speed Alarm & Tripping Issue Call by Customer Name:-Arvind Kumar Mobile No:-7348044917 | Task Start | OSS. Construction Pvt. Ltd. | Excel Diesel Private Limited - Faizabad | 142 | Customer gives the Suddenly jerk load on the DG so, Dg trip with under speed alarm so, Engineer controller set the Under speed alarm(3 to 7 second) & Educate the customer for the jerk load | Closed | Sudhir Awasthi
1 | WEST | 211839453 | 20-03-2025 10:59 | 125.4 | 4H.8041.../2420260 | Display Problem Call by : Customer Name :Suriyanarayen Contact :9363499269 | Task Start | AARTHI SCANS PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 75 | Adblue level low so top up | Closed | Jagdeep Saini
44 | North | 211839340 | 20-03-2025 10:43 | 20 | GP3.1021.../2420387 | INSTANCE ID:- 100784741 SITE ID:- I-UE-POLR-ENB-9130 CALL BY CUSTOMER\\ DG ISSUE:-UNDER VOLTAGE ALRAM ISSUE NAME:-... Atul NUMBER:-8299698439 | Open | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | Visit pending | open | Sudhir Awasthi
15 | WEST | 211839325 | 20-03-2025 10:43 | 20 | GP3.8601.../2520211 | Wiring harness issue Email By - KGD Name -Ranajn Kowale | Cancelled | Third Eye Technologies and Services | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | Cancelled | Closed | Jagdeep saini
4 | North | 211839284 | 20-03-2025 10:36 | 58.5 | T4.8941.../2422230 | Starting/Stopping Issue | Task Start | LA HAULT | SAAN Royal Power Solutions Private Limited - Mandi | 32 | Update Pending | open | Ved Prakash Gupta
45 | North | 211839240 | 20-03-2025 10:23 | 125.4 | 4H.8042.C4../2420132 | Starting/Stopping Issue | Closed | DESERT VALLEY RESORT | Rajdhani Diesels and Electricals - Jodhpur | 289 | found 3031/14, 1761/16 in tool. Flash ECU 125kva_3031_14Dummy. Dg changing fail alarm issue. Check changing alternator found 40A fuse rust. Check continuity and clean fuse. Dg start or stop 4-5 time. Charger fail alarm not come again. | Closed | Gourav Sharma
46 | North | 211839182 | 20-03-2025 10:11 | 15 | GP3.8501.../2420834 | failed to start Issue Email by Customer Name - Sahdev Bishnoi | Task Start | Amar Jyoti Petrol Pump. | Rajdhani Diesels and Electricals - Jodhpur | 245 | Fuel filter & Air filter choke clean the both after that issue resolve | Closed | Gourav Sharma
47 | North | 211839051 | 20-03-2025 09:38 | 320 | F6.8802.../2420330 | Sound/Vibration Issue | Closed | Hirohama India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 144 | Low def level alarm rese the alarm & topup the def after that issue resolve | Closed | Gourav Sharma
48 | North | 211838996 | 20-03-2025 09:28 | 5.5 | CC1.1013.../2400086 | battery issue Call By Customer Name :- ankit Mobile No :- 9928340202 | Closed | Moti Lal Halwai. | Pratap Diesels Pvt. Ltd. - Ajmer | 20 | Controller display not on so, check battery voltage found ok, then give the direct supply Display on, after trace the wire then found that fuse was faulty after replace the fuse then issue resolve | Closed | Gourav Sharma
16 | WEST | 211838971 | 20-03-2025 08:57 | 20 | GP3.1021.../2420339 | DG Parameters are not visible in SMPS | Cancelled | Reliance Jio Infocomm Limited | Mahalaxmi Diesels - Pandharpur |  | Cancelled | Closed | Jagdeep saini
11 | WEST | 211838949 | 20-03-2025 08:49 | 20 | GP3.1021.../2420120 | INSTANCE ID:-100745773 SITE ID:- I-MP-SDHI-ENB-9003 CALL BY CUSTOMER// DG ISSUE:- DG DIESEEL ISSUE / GCU FAULTY NAME:- Jayprakash Patel NUMBER:- 9343012716 | Task Start | Reliance Jio Infocomm Limited | Shree Engineering Service - Satna | 328 | The controller is not turning on. Checked controller power supply on pins 39 and 40 - 12V. EDO placed for the controller. | open | Vijay Patil
49 | North | 211838951 | 20-03-2025 08:21 | 58.5 | T4.8941.../2422818 | Starting Issue Call By Customer Name :-Rahul Garg Mobile No:-9759445599 | Closed | DD MOTORS | Paluck Technologies Ltd. - Ghaziabad | 3 | Airlock in fuel line remove the air then issue was resolve | Closed | Kapil Solanki
7 | East | 211738536 | 20-02-2025 15:27 | 10 | GP3.8301.../2420342 | Engine starting issue | Task Start | M/s. SRIDHANA LAXMI SWEETS | Gangpur Sales and Services - Rourkela | 2 | Rocker assembly broken. Engine is under transit | OPEN | Ujjwal Das
50 | North | 211838247 | 19-03-2025 21:07 | 750 | DV2.8501.C4../2420083 | Load Issue Call By Customer Name :- Parbhakar VCL Number :- 8130464848 | Task Start | Leisure Park Apartment Owner Association | Rajdhani Diesels and Electricals - Jodhpur |  | Customer not give the breakdown | open | Gourav Sharma
20 | East | 211838256 | 19-03-2025 20:56 | 125.4 | 4H.8042.C4../2520044 | Alarm Issue Call By Customer Name:-Sunil . No:-7978605139 | Open | SHANTILATA HOSPITAL AND RESEARCH CENTRE PVT LTD | Gangpur Sales and Services - Jharsuguda | 34 | Visit Pending | OPEN | Ujjwal Das
13 | North | 211838224 | 19-03-2025 20:14 | 400 | 6H.8439.../2420002 & 2420002 | Starting/Stopping Issue | Closed | SKH Sila India Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 75 | Complaint raised as starting issue but no such issue found on site | Closed | Kapil Solanki
2 | WEST | 211838219 | 19-03-2025 20:00 | 58.5 | 6H.9840.../2420014 | Starting issue | Task Start | FUJI TECHNICAL SERVICES PVT LTD | Transcreek Engineers Pvt. Ltd. - Ambernath | 3 | Time of crancking , some amout of gas need to realse from pressure release valve . | Closed | Jagdeep Saini | After Meeting will connect with site engg.
14 | North | 211838156 | 19-03-2025 19:02 | 58.5 | T4.8941.../2422106 | Starting/Stopping Issue | Closed | Sudanshu Saigal. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 55 | Emergency switch found pressed on site so release the same & same communicated to customer | Closed | Kapil Solanki
51 | North | 211838047 | 19-03-2025 18:26 | 20 | GP3.8601.../2421554 | Preventive Maintenance Call By Customer Name : Divyanshu Number : 8006385913 | Cancelled | YAK & YETI INN | Deep Jyoti Electricals and Services - Haldwani |  | Cancelled-Problem solve in PM visit | Cancelled | Sudhir Awasthi
30 | WEST | 211838033 | 19-03-2025 18:16 | 250 | F6.8841.../2420357 | Starting Issue. Call By Customer. Name:-Achyut .. Mobile No.:-6359919875 | Open | SHREE SWAMINARAYAN GURUKUL | Unique Techno Services Pvt Ltd. - Ahmedabad |  | Low battery voltage - 7.5V, so engineer will visit with float battery and investigate further. | Closed
3 | WEST | 211837970 | 19-03-2025 18:02 | 125.4 | 4H.8042.C4../2420927 | Umber Lamp on Alarm Issue Call by Customer Name:-Dayanad sen Mobile No:-8087245056 | Closed | SHIVSAI CONSTRUCTION | Transcreek Engineers Pvt. Ltd. - Panvel | 50 | Error code 3031 Adblue temp high , no issue found connect ikonnect and clear error code. | Closed | Jagdeep Saini
10 | WEST | 211837863 | 19-03-2025 17:41 | 40 | 3H.8951.../2420714 | Display Issue Call By Customer Name :-Sujeet Mobile No:-9637187934 | Closed | AJIT RAMA GIMBHAL | Transcreek Engineers Pvt. Ltd. - Boisar | 219 | Display not working found 1c2 and 2D loose connection , tight the conndction issue solved. | Closed | Jagdeep Saini
4 | WEST | 211837864 | 19-03-2025 17:41 | 40 | 3H.8951.../2520199 | Fuel Sensor issue Call By Customer Name :- Lallan Singh Number :- 9820226317 | Cancelled | Bharat Shatrughna Coop Housing Society | Transcreek Engineers Pvt. Ltd. - Navi Mumbai |  | cancelled | Closed | Jagdeep Saini
9 | WEST | 211837864 | 19-03-2025 17:41 | 40 | 3H.8951.../2520199 | Fuel Sensor issue Call By Customer Name :- Lallan Singh Number :- 9820226317 | Cancelled | Bharat Shatrughna Coop Housing Society | Transcreek Engineers Pvt. Ltd. - Navi Mumbai |  | Cancelled | Closed | Jagdeep saini
15 | North | 211837779 | 19-03-2025 17:26 | 160 | 6H.8475.../2320006 | Door Lock Issue. Call by Customer. Name:- pawan Kumar. Mobile No.:-9354544627 | Closed | ENERDYNE DEVICES PVT. LTD. | Vidyut Engineers - Noida | 202 | Canopy door lock alignment issue ; adjusted the same & resolve the Issue | Closed | Kapil Solanki
10 | WEST | 211837705 | 19-03-2025 17:12 | 30 | 3H.8902.../2420409 | Inspection/Maintenance | Cancelled | ISC Projects Pvt Ltd. | Mahalaxmi Diesels - Dharashiv |  | Cancelled | Closed | Jagdeep saini
16 | North | 211837654 | 19-03-2025 17:01 | 125.4 | 4H.8041.../2320145 | Battery Issue Call By Customer Name :- Datta Mobile No :- 9599637302 | Closed | V. M. Technocoatings | Vidyut Engineers - Noida | 101 | Battery Voltage found very low & not charging so started DG with Float battery(Get from customer) & sent KOEL DG Battery for testing | Closed | Kapil Solanki | Details required after verification
5 | North | 211837580 | 19-03-2025 16:44 | 125.4 | 4H.8042.C4../2420689 | Alarm issue | Open | PRIDE INFRATECH | SAAN Royal Power Solutions Private Limited - Sonipat | 254.51 | SPN/FMI-1761/16 ; Amber lamp on , customer said that Cap of DEF Tank is not opening ; Open the same with help of Key master & top-up AdBlue | Closed | Ved Prakash Gupta
5 | WEST | 211837562 | 19-03-2025 16:44 | 250 | F6.8841.../2420145 | Starting Issue Email By - GOEM Name -Surekha Auti | Open | Rama Synergy Spaces Metro Life Ultima Residences. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | cancelled | Closed | Jagdeep Saini
11 | WEST | 211837562 | 19-03-2025 16:44 | 250 | F6.8841.../2420145 | Starting Issue Email By - GOEM Name -Surekha Auti | Cancelled | Rama Synergy Spaces Metro Life Ultima Residences. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | Cancelled | Closed | Jagdeep saini
17 | North | 211837536 | 19-03-2025 16:38 | 82.5 | 5H.8901.../2320020 | Starting Issue Call by customer Name : Somnath Sir Number : 9999239052 | Closed | KRISHNA GUEST HOUSE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 43 | Starting Issue due to battery found discharged ; Battery charger connection with single phase found dis-connected on site so re-connected the same & keep battery on Charging | Closed | Kapil Solanki
21 | East | 211837510 | 19-03-2025 16:31 | 30 | 3H.8902.../2421618 | Coolant leakage issue Call by Customer Name - Akash Barit Number - 8917370280 | Task Start | Advik Infra | Gangpur Sales and Services - Angul | 49 | Visit Pending | OPEN | Ujjwal Das
52 | North | 211837445 | 19-03-2025 16:16 | 45 | 3H.8951.../2421405 | Leakage Issue | Closed | Kamal Machinery Stores. | S. R Engines Sales And Service - Gorakhpur | 77 | Low load from customer side & coolant level low so, topup the coolant & Increse the load for Educate the Customer | Closed | Sudhir Awasthi
6 | North | 211837318 | 19-03-2025 15:51 | 82.5 | 5H.8901.../2420554 | Starting Issue Call By Customer Name:-RAVI KUMAR . No:-9671012574 | Closed | No. One Ahuja Dhaba & Rooms. | SAAN Royal Power Solutions Private Limited - Sonipat | 74.11 | DG used to trip just after start command ; found 2B3 wire loose on DC MCB (32 AMP) loose so re-connected the same properly & start the DG , Issue resolved | Closed | Ved Prakash Gupta
18 | North | 211837270 | 19-03-2025 15:40 | 58.5 | T4.8941.../2422818 | Starting Issue Call By Customer Name :-Rahul Garg Mobile No:-9759445599 | Closed | DD MOTORS | Paluck Technologies Ltd. - Ghaziabad | 2 | Air lock in fuel line remove the air after that issue resolve | Closed | Kapil Solanki
19 | North | 211837193 | 19-03-2025 15:30 | 58.5 | 6H.9840.../2420007 | Starting/Stopping Issue | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 46 | PNG Gas ; Same adjusted from ZPR | Closed | Kapil Solanki
53 | North | 211837145 | 19-03-2025 15:20 | 7.5 | D3.8305.../2400175 | fluctuation issue Email By KGD Name:- Yash Dev Dahiya | Task Start | AMIT AUTOMOBILES | R K Engineers - Meerut | 2 | Light flactuation so, replace the AVR change in TAVR-20 | Closed | Sudhir Awasthi
7 | North | 211837120 | 19-03-2025 15:15 | 30 | 3H.8902.../2421409 | Automation issue Call by Customer Name - Inderjit Singh Number - 8437379111 | Closed | Head Master Corporate Office C/o. Gillz Beauty & Wellness Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Zirakpur | 25 | Controller showing fuel level variable ; Fuel guage support one bolt found damaged ; grind the same & re-fitted guage in opposite direction ; now fuel level showing constant & right value (61%) | Closed | Ved Prakash Gupta
16 | East | 211837108 | 19-03-2025 15:11 | 160 | 6H.8475.../2420162 | Fan belt brocken | Task Start | Ms Ankur Enterprise | Hibreed Engineering Pvt. Ltd. - Nagaon | 333 | SE visited and found belt loose due to which abnormal sound was audible so adjusted the belt by eye bolt issue resolved | CLOSED | Ujjwal Das
20 | North | 211837043 | 19-03-2025 14:55 | 58.5 | T4.8941.../2520483 | Voltage Fluctuation issue Call By Customer Name:Aaysha Number:9810982850 | Closed | GREEN ENRERGY DIESEL ENGINES PVT LTD | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 12 | Update Pending | open | Kapil Solanki
54 | North | 211836976 | 19-03-2025 14:38 | 40 | 3H.8951.../2420356 | Starting issue Call By Customer Name :- Goga Ram Number :- 9602062139 | Task Start | Sudharam Assoceates | Rajdhani Diesels and Electricals - Barmer | 1335 | Relay card faulty replace the relay after that issue resolve (RELAY BOARD 2 & 1/2 12V DC) | Closed | Gourav Sharma
21 | North | 211836881 | 19-03-2025 14:18 | 125.4 | 4H.8042.C4../2520020 | VOC - CANOPY DOOR/LOCK PROBLEM Customer Name -Shubham Chauhan Customer Number -9958033547 Mode- SR Generated through CDI calling. | Closed | ELEDECO FAIRWAY RESERVE | Paluck Technologies Ltd. - Gurgaon | 282 | Canopy door lock alignment issue ; adjusted the same & resolve the Issue | Closed | Kapil Solanki
17 | East | 211836861 | 19-03-2025 14:10 | 125.4 | 4H.8042.C4../2420886 | Error code issue Call By Customer Name :- Abdul Number :- 8134963146 | Open | Mech Technik India Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Bongaigaon |  | Found ECU fault code 516166,3031/15 after flashing ECU issue resolved | CLOSED | Ujjwal Das
18 | East | 211836832 | 19-03-2025 14:05 | 5 | CP1.1003.../2400165 | Starting Issue Call By Customer Name :-Tarh Mayeng Mobile No :- 8787559248 | Open | City Club | M T Enterprises - Bomdila |  | visit Pending | OPEN | Ujjwal Das
| WEST | 211836796 | 19-03-2025 13:55 | 125.4 | 4H.8042.C4../2420152 | Starting Problem Call by : Customer Name : Aravind Contact : 9676799011 | Task Start | PSOVL RAILONE PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Surat | 182 | Air lock problem so fuel line checked, no leak found. DG starts after using hand primer pump. Next visit is required. | Closed
1 | North | 211836724 | 19-03-2025 13:39 | 30 | 3H.8902.../2320094 | Starting/Stopping Issue | Under Monitoring | DURGESH INDUSTRIES | Paluck Technologies Ltd. - Faridabad | 430 | During morning DG not start, Check the battery condition found ok, Now Today visit with battery tester | open | Kapil Solanki
2 | North | 211836707 | 19-03-2025 13:28 | 250 | F6.8841.../2420091 | Genset Trip | Task Start | Dr.Rakesh Khare | Deep Jyoti Electricals and Services - Moradabad |  | Today Engineer visit | open | Sudhir Awasthi
19 | East | 211836631 | 19-03-2025 13:11 | 82.5 | 5H.8901.../2420301 | Error code issue Email By KGD Name :-SUNRISE POWER | Open | HIGHWAY HAVELI | Globalline India Services Private Limited - Darbhanga |  | low def leve alarm, SR under cancellation | CANCELLED | Prabhakar Kumar
1 | East | 211836550 | 19-03-2025 12:59 | 320 | F6.8802.../2420359 | Starting issue Call By KGD Name :- Babalu Chaudhari Number :- 8822574811 | Open | SUBHASH CHANDRA RABHA | Hibreed Engineering Pvt. Ltd. - Guwahati | 2.4 | Visit pending | OPEN | Ujjwal Das
3 | East | 211836506 | 19-03-2025 12:58 | 30 | 3H.8902.../2422417 | Oil leakage problem Call by : Customer Name :Kajamuhin Contact : 9346547429 | Task Start | Trenzet Infra Private Limited | HACS Engineering and Tech Private Limited - Dhanbad | 169 | SE visited and found that EGR bellow clamp was loose and lube oil seepage from there so clean the EGR and refitted it and also suggested customer to operate DG on mini. 30% load. | CLOSED | Prabhakar Kumar
2 | East | 211836519 | 19-03-2025 12:53 | 200 | 6H.8438.C4../2420034 | Sound issue | Open | Ultratech Cement Limited | Hibreed Engineering Pvt. Ltd. - Nagaon | 25 | SE visited site and found abnormal sound from the fan pulley side due to fan belt loose after tightening issue resolved | CLOSED | Ujjwal Das
11 | WEST | 211836495 | 19-03-2025 12:52 | 200 | 6H.8435.../2420019 | fan belt broken issue Call By Customer Name :-Sahid Number :-8091526887 | Closed | Bloom Suites | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 206 | V belt found broken so change the belt | Closed | Jagdeep Saini
35 | North | 211836478 | 19-03-2025 12:47 | 40 | 3H.8951.../2520044 | Red Lamp Alarm issue Call By Customer Name :- Manoj Number :- 9198938126 | Task Start | Ashish Traders | S.S. Enterprises - Allahabad | 134 | SPN/FMI 2791/1, 2791/18, 637/3 Engine Timing Sensor-Erratic,SPN: 5838,FMI: 1 - Engine Exhaust Gas Recirculation Valve Malfunction-Low , Change the EGR & Flash the ECU | Closed | Sudhir Awasthi | Check KRM data
22 | East | 211836455 | 19-03-2025 12:44 | 10 | GP3.8301.../2420398 | Starting/Stopping Issue | Closed | Hindalco Industries Ltd | Gangpur Sales and Services - BHUBANESWAR | 7 | Update Pending | CLOSED | Ujjwal Das
23 | East | 211836446 | 19-03-2025 12:43 | 10 | GP3.8301.../2420432 | Leakage Issue | Closed | Hindustan Construction Company Ltd. | Gangpur Sales and Services - BHUBANESWAR | 47 | As per complaint SE found no such leakage of diesel, and customer doubt was fuel sensor faulty but its was normal, Door lock was also not locking properly so adjusted its hook restored and customer satisfied. | CLOSED | Ujjwal Das
12 | WEST | 211836408 | 19-03-2025 12:37 | 125.4 | 4H.8042.C4../2420083 | Ad Blue Leakage Issue Call By Customer Name :-Vinod Mobile No:-9960107238 | Task Start | Kings Marque Group. . | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 1102 | adblue leakage , today SD going to change dosing module , B check pending. | Closed | Jagdeep Saini
22 | North | 211836399 | 19-03-2025 12:34 | 500 | DV8.8501.C4../2420062 | Old claim | Open | HL. Residency Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh |  | Visit Pending | Open | Ved Prakash Gupta
3 | North | 211836312 | 19-03-2025 12:17 | 82.5 | 5H.8901.../2520110 | Starting issue. Call by Customer. Name:-Sanjivan Sheth Mobile No:-9910955229 | Closed | SETH ENGINEERING WORKS | Paluck Technologies Ltd. - Ghaziabad | 2 | Dg was not start due to Mcb Connection found loose tightness the same after start the dg running ok & def level show | Closed | Kapil Solanki
13 | WEST | 211836279 | 19-03-2025 12:14 | 125.4 | 4H.8042.C4../2420329 | Error code | Closed | Pyramid Alliance LLP | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 17 | Error code 516166/0 , connect ikonnect and clear error code. | Closed | Jagdeep Saini
14 | WEST | 211836250 | 19-03-2025 12:04 | 125.4 | 4H.8042.C4../2520017 | Genset Trip | Task Start | Samarth Fabricator (Sai Fabricator) | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 36 | 1716/16 , adblue level low so top up adblue . | Closed | Jagdeep Saini
4 | North | 211836156 | 19-03-2025 11:51 | 20 | GP3.8601.../2320039 | Abnormal Sound and Error Code issue Call By Customer Name:- Mohmmad Wali No:-9128000020 | Task Start | Mohammad Wali | Vidyut Engineers - Noida | 1246 | update pending | Open | Kapil Solanki
5 | North | 211836153 | 19-03-2025 11:50 | 15 | GP3.8501.../2420718 | Starting Issue Call By Customer Name :-TeJprakash Number :-7065116762 | Closed | TSL. Electro Power Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 261 | Emergency Switch button found in pressed condition so, realeased the same then issue resolve | Closed | Kapil Solanki
6 | North | 211836143 | 19-03-2025 11:42 | 625 | DV0.8501.C4../2420014 | Electrical Problems | Closed | T. C. Health Care Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 276 | Sync value change automatic, Sync 1 change to -1 and Droop 0 change to -1 after 15 to 16 days | Open | Kapil Solanki | WW
7 | North | 211836087 | 19-03-2025 11:30 | 30 | 3H.8902.../2422343 | DG Not Start, Alarm - Under Speed | Closed | ATC Telecom Infrastructure Private Limited | R K Engineers - Bijnor | 29 | found 2b1 wire DC mcb in control penal loose so retight the same then start the DG found ok then issue resolve | Closed | Sudhir Awasthi
23 | North | 211836075 | 19-03-2025 11:27 | 25 | GP3.8702.../2420939 | Automation Issue Call By Customer Name :- Nasik .. Mobile No :- 9814048151 | Task Start | Prem Lal | MegaGen Services Pvt. Ltd. - Jalandhar | 6 | DG running issue in auto mode due to controller setting for phase was 3-phase so change the same to single phase & resolve the Issue | Closed | Ved Prakash Gupta
36 | North | 211836041 | 19-03-2025 11:23 | 20 | GP3.8601.../2421126 | Starting Issue. Call By Customer Name :- Narndra Patel Mobile No :-9839643782 | Closed | SHREE YOGANAND ASHRAM PUBLIC CHARITABLE TRUST | S.S. Enterprises - Allahabad | 22 | found starting problem due wire is loose in panel after tightness then issue was resolve | Closed | Sudhir Awasthi
4 | East | 211835938 | 19-03-2025 10:55 | 25 | GP3.8702.../2421394 | Starting/Stopping Issue | Task Start | Deputy Director | M/S JHA EQUIPMENT - IMPHAL |  | update pending | OPEN | Ujjwal Das
24 | North | 211835892 | 19-03-2025 10:50 | 500 | DV8.8501.C4../2320088 | Fuel leakage issue | Closed | SUPERCIRCLE CV COMPONENTS PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 961 | Fuel leakage issue found from Injectors fuel return line ; tightened the Joint properly ;issue resolved | Closed | Ved Prakash Gupta
25 | North | 211835848 | 19-03-2025 10:44 | 30 | 3H.8902.../2420176 | Starting/Stopping Issue | Open | Shree Jee Pvd Coatings Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 160.5 | Starting issue due to 1C2 wire found loose in Pannel on relay card; re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
6 | WEST | 211835842 | 19-03-2025 10:42 | 15 | GP3.8501.../2421217 | Starting/Stopping Issue | Closed | VISHWARAJ PETROLEUM | KALA Care Global LLP - Aurangabad | 63 | Air lock issue , remove air lock ,fuel leakage from fuel filter washer so change the benjo bolt . | Closed | Jagdeep Saini
29 | WEST | 211835825 | 19-03-2025 10:37 | 25 | GP3.8702.../2420671 | Oil Leakage issue Call By Customer Name:- Faraz Khan No:-8010870311 | Closed | Star Power Corporation | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 5 | Oil leakage from oil filter O ring so replaced it. | Closed |  | Plant
26 | North | 211835779 | 19-03-2025 10:30 | 1500 | DV2.8508.C4../2420004 & 2420006 | Inspection/Maintenance | Task Start | Guru Nanak Agro Foods Pvt. Ltd. | Gen Powers - PATIALA |  | Visit Pending | Open | Ved Prakash Gupta
15 | WEST | 211835747 | 19-03-2025 10:26 | 7.5 | D3.8305.../2400085 | Foundation issue | Closed | B. T. Kadlag Constructions Pvt. Ltd | Dhanashree Technocrats Pvt. Ltd. - Nasik | 471 | single cylinder engine , 4 AVM broken , belt also broken , replace the avm , RPM Variation . | Closed | Jagdeep Saini
8 | North | 211835741 | 19-03-2025 10:22 | 625 | DV0.8501.C4../2420015 | Electrical Problems | Cancelled | Irish Infrastructure Pvt. Ltd. | Vidyut Engineers - Noida |  | Under Cancellation | Cancelled | Kapil Solanki
31 | WEST | 211835708 | 19-03-2025 10:21 | 400 | DV8.8542.C4../2520003 | leakage issue | Task Start | Magna Automotive India Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 183.55 | Oil was leaking from the rocker cover, so the cover was refited and k sealant was used. Replaced on suspect basis due to error code 633 "water in fuel filter". | Closed
17 | WEST | 211835708 | 19-03-2025 10:21 | 400 | DV8.8542.C4../2520003 | leakage issue | Task Start | Magna Automotive India Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 189 | Dg starting issue error code 633/3 so check all the fuel line found ok no leakage found , replaced the fuel filter on suspect basis , biut problem remain same. Chcek the electric fuel feed pump pressure 930 hpa so replaced the electric feed pump assembly and taken one hour load trail , dg running ok . customer use external fuel tank so paint partical was recived from the fuelso suggest the customer clean the fuel line and use the strainer . | Closed | Jagdeep saini | Failed part require
9 | North | 211835729 | 19-03-2025 10:17 | 125.4 | 4H.8041.../2420953 | Starting issue Call by Customer Name:- Deepak Gupata Mobile No:-6393874599 | Completed | AADITRIZ TRADERS | S. R Engines Sales And Service - Gorakhpur | 17 | Found Battery voltage low, battery charger not connected connected the charger & advice to the customer not remove the connection of battery charger | Closed | Sudhir Awasthi
27 | North | 211835650 | 19-03-2025 09:56 | 400 | 6H.8439.../2420004 & 2420003 | error code and tripping Issue Call By Customer Name :- Asif Mobile No :-9808354184 | Open | The Pearl Petal. | SAAN Royal Power Solutions Private Limited - Rohtak | 56.1 | SPN/FMI-1761/16 AdBlue level low ; Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
28 | North | 211835599 | 19-03-2025 09:46 | 125.4 | 4H.8042.C4../2420694 | uria lekage issue Call By Customer Name :- Bhupendra Mobile No :- 7860629092 | Closed | Vishwasamudra Engg Pvt, Jammu | Suraj Motor Store - Jammu | 1249 | DEF Leakage found from DM due to Gasket defective so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
10 | North | 211835590 | 19-03-2025 09:43 | 58.5 | T4.8941.../2423162 | Starting Issue Call By Customer Name :- Navin .. Mobile No :- 7014415043 | Closed | Bharat Packaging | Pratap Diesels Pvt. Ltd. - Bhiwadi | 15 | SPN/FMI 97/5, 2791/18 Panel connection tight & flash Reset the alarm & flash the ECU after that issue resolve | Closed | Gourav Sharma
11 | North | 211835585 | 19-03-2025 09:43 | 250 | F6.8841.../2320019 | ECU Malfunction Alarm issue Call By Customer Name:- Narendra Nagar No:-9811818373 | Closed | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 520 | SPN/FMI 3031/14 clear the DTC & flash the file with latesh | Closed | Kapil Solanki
5 | East | 211835587 | 19-03-2025 09:43 | 100 | 4H.8042.C4../2421160 | MCD Lamp Alarm. Call by Customer. Name:- Babalu Kumar Mobile No:-7255964695 | Task Start | Thyrocare Technologies Limited | Globalline India Services Private Limited - Bhagalpur |  | low def level alarm need toup the DEF | OPEN | Prabhakar Kumar
12 | North | 211835575 | 19-03-2025 09:41 | 125.4 | 4H.8041.../2420227 | Leakage Issue | Closed | Dynamic Anodizer Aluminium Anodizing | Paluck Technologies Ltd. - Faridabad | 123 | Found Coolant leakage from termostat hose clamp loose so tightness the same , replace the same, Def level low topup the def & Fuel level over fill & Battery charging connection done , Belt was remove on his place | Closed | Kapil Solanki | Under Obs
29 | North | 211835537 | 19-03-2025 09:30 | 125.4 | 4H.8041.../2420036 | Oil Leakage issue Call By Customer Name:- Narendra No:-9671012574 | Open | NEERAJ GENERATOR WORKS | SAAN Royal Power Solutions Private Limited - Sonipat | 1731.8 | Oil lekage found from sump near drain ; DG was in breakdown so M-seal & Aratite paste done on cracks for temprary solution ; need to replace the same | Closed | Ved Prakash Gupta
13 | North | 211835507 | 19-03-2025 09:21 | 20 | GP3.1021.../2420285 | INSTANCE ID:-100776200 SITE ID:-I-UE-BCKH-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-STARTING PROBLEM NAME:-MANISH KUMAR NUMBER:-8810728385 | Open | Reliance Jio Infocomm Limited | SAM Engineering corporation - Varanasi Cantt. |  | Visit Pending | open | Sudhir Awasthi
37 | North | 211835507 | 19-03-2025 09:21 | 20 | GP3.1021.../2420285 | INSTANCE ID:-100776200 SITE ID:-I-UE-BCKH-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-STARTING PROBLEM NAME:-MANISH KUMAR NUMBER:-8810728385 | Open | Reliance Jio Infocomm Limited | SAM Engineering corporation - Varanasi Cantt. |  | Visit Pending | open | Sudhir Awasthi
14 | North | 211835515 | 19-03-2025 09:16 | 500 | DV8.8501.C4../2320021 | Starting issue Called by customer Name : Manjeet Number : 8755023232 | Task Start | SUPRA CRAFT PACKAGING (P) LTD. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 464 | found R-phase power cable burned out due vibration cut the cable ( main alternator terminal plate to MCCB ) | open | Gourav Sharma
38 | North | 211834816 | 18-03-2025 21:41 | 125.4 | 4H.8042.C4../2420734 | Trip_Genset_Low_Voltage | Open | Hotel Subhadra | Espiem Engines & Machines (P) Limited - KANPUR |  | Cancelled-Problem solve without visit | Cancelled | Sudhir Awasthi | Check the KRM data
16 | WEST | 211834812 | 18-03-2025 21:25 | 30 | 3H.8902.../2421489 | Genset Trip | Closed | Tejas Agro Product | Dhanashree Technocrats Pvt. Ltd. - Nasik | 229 | Under speed alarm , check crank sensor connection loose , tight the connection , issue resolved. | Closed | Jagdeep Saini
6 | East | 211834770 | 18-03-2025 19:36 | 15 | GP3.8501.../2422013 | Mobil Leakage issue Call by customer Name: Yuvraj yadav Number:9546260175 | Task Start | DILIP KUMAR SAHA | Globalline India Services Private Limited - Purnia | 146 | Visit pending | OPEN | Prabhakar Kumar
12 | West | 211834737 | 18-03-2025 19:06 | 40 | 3H.8951.../2520067 | Oil Leakage issue Call by customer Name:Gyanenndra ... Number:9807167269 | Closed | SCC Infrastructure Pvt Ltd | Unique Techno Services Pvt Ltd. - Bhavnagar | 314 | Oil was leaking from the breather hose so it was tightened with Teflon tape. | Closed | Amit shandilya
30 | North | 211834242 | 18-03-2025 18:03 | 30 | 3H.8902.../2420081 | Starting/Stopping Issue | Task Start | Nav Nirman Contruction Company | SAAN Royal Power Solutions Private Limited - Panipat | 58 | DG used to trip with under Voltage & under frequency alarm ; re-program the controller in last visit but issue used to come frequently ; now replace the controller & run the DG in Auto mode , Issue resolved | Closed | Ved Prakash Gupta
8 | North | 211834240 | 18-03-2025 18:03 | 7.5 | D3.8305.../2400182 | Preventive Maintenance Email By - KGD Name - Sagar Chopra | Open | Delhi Metro Rail Corporation D. M. R. C. | Vidyut Engineers - New Delhi |  | Visit Pending | open | Kapil Solanki
7 | East | 211834190 | 18-03-2025 18:02 | 15 | GP3.8501.../2422048 | Starting Issue Call By Customer Name:-Rajkishor . No:-9430829510 | Task Start | Sri Ganesh Apartment | Globalline India Services Private Limited - Patna | 1.3 | Emergency Stop switch was pressed tried to restore on telephonic communication but operator was not able to do so. | CLOSED | Prabhakar Kumar
15 | North | 211834005 | 18-03-2025 17:50 | 160 | 6H.8475.../2420025 | TRIPPING Issue Call By Customer Name : -Mustak Number : -9058614379 | Closed | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 2791 | Found Jerk load on the DG so, advice to the customer control the jerk load for Dg tripping issue | Closed | Kapil Solanki | Details required
26 | WEST | 211834014 | 18-03-2025 17:48 | 58.5 | T4.8941.../2421292 | Starting Issue Call By Customer Name :- Ram Kishore Mobile No :- 8770709015 | Task Start | Mahfuz Ahmad S/o Abdul Gani | Shree Engineering Service - Seoni | 25 | There was a problem in DG starting due to discharged battery. DG was not running for the last 15 days, controller display was on and customer had opened the battery charger wire connection. So all the work was done at site and customer was educated. | Closed
16 | North | 211834004 | 18-03-2025 17:48 | 20 | GP3.8601.../2421211 | Abnormal Sound Issue Call By Customer Name:-Pramod Sharma No:-9560374632 | Closed | ADARSH ENGINEERING WORKS | Paluck Technologies Ltd. - Faridabad | 10 | Found No any abnormal sound, but jerk load found on the DG | Closed | Kapil Solanki
17 | North | 211833979 | 18-03-2025 17:37 | 35 | 3H.8902.../2520069 | Battery not charging due to defective battery | Task Start | Western Consolidated | Deep Jyoti Electricals and Services - Bareilly | LR-2 | Battery defective replace with new Check & found Voltage not showing in the multimeter | Closed | Sudhir Awasthi
18 | North | 211833789 | 18-03-2025 17:11 | 35 | 3H.8902.../2520045 | Battery not charging due to defective | Closed | Western Consolidated | Deep Jyoti Electricals and Services - Bareilly | LR-1 | Battery defective replace with new Check & found Voltage not showing in the multimeter | Closed | Sudhir Awasthi
39 | North | 211833684 | 18-03-2025 17:04 | 125.4 | 4H.8042.C4../2420736 | Door lock issue Called by customer Name : SHYAM Number ; 8383824004 | Open | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur |  | Cancelled- SR open by Mistake | Cancelled | Sudhir Awasthi
15 | East | 211833339 | 18-03-2025 16:17 | 40 | 3H.8951.../2421631 | D Phase under voltage Issue Call By KGD Name:Alisha No :9647904206 | Open | Helping Hands Charatable Trust | K.C. Diesel Services - SILIGURI |  | Visit Pending | OPEN | Prosanjit saha
8 | East | 211833018 | 18-03-2025 15:34 | 125.4 | 4H.8041.../2420268 | Leakage Issue | Closed | I. K. U. Ventures. | Globalline India Services Private Limited - Sasaram | 9.5 | Lube oil seepage - Turbo oil drain pipe adaptor was loose after tighten issue issue resolved | CLOSED | Prabhakar Kumar
31 | North | 211832934 | 18-03-2025 15:15 | 62.5 | T4.8941.../2320243 | Starting/Stopping Issue | Closed | Arvind Hospital & Heart Center | SAAN Royal Power Solutions Private Limited - Hisar | 237 | Starting issue due to wire found loose (controller to self starter) on self starter so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta
32 | North | 211832900 | 18-03-2025 15:07 | 15 | GP3.8501.../2420018 | Fuel leakage issue Call by Customer Name - Rahul Kumar Number - 8307868902 | Closed | Keshav S/o. Rajender Kumar | SAAN Royal Power Solutions Private Limited - Hisar | 82 | Fuel leakage found between DC motor to water separator on fuel pipe due to clamp found loose on motor so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
7 | WEST | 211832899 | 18-03-2025 15:06 | 45 | 3H.8951.../2520235 | Starting/Stopping Issue | Closed | Jagannath Gangaram Pednekar Jewellers Dapoli | Mahalaxmi Diesels - Karad | 17 | Battery charger neutral connection supply not available , so give nutral supply from out side . | Closed | Jagdeep Saini
19 | North | 211832882 | 18-03-2025 14:59 | 40 | 3H.8951.../2421403 | Tripping issue Call by Customer Name - Ashish Kashyap Number - 9415005319 | Closed | Ashish Traders | S. R Engines Sales And Service - Gorakhpur | 112 | Found Under speed alarm when check and found Voltage drop after tightness the cable which comes from alternator after that issue resolve | Closed | Sudhir Awasthi
20 | North | 211832849 | 18-03-2025 14:49 | 125.4 | 4H.8042.C4../2420039 | Tripping issue Call By Customer Name :- Samunder Singh Mobile No :-7340632871 | Closed | Gohil Enterprises. | Rajdhani Diesels and Electricals - Barmer | 999 | Low def level alarm but def level 100% found in panel fuse was defective so, replace the same then issue resolve | Closed | Gourav Sharma
9 | East | 211832832 | 18-03-2025 14:41 | 40 | 3H.8951.../2421754 | Automation issue Call By Customer Name:- Vicky Kumar No:-8102230225 | Task Start | SANGITA THAKUR MEMORIAL HOSPITAL | Globalline India Services Private Limited - Muzaffarpur | 37 | automation issue due to mains sensing wire found loose after tighten issue resolved | CLOSED | Prabhakar Kumar
17 | WEST | 211832683 | 18-03-2025 14:05 | 30 | 3H.8902.../2421303 | Generator Supply Problem | Closed | Axis Bank Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 9 | MCB in off condition , so turn on the MCB. | Closed | Jagdeep Saini
21 | North | 211832699 | 18-03-2025 14:02 | 30 | 3H.8902.../2421397 | DG not starting,kindly resolve on priority-520272 | Closed | ICICI Bank Limited | S. R Engines Sales And Service - Gorakhpur | 16 | Customer side panel issue | Closed | Sudhir Awasthi
1 | North | 211832673 | 18-03-2025 13:58 | 58.5 | T4.8941.../2520332 | Starting Issue Call By Customer Name :- DIPTI PATEL Mobile No :- 9680441920 | Task Start | JEET INTERNATIONAL | Pratap Diesels Pvt. Ltd. - JAIPUR | 1.25 | Battery voltage low, Charger wire was defective replace the wire Charging in process | open | Gourav Sharma
2 | North | 211832648 | 18-03-2025 13:55 | 320 | F6.8802.../2420179 | Leakage Issue | Task Start | St. Marys Academy. | R K Engineers - Meerut | 7 | Radiator hose clamp was loose, clamp was completely freely move so, change the clamp after that issue was resolve | Closed | Sudhir Awasthi
3 | North | 211832653 | 18-03-2025 13:49 | 20 | GP3.8601.../2421221 | Automation issue Call By Customer Name:- Jagdish Kumar No:-8550946193 | Task Start | REAL BUILDING CONSTRUCTIONS | SAAN Royal Power Solutions Private Limited - Zirakpur | 41 | dg not proper working in auto mode due to under speed alarm. So check the fuel line so re-tightened the fuel pipe joints & reset the alarm , issue resolved. | Closed | Ved Prakash Gupta
9 | WEST | 211832606 | 18-03-2025 13:38 | 82.5 | 5H.8901.../2420275 | Starting/Stopping Issue | Closed | Rajendra Engineering Works. | Unique Techno Services Pvt Ltd. - Hathijan | 6.27 | Due to block load problem the engineer suggested the customer to start the motors one by one. | Closed | Amit Sandlya | Power Log Data
8 | WEST | 211832580 | 18-03-2025 13:35 | 58.5 | T4.8941.../2421301 | Inspection/Maintenance | Cancelled | ATLAS CASTALLOY LIMITED | Transcreek Engineers Pvt. Ltd. - Wadkhal |  | cancelled | Closed | Jagdeep Saini
8 | WEST | 211832488 | 18-03-2025 13:32 | 20 | GP3.8601.../2520190 | Starting Problem Call by customer Name-Abhishekh No- 8459140509 | Closed | Assured Power Co. | Mahalaxmi Diesels - Satara | 76 | no isse found in dg | Closed | Jagdeep Saini
4 | North | 211832480 | 18-03-2025 13:29 | 82.5 | 5H.8901.../2320063 | Starting/Stopping Issue | Closed | M/S J M INDUSTRIES | Pratap Diesels Pvt. Ltd. - Alwar | `54 | Battery terminal dusty clean the terminal after start the Dg running ok, but B check due (DG running low) | Closed | Gourav Sharma
1 | East | 211832425 | 18-03-2025 13:13 | 25 | GP3.8702.../2520017 | AVR Alam Issue Call By Customer Name: Wadekar Sir No:6207099133 | Open | Nagar Palika Parishad | Globalline India Services Private Limited - Bhagalpur | 3.53 | EGR fault code yesterday was not resolved today SE will visit site | OPEN | Prabhakar Kumar
12 | East | 211832425 | 18-03-2025 13:13 | 25 | GP3.8702.../2520017 | AVR Alam Issue Call By Customer Name: Wadekar Sir No:6207099133 | Open | Nagar Palika Parishad | Globalline India Services Private Limited - Bhagalpur | 3.53 | SR cancelled | CANCELLED | Prabhakar Kumar
5 | North | 211832408 | 18-03-2025 13:12 | 750 | DV2.8501.C4../2420011 | Oil leakage issue | Open | Sleek Brake Products | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 1044 | Lube oil leakage found from Rocker Cover due to bolts found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
16 | East | 211832333 | 18-03-2025 12:50 | 125.4 | 4H.8041.../2420742 | Starting Issue Call By Customer Name :-Amit Kumar Mobile No :- 7828171937 | Task Start | S. P. Goel. | Gangpur Sales and Services - Bolangir |  | Visit Pending | OPEN | Ujjwal Das
2 | East | 211832259 | 18-03-2025 12:44 | 40 | 3H.8951.../2420197 | low oil pressure alarm Issue Call By Customer Name :-Amrit Ranj Mobile No :- 6205944501 | Closed | Maa Annapurna Foods | Globalline India Services Private Limited - Patna | 138 | DG was not starting due lube oil sensor fault code so checked lube oil connector checked voltage found 5,4.5V which was ok so reconnected connector after cleaning issue resolved. | CLOSED | Prabhakar Kumar
9 | WEST | 211832041 | 18-03-2025 12:09 | 5.5 | CC1.1013.../2400117 | Starting issue Call by Service Dealer Name - Saurabh Number - 7385403851 | Closed | Mr. Navneet Kumar.. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 42 | disel ldevel low so top up disel level. | Closed | Jagdeep Saini
6 | North | 211832027 | 18-03-2025 12:08 | 125.4 | 4H.8042.C4../2420076 | Abnormal sound and alarm Issue Call By Customer Name :- Rajnish Mobile No :- 9928200881 | Open | R.B. MINERALS | Pratap Diesels Pvt. Ltd. - Sikar |  | Visit pending | open | Gourav Sharma
7 | North | 211832014 | 18-03-2025 12:04 | 82.5 | 5H.8901.../2320005 | KRM Issue And Alarm Issue Call By Customer Name :-Mahesh Kumar Sharma Mobile No:-9817876322 | Task Start | Noxon Blowers Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 179 | SPN/FMI-4375/3 ; Related to AdBlue Pump Motor ; DEF Parameters are not showing on controller ; will program the same by Today | Open | Ved Prakash Gupta | KG 640 C
8 | North | 211831972 | 18-03-2025 11:57 | 250 | F6.8841.../2420286 | ECU Alarm Issue Call By Customer Name :- Baldev Mobile No:7742405900 | Closed | Bala Ji Enterprises | Rajdhani Diesels and Electricals - Barmer | 50 | Low def level alarm & 516166/0 reset the alarm & top up the def | Closed | Gourav Sharma
9 | North | 211831919 | 18-03-2025 11:48 | 82.5 | 5H.8901.../2420577 | High Voltage Issue. Call By Customer. Name:-Anuj Kumar Mobile No.:-7417454618 | Closed | MAHARAJA AGRASEN SEWA SADAN TRUST | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 21 | Volatge set from AVR before voltage 237 now set the voltage 230 | Closed | Sudhir Awasthi
3 | East | 211831871 | 18-03-2025 11:40 | 25 | GP3.8702.../2421395 | Tripping Issue Call By Customer Name :-pushpendra singh Mobile No :- 9955361121 | Open | pushpendra singh | Globalline India Services Private Limited - Bhagalpur | 87 | Emergency Switch alarm was popuped on display so checked all wiring connnection after that issue resolved | CLOSED | Prabhakar Kumar
10 | North | 211831809 | 18-03-2025 11:32 | 45 | 3H.8951.../2420715 | AMF panel Problem Call by : Customer Name : Ravikumar Contact : 9441335332 | Task Start | Ravi kumar | SAM Engineering corporation - Varanasi Cantt. | 72 | Battery terminal loose, tightness the same | Closed | Sudhir Awasthi
11 | North | 211831734 | 18-03-2025 11:20 | 125.4 | 4H.8041.../2420729 | Starting/Stopping Issue | Task Start | devanshi construction and supplier | Excel Diesel Private Limited - Faizabad | 117 | DG trip due to over load issue, so, same educate the customer for maintain the load | Closed | Sudhir Awasthi
12 | North | 211831720 | 18-03-2025 11:20 | 57 | T4.8941.../2320010 | Starting Issue Call By Customer Name :-Rajeev Mobile No:-9718928356 | Closed | Zelleven Lifescience Pvt Ltd | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 173 | Low Electrolyte level top up the electrolyte then issue was resolve | Closed | Kapil Solanki
13 | North | 211831674 | 18-03-2025 11:12 | 30 | 3H.8902.../2420445 | Starting/Stopping Issue | Open | Deep Engines & Electricals | S. R Engines Sales And Service - LUCKNOW | 1.5 | Found Emergency switch was pressed condition so, realeased the same then issue resolve | Closed | Sudhir Awasthi
4 | East | 211831671 | 18-03-2025 11:11 | 30 | 3H.8902.../2420124 | Leakage Issue | Open | Capital University | HACS Engineering and Tech Private Limited - Hazaribagh | 42 | Found coolant leakage at thermostat outlet hose clamp loose after tightening issue resolved | CLOSED | Prabhakar Kumar
14 | North | 211831656 | 18-03-2025 11:06 | 20 | GP3.1021.../2420366 | INSTANCE ID:- 100779498 SITE ID:-I-UE-KEAT-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-KAMLESH SINGH NUMBER:-8887532259 | Open | Reliance Jio Infocomm Limited | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi
15 | North | 211831611 | 18-03-2025 10:59 | 125.4 | 4H.8042.C4../2421095 | Starting Issue Email By - OEM Name -Yash Dev Dahiya | Task Start | 1st Alarm System Association Pvt Ltd | Vidyut Engineers - New Delhi | 6.15 | Customer side panel issue, Auto command not come from the auto panel | Closed | Kapil Solanki
16 | North | 211831580 | 18-03-2025 10:55 | 160 | 6H.8475.../2420006 | Belt issue Call By Customer Name :- Shubahm Kumar Mobile No :-6306784581 | Closed | India Shine Technologies | Paluck Technologies Ltd. - Faridabad | 720 | found v-belt was loose tightnees the same then issue resolve | Closed | Kapil Solanki
17 | North | 211831419 | 18-03-2025 10:26 | 30 | 3H.8902.../2320159 | Starting/Stopping Issue | Closed | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 246 | Under speed alarm, reset the alarm after trail on load found no any issue | Closed | Kapil Solanki
18 | North | 211831358 | 18-03-2025 10:19 | 20 | GP3.8601.../2421695 | Starting Issue Call by customer Name : Narsing Prasad Number : 9305404820 | Closed | SANITARIO INDIA | Paluck Technologies Ltd. - Gurgaon | 75 | Maintenance due alarm, reset the alarm then issue resolve (A- check due) | Closed | Kapil Solanki
19 | North | 211831297 | 18-03-2025 10:01 | 58.5 | 6H.9840.../2420007 | Starting issue Call By Customer Name :- M. D Afroj Number :- 8700479015 | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 43 | Gas Pressure low & Unbalance the load, Over load same Educate the customer for balancing the load | Closed | Kapil Solanki
1 | WEST | 211831288 | 18-03-2025 09:58 | 30 | 3H.8902.../2421925 | Starting issue Call By Customer Name :- Gopinath Number :- 9078345999 | Task Start | Navayuga Engineering Company Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 257 | Error code 5838/2(inducement ) , 2791/18 check EGR connection found ok , connect ikonnect and clear error code , and flash the ECU | Closed | Jagdeep Saini
20 | North | 211831275 | 18-03-2025 09:53 | 62.5 | T4.8941.../2420028 | Tripping issue Called by customer Name : Snehil Number : 8570991111 | Task Start | Chadha Generators Private Limited | SAAN Royal Power Solutions Private Limited - Yamuna Nagar |  | Update Pending | Open | Ved Prakash Gupta
5 | East | 211831271 | 18-03-2025 09:52 | 15 | GP3.8501.../2421553 | Automation issue Call By Customer Name :- Sushil . Mobile No :-9401930091 | Task Start | D.K. ENTERPRISE | Hibreed Engineering Pvt. Ltd. - Guwahati | 16 | There was automation problem due to the main sensing wire R & B fuse was blown out so replaced by new one issue resolved | CLOSED | Ujjwal Das
21 | North | 211831219 | 18-03-2025 09:40 | 500 | DV8.8501.C4../2420071 | error code / tripping issue Call By Customer Name :- sahib singh Mobile No :-7006795040 | Task Start | Gupta Hospital And Research Center (Managed By Chuni Lal Memorial Trust) | Suraj Motor Store - kathua | 105 | Various DTC occurred regarding communication so flash ECU & both the DCU , Issue resolved | Closed | Ved Prakash Gupta
2 | WEST | 211831218 | 18-03-2025 09:39 | 30 | 3H.8902.../2420180 | Protective Lamb Alarm Problem Call by : Customer Name :Rajeshkumar Contact :7708341090 | Cancelled | L & T CONSTRUCTION. | Transcreek Engineers Pvt. Ltd. - Boisar |  | cancelled | Closed | Jagdeep Saini
17 | East | 211831175 | 18-03-2025 09:15 | 25 | GP3.8702.../2420150 | Genset oil leakage issue | Closed | BHARTI AIRTEL LIMITED | Revenus Industries Pvt. Ltd. - Central Kolkata | 192 | SE found fuel leakage from fuel pipe(Pump to filter) due to clamp was in loose condition. So, retight the clamp properly & solve the issue. | CLOSED | Prosanjit saha
22 | North | 211831167 | 18-03-2025 09:04 | 10 | GP3.8301.../2420296 | Voltage Fluctuation | Closed | BVG. India Ltd. | Megatron Engineers - Amb | 53 | DG tripping issue due to over load ; (R-14.7,Y-9.8,B-12.8) Amp ; Advised customer to keep load within KOEL Parameter | Closed | Ved Prakash Gupta
23 | WEST | 211831168 | 18-03-2025 09:04 | 500 | DV8.9313.../2420040 | Electrical Problems | Task Start | Powercare | Unique Techno Services Pvt Ltd. - Surat | 79 | SPN/FMI-523531/7(Communication Fault),523582/0(Inducement) Engineer checked the DEF line found Ok and clean the dosing modul with hot water but problem same. iKonnect is not connecting in CAN1 round connector. Checked the DCU1 & DCU2 power supply & ignition supply OK. | Closed | Amit Sandlya
23 | North | 211831154 | 18-03-2025 08:39 | 15 | GP3.8501.../2420284 | Starting/Stopping Issue | Closed | Zaidi | R K Engineers - Bijnor | 58 | Fuel rack Actuator K1 ferule connector was loose, open the connector & Properly fitted after start the DG running ok | Closed | Sudhir Awasthi
20 | East | 211729533 | 18-02-2025 12:11 | 250 | F6.8841.../2420312 | STARTING ISSUE | Task Start | M/s. Planter Hotel A. Unit Of Jigden Hotel & Resort Pvt. Ltd. | K.C. Diesel Services - SILIGURI | LR | Engine hunting with white smoke. Solution is pending from HO | OPEN | Prosanjit saha
24 | North | 211830391 | 17-03-2025 21:44 | 25 | GP3.8702.../2420075 | Heating Issue & Coolant Leakage Issue Call By Customer Name:-IRFAN . No:-9840017886 | Task Start | Irfan Mir. | Suraj Motor Store - Srinagar |  | Update Pending | Open | Ved Prakash Gupta
3 | WEST | 211830359 | 17-03-2025 20:29 | 58.5 | T4.8941.../2421518 | Battery Issue Call By Customer Name:-Jiddesh Gaikwad . No:-8879006368 | Closed | Ecoverus Green Fuels LLP. | Transcreek Engineers Pvt. Ltd. - Bhiwandi | 5 | Dg did not started for 1 month but controller was in ON condition , battery charger not connected with mains so battery discharged, educate the customer to connect the battery charger with mains. | Closed | Jagdeep Saini
18 | East | 211830273 | 17-03-2025 18:37 | 250 | F6.8842.C4../2420041 | Diesel leakage issue Call By customer Name :Abdul Rahin Number:9851012211 | Closed | N. S. R. R. K. Cold Storage Pvt. Ltd. | Revenus Industries Pvt. Ltd. - Malda | 28 | Fault code 516166 triggred so cleared DTC after that connect the IKonnect clear the code and found no leakage as per the complain. | CLOSED | Prosanjit saha
4 | WEST | 211830020 | 17-03-2025 17:59 | 160 | 6H.8475.../2420251 | Coolant Leakage Issue. Call By customer. Name:-Amit Mobile No.:-9050743066 | Task Start | COMPACT INFRA | Transcreek Engineers Pvt. Ltd. - Boisar | 22 | coolant leakage from hose pipe , tight the clip issue solved. | Closed | Jagdeep Saini
4 | WEST | 211830020 | 17-03-2025 17:59 | 160 | 6H.8475.../2420251 | Coolant Leakage Issue. Call By customer. Name:-Amit Mobile No.:-9050743066 | Cancelled | COMPACT INFRA | Transcreek Engineers Pvt. Ltd. - Boisar |  | Cancelled | Closed | Jagdeep saini
5 | WEST | 211829947 | 17-03-2025 17:43 | 200 | 6H.8438.C4../2420035 | Starting/Stopping Issue | Closed | LAHOTI PROPERTIES | KALA Care Global LLP - Latur | 53 | low adblue level so top up adblue. | Closed | Jagdeep Saini
6 | East | 211829942 | 17-03-2025 17:42 | 400 | 6H.8439.../2420006 & 2420006 | Abnormal sound and Tripping issue Call By customer Name :Tariful Islam Number :7002364264 | Closed | RuralShores Business Services Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 15 | SE visited site and found abnormal sound due to V belt loose so tighten and issue resolved | CLOSED | Ujjwal Das
25 | North | 211829725 | 17-03-2025 17:00 | 30 | 3H.8902.../2320095 | Starting/Stopping Issue | Task Start | Nuteck Paper Products | Paluck Technologies Ltd. - Faridabad | 98 | Yesterday Company was closed, Today Engineer again visit | open | Kapil Solanki
19 | East | 211829660 | 17-03-2025 16:39 | 7.5 | D3.8305.../2400155 | Starting/Stopping Issue | Closed | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - BHUBANESWAR | 288 | SE found engine cranking but not start &show alram fail to start check the fuel line then check all conector & retight all wiring conection found all r normally but issue not solved then found 2C fuse wire loose then tight the wire issue resolved. | CLOSED | Ujjwal Das
7 | East | 211829519 | 17-03-2025 16:13 | 57 | T4.8941.../2520619 | UNDER SPEED ALARM | Task Start | Powerline Industries | Hibreed Engineering Pvt. Ltd. - Nagaon | LR | LR- DG was not taking load and trip showing under speed alarm checked fuel line all ok, so checked air line and found turbo choked by plastic bag. | CLOSED | Ujjwal Das
6 | WEST | 211829304 | 17-03-2025 16:06 | 20 | GP3.8601.../2421897 | Amber Lamp On Alaram Issue & Starting Issue. Call By Customer. Name:- Shivam Mobile No.:-9028272761 | Closed | KHUSHI FABRICATORS | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 70 | Battery did not charged due to MR1 fuse found faulty so change the fuse , issue solved | Closed | Jagdeep Saini
26 | North | 211828904 | 17-03-2025 15:35 | 160 | 6H.8475.../2420231 | Coolant leakage issue Call By Customer Name :- Subhash Shukla No-9968971556 | Closed | SUNRISE ENGINEERS | Vidyut Engineers - Noida | 4.45 | Coolant leakage from radiator hose clamp was loose tightness the same then issue was resolve (Before cutoff) | Closed | Kapil Solanki
1 | East | 211828882 | 17-03-2025 15:31 | 15 | GP3.8501.../2421464 | Mobile Leakage Issue Call By Customer Name :-Ram Kumar Mobile No :- 6201204802 | Open | M.S Interprices | Globalline India Services Private Limited - Biharsharif | 226 | Visit Pending | OPEN | Prabhakar Kumar
8 | East | 211828882 | 17-03-2025 15:31 | 15 | GP3.8501.../2421464 | Mobile Leakage Issue Call By Customer Name :-Ram Kumar Mobile No :- 6201204802 | Open | M.S Interprices | Globalline India Services Private Limited - Biharsharif | 226 | Found wet staking staking at exaust side repaired turbo but same issue on removing the exhaust manifold found all there cylinder port were wet so suggested to give load on increasing load by 2.1 KW to 4 KW and operated DG for an hr found same problem | OPEN | Prabhakar Kumar | Obs After resolution
27 | North | 211828828 | 17-03-2025 15:21 | 15 | GP3.8501.../2420060 | DG not working in automode. | Closed | BHARTI AIRTEL LIMITED | Vidyut Engineers - Noida | 2 | Wrong reporting by customer- Customer not pickup the call | Closed | Kapil Solanki
28 | North | 211828788 | 17-03-2025 15:16 | 20 | GP3.8601.../2421693 | Genset Trip | Closed | Fortune Cars | Pratap Diesels Pvt. Ltd. - Bhiwadi | 143 | Unbalance & over load so, same educate the customer | Closed | Gourav Sharma | KRM SMS Confirmation
2 | East | 211828773 | 17-03-2025 15:10 | 100 | 4H.8042.C4../2420903 | Alarm Issue Call By Customer Name :- Rajib Das Mobile No :-8167206605 | Open | National Highways Infra Projects Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 67 | Visit Pending | OPEN | Ujjwal Das
9 | East | 211828773 | 17-03-2025 15:10 | 100 | 4H.8042.C4../2420903 | Alarm Issue Call By Customer Name :- Rajib Das Mobile No :-8167206605 | Open | National Highways Infra Projects Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 67 | 3031/14 and 4095/1 checked DEF concentration found ok level also OK DEF level voltage connector continuity and can restistance also found ok so flashed then issue resolved | CLOSED | Ujjwal Das
29 | North | 211828729 | 17-03-2025 15:09 | 57 | T4.8941.../2320032 | Abnormal Sound Issue Call By Customer Name -malik Number : -9810048518 | Closed | RAR AVIATION PRIVATE LIMITED | Vidyut Engineers - New Delhi | 389 | found v-belt was loose tightnees the same then issue resolve | Closed | Kapil Solanki
30 | North | 211828648 | 17-03-2025 14:53 | 250 | F6.8842.C4../2420063 | Genset Trip | Closed | Digiway Net Private Limited | Espiem Engines & Machines (P) Limited - KANPUR | 300 | Found Emegency wire was loose tightness the same then issue was resolve | Closed | Sudhir Awasthi
31 | North | 211828642 | 17-03-2025 14:48 | 750 | DV2.8501.C4../2420083 | Load Issue Call By Customer Name :- Parbhakar VCL Number :- 8130464848 | Task Start | Leisure Park Apartment Owner Association | Rajdhani Diesels and Electricals - Jodhpur | 127 | ECU malfunctioning alarm, Customer not allow the shut down | open | Gourav Sharma
41 | South Zone | 211828608 | 17-03-2025 14:40 | 20 | GP3.8601.../2421915 | customer need commissioning | Open | Lova Raju | Powerlinks Infra Tech Pvt Ltd - Khammam | NA | Visit pending | Open | Mr. MD Saleem
3 | East | 211828566 | 17-03-2025 14:39 | 20 | GP3.8601.../2420741 | Red Lamp On Alarm Issue Call By Customer Name :-Amit .. Mobile No :- 8929151618 | Open | AAROHI HOSPITALITY | Globalline India Services Private Limited - Purnia | 92 | Visit Pending | OPEN | Prabhakar Kumar
32 | North | 211828565 | 17-03-2025 14:39 | 58.5 | T4.8941.../2520226 | Starting Issue Call By Customer Name :- Bablu Mobile No :- 9958778186 | Closed | Jagdamba Generator Service | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 6 | Found Start relay 1C2 wire was loose so, tightness the same then issue resolve | Closed | Kapil Solanki
10 | East | 211828566 | 17-03-2025 14:39 | 20 | GP3.8601.../2420741 | Red Lamp On Alarm Issue Call By Customer Name :-Amit .. Mobile No :- 8929151618 | Open | AAROHI HOSPITALITY | Globalline India Services Private Limited - Purnia | 92 | Under frequency alarm was found event log but when SE visited checked for 2-3 hrs but found no issue in DG | CLOSED | Prabhakar Kumar | KRM Data
4 | East | 211828551 | 17-03-2025 14:30 | 30 | 3H.8902.../2420406 | load phase issue Email By - KGD Name -Power Generators | Closed | Samdudra shaan Bhardwaj | Hibreed Engineering Pvt. Ltd. - Guwahati |  | update pending | CLOSED | Ujjwal Das
10 | East | 211828551 | 17-03-2025 14:30 | 30 | 3H.8902.../2420406 | load phase issue Email By - KGD Name -Power Generators | Closed | Samdudra shaan Bhardwaj | Hibreed Engineering Pvt. Ltd. - Guwahati |  | update pending at Dealer end | CLOSED | Ujjwal Das
20 | East | 211828499 | 17-03-2025 14:21 | 40 | 3H.8951.../2421597 | Controller problem | Closed | MANOJ KUMAR PANDA | Gangpur Sales and Services - Nayagarh | 3 | SE found controller damaged due to customer end, then replaced a controller with paid basis | CLOSED | Ujjwal Das
33 | North | 211828511 | 17-03-2025 14:16 | 58.5 | T4.8941.../2423285 | MCD Lamp on Alarm. Call By Customer. Name:-Suresh .. Mobile No.:-9519506601 | Closed | Bharat Associates Pvt.Ltd. | Espiem Engines & Machines (P) Limited - KANPUR | 98 | Update Pending | open | Sudhir Awasthi
40 | South Zone | 211828401 | 17-03-2025 13:56 | 35 | 3H.8902.../2422322 | Inspection/Maintenance | Open | VALUE SUPPLY CHAIN SOLUTIONS | Bharath Diesel Sales and Service - Chengalpattu | NA | Visit pending | Open | Mr. NandhaGopal
39 | South Zone | 211828426 | 17-03-2025 13:55 | 40 | 3H.8951.../2420964 | Hunting Problem Call by : Customer Name :Jakatheesh Contact :9744942478 | Open | KR. Bakes | G-Care Diesels Private Limited - Malappuram | NA | Visit pending | Open | Mr. Sanjaimon S
34 | North | 211828356 | 17-03-2025 13:37 | 20 | GP3.1021.../2420275 | INSTANCE ID :-100777774 SITE ID :-I-UE-FZAD-ENB-0186 CALL BY CUSTOMER// DG ISSUE :- UNDER VOLTAGE ALARM \ SMOKE PROBLEM NAME :- JAYPRAKASH TIWARI NUMBER :-7355411582 | Closed | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Faizabad | 1493 | Fuel level low, so Dg was show the under speed alarm after fuel fill & remove the air, reset the alarm then issue resolve | Closed | Sudhir Awasthi
38 | South Zone | 211828285 | 17-03-2025 13:25 | 25 | GP3.8702.../2421443 | Starting issue Call by : Customer Name :Rajendhiran Contact :9445830050 | Open | Mohan Mutha Infrastructures Pvt Ltd | Momani Diesels - PORT BLAIR | NA | Visit pending | Open | Mr. NandhaGopal
35 | North | 211828269 | 17-03-2025 13:18 | 30 | 3H.8902.../2420661 | INSTANCE ID:-100773803 SITE ID:- UP/KSB/BS/14128 CALL BY CUSTOMER// DG ISSUE:- DG automation /exttention blow faulty NAME:- umesh kumar triparti NUMBER:-9076556117 | Task Start | ATC Telecom Infrastructure Private Limited | S.S. Enterprises - Allahabad | 1151 | Update Pending | open | Sudhir Awasthi
36 | North | 211828142 | 17-03-2025 12:51 | 15 | GP3.8501.../2422153 | Excessive Smoke | Task Start | Indian Army | Suraj Moters Stores - Leh | 106 | Customer raised complain as RPM variation but no such issue observed on site ; same communicated to customer | Closed | Ved Prakash Gupta
37 | North | 211828134 | 17-03-2025 12:46 | 15 | GP3.8501.../2420415 | Load issue | Task Start | Jai Shree Maa Filling Statation | Megatron Engineers - Pathankot | 50 | DG tripping on load due to Load cable found damaged on site so repaired the same & resolve the Issue | Closed | Ved Prakash Gupta | Event Log
38 | North | 211828120 | 17-03-2025 12:46 | 160 | 6H.8475.../2420031 | Fan Belt Issue Call By Customer Name :-Kunal Mobile No:-9318326116 | Closed | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 3429 | V-belt loose tightness the same, then issue was resolve | Closed | Kapil Solanki
21 | East | 211828087 | 17-03-2025 12:40 | 30 | 3H.8902.../2420537 | Oil leakage Issue Call By Customer Name : -abhijeet Number : -7047281146 | Closed | Panjabi Museum. | Revenus Industries Pvt. Ltd. - Malda | 12 | SE found fuel leakage from fuel tank due to customer over flow the fuel | CLOSED | Prosanjit saha
7 | WEST | 211828002 | 17-03-2025 12:25 | 5.5 | CC1.1013.../2400714 | Starting/Stopping Issue | Closed | Akshay Sawle | Dicksons Engineering Co.Pvt.Ltd. - Akola | 24 | Genset not start at auto during night but SE check but did ot found any problem . Under observation | Closed | Jagdeep Saini
39 | North | 211827996 | 17-03-2025 12:23 | 125.4 | 4H.8042.C4../2420555 | VOC - MCB Lamp & Red lamp alarm Issue Customer Name - Vinod Customer Number -9728881938 Mode- SR Generated through CDI calling. | Closed | ASHWANI COATING INDIA PVT LTD | Paluck Technologies Ltd. - Gurgaon | 17 | Low def level (47%) alarm need to be required top-up the def | Closed | Kapil Solanki
27 | WEST | 211827991 | 17-03-2025 12:22 | 20 | GP3.8601.../2421109 | Alarm Issue Call By SD Name :- Mukesh Number :- 7583889815 | Closed | Natural Sweets N. Bakes | Shree Engineering Service - KORBA | 23 | DG trip due to unbalance load(over current alarm). R Phase- 32A, Y-0A & B -0A. So educated to the customer for use the balance load. | Closed
40 | North | 211827983 | 17-03-2025 12:20 | 500 | DV8.8501.C4../2320063 | Automation issue Call By Customer Name:- Ahmed No:-9797988916 | Task Start | Himalaya Cold Chain Pvt. Ltd. | Suraj Motor Store - Srinagar | 51 | SPN/FMI-4453/8related to AdBlue Quality ; Clean the DEF Tank & supply line & top-up kirloskar DEF , reset the code & resolve the Issue | Closed | Ved Prakash Gupta
22 | East | 211827958 | 17-03-2025 12:17 | 2.8 | AP1.7003.../2400148 | overheat Issue Email By -Customer Name:- Amlan Kishore Malik | Task Start | RANJIT TENT HOUSE | Gangpur Sales and Services - BHUBANESWAR |  | Update Pending | OPEN | Ujjwal Das
24 | East | 211827958 | 17-03-2025 12:17 | 2.8 | AP1.7003.../2400148 | overheat Issue Email By -Customer Name:- Amlan Kishore Malik | Task Start | RANJIT TENT HOUSE | Gangpur Sales and Services - BHUBANESWAR |  | SR Created by customer mistake,so SR will cancel | CANCELLED | Ujjwal Das
41 | North | 211827895 | 17-03-2025 12:05 | 750 | DV2.8501.C4../2420004 | Loading issue & tripping isue Call by Customer Name - Gajendra Pal Number - 8383872040 | Closed | Skardi Greens | Paluck Technologies Ltd. - Ghaziabad | 105 | Over load Ampere (R-670, B-640, Y-635) Educate the customer maintain the load | Closed | Kapil Solanki
37 | South Zone | 211827731 | 17-03-2025 11:34 | 25 | GP3.8702.../2420200 | Staring Problem Call by :Customer Name : fusuf Contact : 9591636584 | Open | K. M. E. S. Institution of Education. | Prasad Power Engineers - Karakala | NA | Visit pending | Open | Mr. Anil Kumar H G
36 | South Zone | 211827662 | 17-03-2025 11:32 | 45 | 3H.8951.../2421504 | Starting issue Call by Customer Name - SANJEEVANI . Number - 9989449441 | Open | SANJEEVANI HOSPITAL | Powerlinks Infra Tech Pvt Ltd - Khammam | NA | Visit pending | Open | Mr. MD Saleem
41 | WEST | 211827620 | 17-03-2025 11:21 | 45 | 3H.8951.../2520260 | Diesel Lekages issue Email By KGD Name:- Poonam Shedage | Task Start | Blinkit. . | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 24 | Disesl overfilled by customer. | Closed | Jagdeep Saini
42 | North | 211827264 | 17-03-2025 11:14 | 125.4 | 4H.8041.../2320164 | Inspection/Maintenance | Closed | Medipulse Aadhar Hospital & Diagnostic | Pratap Diesels Pvt. Ltd. - Bhiwadi | 596 | Maintenance due alarm, reset the alarm then issue resolve | Closed | Gourav Sharma
25 | WEST | 211827282 | 17-03-2025 11:05 | 25 | GP3.8702.../2420202 | Engine overheat problem | Closed | Mr. Sunil Ahirwar. | Natraj Power Tech - Sagar | 616 | SD visited site for overheating problem (tripping with high temperature) but engineer took 1 hour trial but engine did not trip due to overheating - max temperature 86. The coolant reservoir was not in the tank so coolant was filled to the top between H and L. | Closed | Vijay patil
43 | North | 211826966 | 17-03-2025 10:44 | 200 | 6H.8435.../2420065 | Ab Normal Sound Issue Call By Customer Name :-Vishan Singh Mobile No:-9784326968 | Closed | Leadengage LLP | Rajdhani Diesels and Electricals - Jodhpur | 84 | Found Emergency switch was pressed condition so,(Hooter sound) realeased the same then issue resolve | Closed | Gourav Sharma
42 | WEST | 211826938 | 17-03-2025 10:39 | 200 | 6H.8435.../2420036 | Starting Issue Call By Customer Name - Sanjay Patil No -9325248529 | Task Start | Shree Ashoka Buildcon | Transcreek Engineers Pvt. Ltd. - Vasai | 38 | Air lock issue so remove air lock and fan belt found loose tight the belt. | Closed | Jagdeep Saini
44 | North | 211826836 | 17-03-2025 10:16 | 40 | 3H.8951.../2421296 | Starting issue Call by Customer Name - Vishal Diwan Number - 9235777777 | Closed | Vishal Dewan | Espiem Engines & Machines (P) Limited - KANPUR | 28 | Update Pending | open | Sudhir Awasthi
28 | WEST | 211826837 | 17-03-2025 10:16 | 25 | GP3.8702.../2422108 | LOAD ISSUE | Task Start | Lcc Projects Pvt. Ltd. . | Shree Engineering Service - Satna | 58 | 1.) Load cable burnt because customer use welding machine. 2.) Fuel level was 2% in tank. 3.) Canopy emergency alarm was showing in the controller so refited the emergency switch back side wire. | Closed
45 | North | 211826832 | 17-03-2025 10:14 | 200 | 6H.8435.../2420007 | Tripping Issue & MIL Lamp On alarm Issue. Call By customer. Name:-Ashish .. Mobile No.:-9891239461 | Closed | SUPER COMPUTECH PRIVATE LIMITED | Vidyut Engineers - Noida | 234 | DM2 alarm show SPN:516159 FMI:0 and DM1 alarm show DM1 SPN:5461 & FMI:0 and rest the alarm with the help of I-konnect tool check the DTC alarm show SPN 1761/16, 110/4, 171/4, 105/4, 5461/8 all active alarm clear and check the engine radiator coolant tank bypass hose clamp loose to coolant leakage tightness the clamp then issue was resolve | Closed | Kapil Solanki
46 | North | 211826798 | 17-03-2025 10:09 | 125.4 | 4H.8041.../2320121 | Starting Issue Email By Customer Name:-VINOD RANA | Closed | XPERT POWERGEN PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1963 | Low def level alarm top up the def reset the alarm | Closed | Kapil Solanki
5 | East | 211826791 | 17-03-2025 10:06 | 200 | 6H.8435.../2420109 | Coolant Leakage issue Call by KGD Name :-Sheetal Gupta NO :- 6299024030 | Closed | Yogeda Satsanga Society of India | HACS Engineering and Tech Private Limited - Ranchi | 26 | SE visited and found high engine temp. alarm as he found that the charging alternator Eye bolt found broken due to which belt loosen and issue raised. | CLOSED | Prabhakar Kumar
47 | North | 211826709 | 17-03-2025 09:52 | 30 | 3H.8902.../2421410 | Starting/Stopping Issue | Closed | Farha Khanum. | Gen Powers - Nabha,Patiala | 2 | Update Pending | Open | Ved Prakash Gupta
48 | North | 211826683 | 17-03-2025 09:51 | 500 | DV8.8501.C4../2320052 | Tripping issue Call By Customer Name :-Lalit Kumar Number:- 9999286305 | Closed | NATIONAL TRUST FOR THE HANDICAPPED | Vidyut Engineers - New Delhi | 10.45 | Phase reverse alarm, check & found CT Neutral was not proper fitted , Fitted the CT connection then issue was resolve | Closed | Kapil Solanki
24 | WEST | 211826682 | 17-03-2025 09:48 | 400 | DV8.8542.C4../2420141 | On load the same 400 kva run for 3-4 minutes EGT become red hot & hevy smoke | Task Start | JAKSON & COMPANY | Unique Techno Services Pvt Ltd. - Vapi | LR | 1.) Black smoke issue. 2.) At 50% load the turbo exhaust side became red hot. | Closed | Amit Sandlya
19 | East | 211727938 | 17-02-2025 19:55 | 125.4 | 4H.8042.C4../2421093 | STARTING ISSUE | Task Start | POWERLINE GREEN | Hibreed Engineering Pvt. Ltd. - Nagaon | 67 | Engine not starting due to airlock at plant. Dispatched at field | CLOSED | Ujjwal Das
49 | North | 211826105 | 16-03-2025 19:34 | 250 | F6.8841.../2420246 | There was some smoke and Genset stopped | Open | Sunflag Global Hospital. | SAAN Royal Power Solutions Private Limited - Rohtak | 86 | Self starter found burnt on site ; same sent to vendor for repairing | Open | Ved Prakash Gupta
5 | WEST | 211826101 | 16-03-2025 18:31 | 320 | F6.8802.../2420355 | Trip_Genset_Low_Voltage | Cancelled | Kutwal Foods Pvt.Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Choufulla,Daund |  | Cancelled | Closed | Jagdeep saini
50 | North | 211826094 | 16-03-2025 17:14 | 20 | GP3.8601.../2421099 | Load Issue Call By Customer Name :-Harpal Singh Mobile No:-8146843675 | Open | M/s Abdul Aziz mir | Suraj Motor Store - Srinagar | 216 | Fuel mixing with lube oil in sump ; re-visit required | Open | Ved Prakash Gupta
1 | East | 211826079 | 16-03-2025 17:12 | 58.5 | T4.8941.../2422308 | Inspection/Maintenance | Open | RASHMI CHHOTRAY | Gangpur Sales and Services - Bhubaneswar |  | Visit Pending | OPEN | Ujjwal Das
24 | East | 211826079 | 16-03-2025 17:12 | 58.5 | T4.8941.../2422308 | Inspection/Maintenance | Open | RASHMI CHHOTRAY | Gangpur Sales and Services - Bhubaneswar | 54 | SR will be cancelled ,customer required maintanance | OPEN | Ujjwal Das
51 | North | 211826091 | 16-03-2025 17:10 | 20 | GP3.8601.../2421021 | Starting Issue Call By Customer Name :-Harpal Singh Mobile No:-8146843675 | Open | M/s Abdul Aziz mir | Suraj Motor Store - Srinagar | 71 | As soon as DG comes on load ; RPM used to reduce with black smoke re-visit required | Open | Ved Prakash Gupta
6 | East | 211826074 | 16-03-2025 15:44 | 30 | 3H.8902.../2420815 | Exhaust Muffler Silencer Damaged Email By OEM Name:-Mech Agartala | Open | Dinesh Chandra R. Agrawal Infra Con Pvt. Ltd. | Johnson Techno Sales & Services - Agartala | 745 | Customer is unable to answer the call. | OPEN | Ujjwal Das
11 | East | 211826074 | 16-03-2025 15:44 | 30 | 3H.8902.../2420815 | Exhaust Muffler Silencer Damaged Email By OEM Name:-Mech Agartala | Open | Dinesh Chandra R. Agrawal Infra Con Pvt. Ltd. | Johnson Techno Sales & Services - Agartala | 745 | Customer is unable to answer the call.SR cancelled | CANCELLED | Ujjwal Das
2 | East | 211826050 | 16-03-2025 15:14 | 25 | GP3.8702.../2520097 | INSTANCE ID :-100808761 SITE ID :-OR/GN/VO/0366 CALL BY CUSTOMER// DG ISSUE :- LLOP PEOBLEM \ AUTO MAINS PROBLEM NAME :-PRAMOD CHANDR PAHADI NUMBER :-7021425620 | Task Start | ATC Telecom Infrastructure Private Limited | Gangpur Sales and Services - BHUBANESWAR | 59 | Visit Pending | OPEN | Ujjwal Das
56 | South Zone | 211825984 | 16-03-2025 13:30 | 125.4 | 4H.8042.C4../2420478 | Tripping Issue. Call By Customer Name :-Rakesh Mobile No:-7204581996 | Task Start | Sri PVR Constructions | Surya Power Services - Kolar | 445 | SPN 3031FMI 14, Falsh the dummy file, Customer using other DEF, found Adblue Contaminated. | Task Start | Mr. Anil Kumar H G
1 | North | 211826018 | 16-03-2025 13:15 | 82.5 | 5H.8901.../2420238 | Under speed alarm issue Call By Customer Name :- Bajarangraj Gujar Mobile No. :- 6376439284 | Open | Kalyaneshwar Mahadev Trust | Pratap Diesels Pvt. Ltd. - Sikar | 103.83 | Visit Pending | Open | Gourav Sharma
2 | North | 211826015 | 16-03-2025 12:53 | 250 | F6.8842.C4../2420067 | Starting/Stopping Issue | Closed | SHREE KRISHNA COLD STORAGE | Espiem Engines & Machines (P) Limited - Agra | 115 | SPN/FMI-516166/0 ; Open rocker cover & injector wire found damaged of Cylinder No. 5 so repaired the same & resolve the Issue Update Pending | Open | Sudhir Awasthi
19 | WEST | 211825994 | 16-03-2025 11:04 | 500 | DV8.9313.../2420038 | Starting/Stopping Issue | Task Start | Powercare | Unique Techno Services Pvt Ltd. - Surat | 15 | ECU parameters were not showing in controller- SD is not overriding the controller. SPN/FMI- 523576/0, Checked the DEF line and cleared DTC but engineer will visit today for another DG same error code. | OPEN | Amit Sandlya
3 | North | 211825970 | 16-03-2025 11:00 | 500 | DV8.8501.C4../2420064 | ECU Amber lamp Alarm Lock Out Alarm Call By Customer Name :-Manpal Tomar Mobile No :- 8802283075 | Closed | KAYNES TECHNOLOGY INDIA LIMITED | Paluck Technologies Ltd. - Gurgaon | 41 | SPN/FMI-1761/16 ;AdBlue level found low(10%) so top-upthe same & resolve the Issue | Closed | Kapil Solanki
4 | North | 211825967 | 16-03-2025 10:40 | 15 | GP3.8501.../2422135 | Maintenance Due Alarm Issue Call By Customer Name :- Dharmendra Kumar Mobile No :- 9055153454 | Open | AV Enterprises. | Suraj Motor Store - Jammu | 110 | Fuel leakage found from fuel guage due to bolt found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
30 | South Zone | 211825506 | 16-03-2025 10:37 | 125.4 | 4H.8042.C4../2420467 | Starting Problem Call by : Customer Name : Mohammed rafi Contact : 8008441505 | Open | Abode School | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 1.31 | Check the 2C fuse blown. so as replace the new fush after start the engine working on | Closed | Mr. MD Saleem
5 | North | 211825966 | 16-03-2025 10:33 | 125.4 | 4H.8042.C4../2420757 | Genset Trip | Open | Sanghamitra Apartment | OVN Industries Private Limited - New Delhi |  | Under Cancellation | Cancelled | Kapil Solanki
77 | South Zone | 211825964 | 16-03-2025 10:27 | 40 | 3H.8951.../2421656 | Starting/Stopping Issue | Task Start | HOTEL TRIDENT | Electro Controls - Coonoor | 2.2 | checked error code issue SPN 637 FMI2 Crank Sen flt sig Err .so remove the crank sensor checked found ok and fitted the I konnect tool and clear the error code | Task Start | Mr. Sanjaimon S
6 | North | 211825502 | 16-03-2025 10:14 | 125.4 | 4H.8041.../2420138 | Tripping Issue Call By Customer Name :- Deepak Tripathi Mobile No :-9696170582 | Open | PLATINIUM DIAGNOSTIC & IMAGING CLINIC | S. R Engines Sales And Service - Gorakhpur | 1206.45 | Visit Pending | Open | Sudhir Awasthi
7 | North | 211825953 | 16-03-2025 09:54 | 125.4 | 4H.8042.C4../2420394 | Low Fuel Level Alarm Call by customer Name:-Jitendra Number :-8004972675 | Task Start | ACME ELECTRICAL & INDUSTRIAL CO | Excel Diesel Private Limited - Faizabad | 17.56 | Visit Pending | Open | Sudhir Awasthi
7 | East | 211825948 | 16-03-2025 09:36 | 20 | GP3.8601.../2420072 | Tripping Issue Preventive Maintenance Call By Customer Name :- Ravi Kedia Mobile No :-7004596799 | Cancelled | Kedia Hardware. | HACS Engineering and Tech Private Limited - Hazaribagh | 323 | No issue inDG by mistake SR was created, so cancelled | CANCELLED | Prabhakar Kumar
57 | South Zone | 211825945 | 16-03-2025 09:31 | 20 | GP3.8601.../2420581 | Battery Problem Call by : Customer Name :Logesh Kumar Contact :9994621096 | Open | S. Meenakshi Sundaram Associates. | Bharath Diesel Sales and Service - Ashoknagar |  | visit pending | Open | Mr. NandhaGopal
18 | WEST | 211825942 | 16-03-2025 09:06 | 15 | GP3.8501.../2422090 | Starting Issue Call By Customer Name :-Prashant Mobile No:-9767729928 | Cancelled | HOTEL APSARA RESTAURANT | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune |  | cancelled | Closed | Jagdeep Saini
8 | North | 211825918 | 16-03-2025 08:40 | 250 | F6.8842.C4../2420062 | ECU Protect Alarm And Load Issue Call By Customer Name:-Mukesh Mobile No :-6367536899 | Closed | The Savoy And Holidays Resorts | Pratap Diesels Pvt. Ltd. - Alwar | 69 | SPN/FMI-157/14 & 516166/0 Related to Common Rail & ECU Malfunctioning , clean the Fuel injectors connectors & remove the DTC and resolve the Issue | Closed | Gourav Sharma
29 | South Zone | 211825917 | 16-03-2025 07:56 | 125.4 | 4H.8042.C4../2420316 | Starting Issue Call By Customer Name :- Das Sir Mobile No :- 8906492785 | Open | KNC INFRASTRUCTURES | Prasad Power Engineers - Tumkur | 377 | Observed thet there is a emergency stop button active. After clear the emergency stop button found ok. Finally started the engine observed on running condition working found ok | Closed | Mr. Anil Kumar H G
9 | North | 211825278 | 15-03-2025 21:45 | 125.4 | 4H.8041.../2320139 | Starting issue call By Customer Name:Nitin . Number:8447344441 | Closed | Vijay Lakshmi Transoltions Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 65 | Controller found faulty due to mains found shorted ; MCB & Relay found shorted in Customer'spannel ; controller need to replace | Closed | Kapil Solanki
10 | North | 211825174 | 15-03-2025 18:13 | 160 | 6H.8475.../2420233 | Oil Lekage Issue Call By Customer Name :-Gordhan Mobile No :-9602270032 | Task Start | Dr .Heera Diagnostic Centre Pvt ltd | Rajdhani Diesels and Electricals - Jodhpur | 23.43 | Oil leakage found from Oil Filter slightly when engine starts , tightened the Filters & resolve the Issue | Closed | Gourav Sharma
20 | WEST | 211825139 | 15-03-2025 17:54 | 30 | 3H.8902.../2422470 | RELAY CARD FAULTY | Task Start | ATC Telecom Infrastructure Private Limited | Unique Techno Services Pvt Ltd. - Ankleshwar | 1h,LR | DG was not starting in auto mode so remote start relay R8 was checked and found that relay coil supply is ok but relay is not on so it needs to be replaced. | OPEN | Amit Sandlya
6 | WEST | 211825108 | 15-03-2025 17:44 | 58.5 | T4.8941.../2421315 | CPH | Cancelled | ASCEND TELECOM | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC |  | Cancelled | Closed | Jagdeep saini
19 | WEST | 211825104 | 15-03-2025 17:42 | 58.5 | T4.8941.../2421607 | CPH | Cancelled | ASCEND TELECOM | Mahalaxmi Diesels - Solapur |  | cancelled | Closed | Jagdeep Saini
35 | South Zone | 211825031 | 15-03-2025 17:21 | 200 | 6H.8435.../2420049 | Voltage issue Call By Customer Name :- Purushotam . Mobile No :- 9482160721 | Open | BIMBA HOSPITALITY LLP | Surya Power Services - Mysuru | NA | Visit pending | Open | Mr. Anil Kumar H G
11 | North | 211824932 | 15-03-2025 16:51 | 25 | GP3.8702.../2320003 | Tripping issue and coolent issue Called by customer Name : Satyavir Number : 9799207333 | Open | Pawan Tanay Chem Plast Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 232 | Exhaust gases not going out through silencer while DG running on site ; checked and found expansoin ballow defective & silencer fully filled with Carbon particles ; need to replacethe same | Open | Gourav Sharma
73 | South Zone | 211824866 | 15-03-2025 16:39 | 0 | GP3.8702.../2520363 | OIL PRESSURE SENDOR FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | 100/4 high oil pressure | Task Start | Mr. NandhaGopal
72 | South Zone | 211824833 | 15-03-2025 16:28 | 0 | 6H.8475.../2520044 | ABNORMAL NOISE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | alternator side coupling tighten | Task Start | Mr. NandhaGopal
38 | WEST | 211824669 | 15-03-2025 16:01 | 125.4 | 4H.8041.../2420520 | Starting/Stopping Issue | Closed | CHOWGULE INDUSTRIES PVT LTD | Mahalaxmi Diesels - Satara | 151 | Battery was discharged due to loose connection from battery charger , charge the battery and connect the battery charger properly. | Closed | Jagdeep Saini
28 | South Zone | 211824666 | 15-03-2025 16:00 | 15 | GP3.8501.../2421458 | Electrical Problems | Task Start | RRR Developers | Sri Manjunath Technical Services - Narasaraopet | 1.2 | Electrical issue raised at the panel board because of loose connection tighten the particular defected wire (C2(10)) | Closed | Mr. MD Saleem
3 | East | 211824658 | 15-03-2025 15:58 | 40 | 3H.8951.../2421571 | Under Speed Alarm Issue & Automation Issue Call By Customer Name :- Mishra Mobile No :- 8327779009 | Open | SHYAM POWER SOLUTION | Gangpur Sales and Services - Bhubaneswar | 37 | Visit Pending | OPEN | Ujjwal Das
25 | East | 211824658 | 15-03-2025 15:58 | 40 | 3H.8951.../2421571 | Automation Issue Call By Customer Name :- Mishra Mobile No :- 8327779009 | Open | SHYAM POWER SOLUTION | Gangpur Sales and Services - Bhubaneswar | 70 | Customer side unbalance load | OPEN | Ujjwal Das
8 | East | 211824634 | 15-03-2025 15:55 | 25 | GP3.8702.../2520117 | Electrical Problems | Open | Pankaj Das | HACS Engineering and Tech Private Limited - Jamshedpur | 173 | Found neutral link got burn, and also found that customer operate DG on unbalance load. so due to unbalancing link got burn | CLOSED | Prabhakar Kumar
12 | North | 211824630 | 15-03-2025 15:54 | 30 | 3H.8902.../2421410 | AMF Panel Installation & Abnormal Sound Issue. Call By Customer. Name:-Parvej Mobile No.:-9878612352 | Cancelled | Farha Khanum. | Gen Powers - Nabha,Patiala |  | Under Cancellation | Cancelled | Ved Prakash Gupta
34 | South Zone | 211824557 | 15-03-2025 15:46 | 320 | F6.8802.../2420232 | Battery problem Call by : Customer Name Shan Contact :9961178721 | Open | Yes barath wedding centre | EMKAY MOTORS - Kollam | NA | Visit pending | Open | Mr. Sanjaimon S
13 | North | 211824539 | 15-03-2025 15:42 | 25 | GP3.8702.../2422052 | Load Issue Email By KGD Name :-Harsh Pratap Singh | Closed | Lenexis Foodworks Pvt. Ltd. | Vidyut Engineers - Noida | 72.33 | DG tripping issue due to unbalance load so same corrected by Customer's technician,no issue found in DG | Closed | Kapil Solanki
9 | East | 211824510 | 15-03-2025 15:34 | 15 | GP3.8501.../2421741 | maintanance due alarm issue called by customer name : DAIKHO number:8178931021 | Open | KISHAN RATHI | M/S JHA EQUIPMENT - IMPHAL | 59 | Visit Pending | OPEN | Ujjwal Das
12 | East | 211824510 | 15-03-2025 15:34 | 15 | GP3.8501.../2421741 | maintanance due alarm issue called by customer name : DAIKHO number:8178931021 | Open | KISHAN RATHI | M/S JHA EQUIPMENT - IMPHAL | 59 | Visit Pending | OPEN | Ujjwal Das
13 | East | 211824510 | 15-03-2025 15:34 | 15 | GP3.8501.../2421741 | maintanance due alarm issue called by customer name : DAIKHO number:8178931021 | Open | KISHAN RATHI | M/S JHA EQUIPMENT - IMPHAL | 59 | Visit Pending | OPEN | Ujjwal Das
1 | WEST | 211824469 | 15-03-2025 15:26 | 250 | F6.8841.../2420164 | Genset Trip | Completed | W.T.E. Infra Projects Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 60 | Need to top up DEF | Closed | Jagdeep Saini
2 | WEST | 211824419 | 15-03-2025 15:25 | 500 | DV8.8501.C4../2420033 | ECU ALARM ISSUE CALL BY CUSTOMER NAME :Subhash Gaikwad NO :7666900429 | Task Start | Unitherm Engineers Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | SE on site | OPEN | Jagdeep Saini
27 | South Zone | 211824411 | 15-03-2025 15:18 | 58.5 | T4.8941.../2420797 | Starting issue Call By Service Dealer Name:- Pramila No:-7722070508 | Closed | Riviera Infraprojects Private Limited | Surya Power Services - Bangalore | 51 | oil leakage from the oil hose side tighten the same. | Closed | Mr. Anil Kumar H G
26 | South Zone | 211824329 | 15-03-2025 15:02 | 125.4 | 4H.8041.../2420201 | Electrical Problems | Closed | Sri Vasista Educational Trust | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 201.5 | Attend the site along with koel AO office team then checked the active fault code found 516166/0 checked all electrical connection found ok and flash the ecu with v8 version software through ikonnect tool found same fault code active then as per koel instructions replace the ECU with new one.and checked the battery voltage found ok and checked the wiring connection found ok but ECU flaut alarm is still active so replaced the ECU found ok. Old ECU number :7923 0059 New ECU no: 7923 0055 | Closed | Mr. MD Saleem
14 | North | 211824327 | 15-03-2025 15:00 | 250 | F6.8841.../2420156 | Leakage Issue | Closed | Morvi Nandan Agro Foods | SAAN Royal Power Solutions Private Limited - Karnal | 128 | Coolant leakage found on Top side of Radiator due to clamp found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
3 | WEST | 211824320 | 15-03-2025 14:58 | 58.5 | T4.8941.../2422848 | Inspection/Maintenance | Cancelled | Jay Bhole Electrical | KALA Care Global LLP - Nanded |  | cancelled | Closed | Jagdeep Saini
40 | WEST | 211824289 | 15-03-2025 14:51 | 45 | 3H.8951.../2520235 | Battary issue | Closed | Jagannath Gangaram Pednekar Jewellers Dapoli | Mahalaxmi Diesels - Karad | 17 | Battery did not charged due to battery charger faulty , battery charger get proper supply but no output come so need to change the battery charger. | Closed | Jagdeep Saini
33 | South Zone | 211824270 | 15-03-2025 14:41 | 40 | 3H.8951.../2420946 | Starting Problem Call by : Customer Name : Patil Contact : 9945764768 | Open | Bhimanagouda Goudappagouda Patil. | KALA Care Global LLP - Bagalkote | NA | Visit pending | Open | Mr. Anil Kumar H G
15 | North | 211824254 | 15-03-2025 14:30 | 40 | 3H.8951.../2421627 | Automation Issue Call By Customer Name :- Pavan Mobile No :- 8275582755 | Cancelled | TARANPREET SINGH | Industrial Power Solutions - LUDHIANA |  | Under Cancellation | Cancelled | Ved Prakash Gupta
25 | South Zone | 211824237 | 15-03-2025 14:28 | 125.4 | 4H.8041.../2420337 | Starting Problem Call by : Customer Name : Pydinaidu Contact :8096351584 | Task Start | AMR. India Limited. | Ultimate Power Source - Ananthapuramu | 2791 | Checked battery voltage and condition found ok. Observed battery input charging voltage found not came. Observed control panel input EB supply not given by customer. So We given the EB supply 230 volts to control panel found ok. Now battery charging voltage is increasing found ok. Checked giving all necessary connections found ok. Started the engine load trail and noted all running parameters are found satisfactory. | Closed | Mr. NandhaGopal
21 | WEST | 211824232 | 15-03-2025 14:23 | 58.5 | T4.8941.../2423141 | Display issue Call by customer Name: Aman . Number :9773075742 | Closed | Asian Paints. | Unique Techno Services Pvt Ltd. - Surat | 36 | SPN/FMI- 2791/18, Flashed the ECU. | Closed | Amit Sandlya
28 | WEST | 211824232 | 15-03-2025 14:23 | 58.5 | T4.8941.../2423141 | Display issue Call by customer Name: Aman . Number :9773075742 | Closed | Asian Paints. | Unique Techno Services Pvt Ltd. - Surat | 36 | SPN/FMI- 2791/18, Flashed the ECU. | Closed | Amit Sandlya
24 | South Zone | 211824221 | 15-03-2025 14:19 | 2.8 | AP1.7003.../2400145 | Starting Problem Call by : KGD Name :PREM Contact :8075359500 | Closed | Tata Consultancy Services | G-Care Diesels Private Limited - Ernakulam | 1 | Checked carbarator faulty and replaced new one and checked fuel lines and connections found ok after work DG started working performance satisfactory. | Closed | Mr. Sanjaimon S
4 | WEST | 211824218 | 15-03-2025 14:17 | 15 | GP3.8501.../2421533 | Leakage Issue | Closed | United Petroleum. | Dicksons Engineering Co.Pvt.Ltd. - AMRAVATI | 17 | coolant leakage , coolar plate o ring not found, placed o ring , issue solved | Closed | Jagdeep Saini
23 | South Zone | 211824208 | 15-03-2025 14:17 | 82.5 | 5H.8901.../2420821 | Automation Issue Email By - KGD Name - Sandhya | Closed | Dinesh L Devnani | Surya Power Services - Bangalore | 70 | As per as customer complaint visit the site and check the dg auto sensing cables and fuses and fuses were unplugged. so plugged the fuses and resolved the issue now engine automatic issue resolved. | Closed | Mr. Anil Kumar H G
22 | South Zone | 211824179 | 15-03-2025 14:06 | 15 | GP3.8501.../2421832 | Starting Issue. Call By Service Dealer Name :- Nazher Ahmed Mobile No :-9986586467 | Task Start | SRI BALAPPA HULIGEMMA PETROLEUM | KALA Care Global LLP - Hospet | 73 | Found the DC supply switch issue due to lug damaged. so resolved the issue by replaced the lug and checked the all DG parameters found ok taken trial dg is good working condition. | Closed | Mr. Anil Kumar H G
21 | South Zone | 211824147 | 15-03-2025 14:03 | 250 | F6.8842.C4../2420070 | Engine Over Heating Issue Email By - GOEM Name - M.K.GURUMURTHY | Closed | Cadabams Diagnostics Kanakapura Road LLP | Surya Power Services - Billekahalli | 9 | As per customer complent attend the site checked the engine stutus due to over heating issue. Observation the engine installation in basement and check the bedding connection and load Cable connection ok check the engine ventilation system issue. After started the engine manual and auto running observed the heat air re circulation Inform the customer need to ventilation system required | Closed | Mr. Anil Kumar H G
20 | South Zone | 211824163 | 15-03-2025 13:56 | 125.4 | 4H.8042.C4../2420535 | Coolant Leakage Issue. Call By Customer Name :-Prvez .. Mobile No :- 8217864985 | Closed | VCHART SERVICES | Surya Power Services - Mysuru | 1115 | Coolant leakege from radiator hose pipe clamp and replace with new one radiator hose clamp | Closed | Mr. Anil Kumar H G
19 | South Zone | 211824119 | 15-03-2025 13:36 | 40 | 3H.8951.../2421115 | Starting/Stopping Issue | Closed | Mr. Ujjwal | Surya Power Services - J C Road, Bangalore | 4 | Visit the site start the engine found the LLOP Wiring loose contact and reconnected the wire start the engine check the all parameters found ok | Closed | Mr. Anil Kumar H G
16 | North | 211824086 | 15-03-2025 13:25 | 30 | 3H.8902.../2420952 | Starting issue Call by customer Name :ARRAM G Number :9897089103 | Open | INDO ENGINEERING SERVICES | Espiem Engines & Machines (P) Limited - Aligarh |  | Under Cancellation | Cancelled | Sudhir Awasthi
18 | South Zone | 211824044 | 15-03-2025 13:14 | 20 | GP3.8601.../2421990 | Automation Issue Call by customer Name :saleem CK Number :7411110099 | Closed | Saleem C. K. | G-Care Diesels Private Limited - Ernakulam | 5 | After attending the site the engine was tested in the presence of the customer representative. The engine was started and run 3 times in front of the customer But currently no complaints were found. The engine is working well | Closed | Mr. Sanjaimon S
61 | South Zone | 211824030 | 15-03-2025 13:06 | 200 | 6H.8435.../2420215 | Abnormal Sound Issue Call By Customer Name : Mithun Sir Number : 8866893588 | Closed | URC Construction (P) Ltd | Bharath Diesel Sales and Service - Chennai | 78 | V-belt found loose, so tighten the same also found SPN 516166 FMI 0, so clear the DTC and flash the ECU | Closed | Mr. NandhaGopal
48 | WEST | 211823984 | 15-03-2025 13:02 | 30 | 3H.8902.../2420072 | Inspection/Maintenance | Closed | Zetwerk Manufacturing Businesses Pvt. Ltd. | Natraj Power Tech - Guna | 1788 | SPN/FMI-157/3, Dust was in rail pressure sensor connector so cleaned it and cleared the DTC. DG running smoothly. | Closed | Vijay Patil
5 | WEST | 211823892 | 15-03-2025 12:48 | 25 | GP3.8702.../2421962 | KRM Issue Call By Customer Name: Yaswant Mahadik Number: 8600885544 | Cancelled | Veda Generator Services Kankavali | Mahalaxmi Diesels - Kankavali |  | cancelled | Closed | Jagdeep Saini
17 | South Zone | 211823744 | 15-03-2025 12:44 | 200 | 6H.8438.C4../2420073 | Radiator Water leakage issue Call by : Customer Name : Ajith kumar Contact : 9655995833 | Closed | SHANMUGAM SURESH BABU | Ultimate Power Source - Vellore | 27 | Coolant leakage from the radiator Hose pipe, then tightened all the clamps and leakage arrested, | Closed | Mr. NandhaGopal
50 | South Zone | 211823702 | 15-03-2025 12:42 | 2.8 | AP1.7003.../2400079 | Starting/Stopping Issue | Open | Tata Consultancy Services 1 | G-Care Diesels Private Limited - Ernakulam |  | Cancelled | Cancelled | Mr. Sanjaimon S
17 | North | 211823329 | 15-03-2025 12:38 | 125.4 | 4H.8042.C4../2420699 | Leakage Issue | Closed | MAHANT SHRI SATISH DASS CHARITABLE FOUNDATION | SAAN Royal Power Solutions Private Limited - Rohtak | 3.45 | Fuel leakage found from tank due to over Top-up so reduce the same & communicated to customer | Closed | Ved Prakash Gupta | PR to raise
18 | North | 211823268 | 15-03-2025 12:30 | 125.4 | 4H.8041.../2420183 | Starting Issue Call By Customer Name :Abhijit Hegde Number :9738489783 | Closed | VRL LOGISTICS LTD. | Paluck Technologies Ltd. - Gurgaon | 873.15 | SPN/FMI-1761/16 & 516166/0 ;Top-up the AdBlue & remove the code & resolve the Issue | Closed | Kapil Solanki
63 | South Zone | 211823230 | 15-03-2025 12:26 | 58.5 | T4.8941.../2422648 | Leakage Issue | Closed | KAVIN RESIDENCY | Bharath Diesel Sales and Service - Kallakurichi | 5 | the copper washer was found to be damaged.the damage washer was replaced with a new one | Closed | Mr. NandhaGopal
16 | South Zone | 211823228 | 15-03-2025 12:25 | 160 | 6H.8475.../2420289 | Abnormal noise issue Call by : Customer Name : Muthukumar Contact : 9943300916 | Closed | S.R.M. Hotel P. Ltd. | Madhu Engineering Sales & Service - Teynampet,Chennai | 78 | V-belt loose tighten the same | Closed | Mr. NandhaGopal
6 | WEST | 211823187 | 15-03-2025 12:23 | 20 | GP3.8601.../2420450 | Error Code Issue Call By Service Dealer Name - ANIL Number - 8830973072 | Closed | New Dayanand Machinery Agencies | KALA Care Global LLP - Ahmednagar | 88 | Charging alternator +ve supply fuse found burn so change the fuse issue resolved. | Closed | Jagdeep Saini
71 | South Zone | 211823217 | 15-03-2025 12:17 | 5.5 | CC1.1013.../2400616 | Starting Problem Call by : Customer Name :Gowithan Contact :8072722517 | Closed | LATHA STEEL HOUSE | Bharath Diesel Sales and Service - Pattanur | 13.3 | Not starting due to battery voltage low, customer not use dg for a long time | Closed | Mr. NandhaGopal
19 | North | 211823215 | 15-03-2025 12:17 | 30 | 3H.8902.../2421098 | Starting Issue. Call By Customer. Name:-Ranjeet Singh Mobile No.:-9810207388 | Closed | New Vishvekarma Auto Industries | Paluck Technologies Ltd. - Faridabad | 5 | Starting issue due to fuel found vacant in Tank ; Top-up the same & advised customer to maintain fuel 30% minimum,issue resolved | Closed | Kapil Solanki
20 | North | 211823138 | 15-03-2025 12:00 | 200 | 6H.8435.../2420275 | Starting issue Call by customer Name: Sanjay Varma Number : 9319722931 | Closed | RANA COLD STORAGE AND ICE FACTORY | R K Engineers - Meerut | 32 | 1761/16 , 3031/14 ,4095/0 516166/0 clear all code flash the ECU engine running on load , issue resolved | Closed | Sudhir Awasthi
15 | South Zone | 211823122 | 15-03-2025 11:55 | 40 | 3H.8951.../2420781 | Genset Trip | Closed | Serene Woods. | Laxmi Diesels - Srikakulam | 52 | Unbalanced load issue. Adviced customer to equal load distribution. | Closed | Mr. MD Saleem
14 | South Zone | 211823098 | 15-03-2025 11:43 | 250 | F6.8842.C4../2420081 | Coolant Leakage Problem Call by : Customer Name : SrinivasReddy Contact : 9396528908 Dealer Contact: 9848417701 | Closed | SSR Conventional Hall | Powerlinks Infra Tech Pvt Ltd - L B Nagar | 64 | Coolant leakage from the radiator Hose pipe, then tightened all the clamps and leakage arrested, | Closed | Mr. MD Saleem
26 | WEST | 211823064 | 15-03-2025 11:36 | 40 | 3H.8951.../2421136 | Starting/Stopping Issue | Closed | ISC Projects Pvt Ltd. | Natraj Power Tech - Dhar | 896 | Engine starting issue due to Chock fuel filter so replaced it. A Check- Closed(500H). Commissioning date-26/10/2024, A check task end date- 14/12/2024. | Closed | Vijay Patil
21 | North | 211823013 | 15-03-2025 11:26 | 125.4 | 4H.8041.../2420456 | Starting/Stopping Issue | Closed | Pin Flux Technology Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 42.1 | SPN/FMI-1761/16 & 516166/0 ;Top-up the AdBlue & remove the code & resolve the Issue | Closed | Ved Prakash Gupta
22 | North | 211823012 | 15-03-2025 11:26 | 57 | T4.8941.../2320063 | Starting/Stopping Issue | Closed | NEW GAGAN GENERATOR | Vidyut Engineers - New Delhi | 1383 | Under spped alarm occurred due to air locked found inFuel line ; check the fuel line ,no issue found , release the Air & start the DG,Issue resolved | Closed | Kapil Solanki
67 | South Zone | 211822987 | 15-03-2025 11:23 | 320 | F6.8802.../2420266 | ECU amber Alram Issue Email By - GOEM Name - S.K.POWER SYSTEMS | Completed | TRENT LIMITED | Bharath Diesel Sales and Service - Karappakkam | 151 | radiator top hose leakage checked and hose clamp move and tight the clamp | Completed | Mr. NandhaGopal
32 | South Zone | 211822977 | 15-03-2025 11:17 | 20 | GP3.8601.../2421739 | Inspection/Maintenance | Open | Innovative technologies | G-Care Diesels Private Limited - Ernakulam | NA | Visit pending | Open | Mr. Sanjaimon S
10 | East | 211822947 | 15-03-2025 11:13 | 25 | GP3.8702.../2421294 | Error Code Issue Call By Customer Name :- Rahul Saini Mobile No :-8899449833 | Open | WOW EQUIPMENT & INFRA PVT LTD | M/S JHA EQUIPMENT - IMPHAL | 47 | Visit Pending | OPEN | Ujjwal Das
13 | East | 211822947 | 15-03-2025 11:13 | 25 | GP3.8702.../2421294 | Error Code Issue Call By Customer Name :- Rahul Saini Mobile No :-8899449833 | Open | WOW EQUIPMENT & INFRA PVT LTD | M/S JHA EQUIPMENT - IMPHAL | 47 | Visit Pending | OPEN | Ujjwal Das
14 | East | 211822947 | 15-03-2025 11:13 | 25 | GP3.8702.../2421294 | Error Code Issue Call By Customer Name :- Rahul Saini Mobile No :-8899449833 | Open | WOW EQUIPMENT & INFRA PVT LTD | M/S JHA EQUIPMENT - IMPHAL | 47 | SR cancelled created by mistake | OPEN | Ujjwal Das
13 | South Zone | 211822920 | 15-03-2025 11:04 | 82.5 | 5H.8901.../2420407 | Electrical Problems | Closed | TCF. Pvt. Ltd. | G-Care Diesels Private Limited - Ernakulam | 2 | 516166/0 error code issue clear the dtc. | Closed | Mr. Sanjaimon S
23 | North | 211822914 | 15-03-2025 11:00 | 58.5 | 6H.9840.../2420007 | Starting issue Call By Customer Name :- M. D Afroj Number :- 8700479015 | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 42.49 | PNG Engine ; Gas pressure found below 300 milibar , so communicated to customer to increase gas pressure , No issue in DG | Closed | Kapil Solanki
24 | North | 211822911 | 15-03-2025 10:59 | 20 | GP3.8601.../2421061 | Power Supply Issue Call By Customer Name :- Varsha Sharma Mobile No :- 8955776137 | Open | Anand Shankar Mall. | Pratap Diesels Pvt. Ltd. - BIKANER |  | Under Cancellation | Cancelled | Gourav Sharma
25 | North | 211822893 | 15-03-2025 10:48 | 58.5 | T4.8941.../2422630 | Protector Fail and charging fail alarm Call by customer Name :Vishal Mishra Number :9877385194 | Closed | FLEET SAFETY INFOTEC | Industrial Power Solutions - LUDHIANA | 4 | Charging alternator support bolt found loose due to which belt found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
34 | WEST | 211822872 | 15-03-2025 10:44 |  | 58.5 | Sync | OPEN | NNR Biofuels Ltd | Mahalaxmi Diesels - Kolhapur | 2 | Engineer visited on site for speed biasing issue so checked the continuity from terminal to ECU connector found OK. No cross continuity. Checked the biasing voltage on terminal & same voltage found ECU connector but RPM is not changing wrt biasing voltage. Flashed the ECU but problem is same. | OPEN | Jagdeep Saini
14 | WEST | 211822847 | 15-03-2025 10:42 | 500 | DV0.8552.C4../2420004 | Starting/Stopping Issue | Closed | Oetiker India Pvt Ltd | Transcreek Engineers Pvt. Ltd. - Panvel | 81 | Leakgar from dosing module coolant pipe so tight the connector , issue solved | Closed | Jagdeep Saini
7 | WEST | 211822852 | 15-03-2025 10:39 | 250 | F6.8841.../2420145 | Starting Issue Call By Customer Name :- Amol .. Mobile No :-9970261123 | Closed | Rama Synergy Spaces Metro Life Ultima Residences. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 149 | need to top up def | Closed | Jagdeep Saini
8 | WEST | 211822796 | 15-03-2025 10:25 | 500 | DV8.8501.C4../2420280 | Genset Trip | Closed | PRAFULL DESHMUKH | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 53 | DEF level low so top up def | Closed | Jagdeep Saini
36 | WEST | 211822811 | 15-03-2025 10:24 | 250 | F6.8841.../2420331 | Error code and Starting Issue Call by customer Name :Nitin Devkule Number :8369723341 | Closed | CHEMOTEST LABORATORY | Transcreek Engineers Pvt. Ltd. - Navi Mumbai | 40 | Fuse between XDBK 1 and controller +ve supply found burn so change the fuse. | Closed | Jagdeep Saini
70 | South Zone | 211822778 | 15-03-2025 10:15 | 0 | DV8.8501.C4../2420167 | ADAPTOR REPLACMENT | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Adapter replace | Task Start | Mr. NandhaGopal
47 | WEST | 211822777 | 15-03-2025 10:15 | 58.5 | T4.8941.../2422890 | KRM issue and fuel gauge problem | Closed | Megha Mam | Unique Techno Services Pvt Ltd. - Surat | 12 | KRM was not showing current data, so re-fitted the RS485 port KRM connection and spoke to KRM team, now KRM is working. Fuel level was showing 86% but actually it was 100%, so cleaned the gauge and re-fitted it. | Closed | Amit Sandlya
26 | North | 211822775 | 15-03-2025 10:14 | 640 | F6.8803.C4../2420004 & 2420004 | LINE REJECTION | Closed | Raath International School | Pratap Diesels Pvt. Ltd. - Bhiwadi | 1(LR) | Coolant leakage found from Coolant pipe(Radiator to Dosing Module) ; replace the Coolant Pipe & top-up the coolant 10 litre ,Issue resolved | Closed | Gourav Sharma | Optiprime
76 | South Zone | 211822728 | 15-03-2025 10:00 | 40 | 3H.8951.../2421656 | LINE REJECTION | Closed | HOTEL TRIDENT | Electro Controls - Coonoor | LR | SPN 97 and FMI 5 so checked dg set wire line problem Main relay line 2A and buzzer line relay 2A1 so interchange the 2A and 2A1 wire line start the engine checked starting properly.and no error code issue | Closed | Mr. Sanjaimon S | GOEM issue
9 | WEST | 211822718 | 15-03-2025 09:56 | 82.5 | 5H.8901.../2420324 | add blue required & Preventive Maintenance Email By - KGD Name - Surekha Auti | Cancelled | Viji Carbon LLP | KALA Care Global LLP - Ahmednagar |  | cancelled | Closed | Jagdeep Saini
49 | South Zone | 211822713 | 15-03-2025 09:53 | 45 | 3H.8951.../2421504 | Stoping problem Call by : Customer Name : Ramakrishna Contact : 9989449441 | Cancelled | SANJEEVANI HOSPITAL | Powerlinks Infra Tech Pvt Ltd - Khammam |  | Cancelled | Cancelled | Mr. MD Saleem
27 | North | 211822627 | 15-03-2025 09:35 | 58.5 | T4.8941.../2422321 | Back pressure/ low oil level issue Call By Customer Name:- RAJU No:-9212005372 | Task Start | RAJU GENERATORS | OVN Industries Private Limited - New Delhi |  | Visit Pending | Open | Kapil Solanki
27 | WEST | 211822654 | 15-03-2025 09:34 | 15 | GP3.8501.../2420330 | Starting/Stopping Issue | Closed | D. D. H. Technologies India Pvt. Ltd. | Natraj Power Tech - Bhopal | 7 | DG was tripping due to emergency and MPU alarm, so emergency 4 pin connector and MPU connector were refited and cable tie was used. DG is running smoothly. | Closed | Vijay Patil
66 | South Zone | 211822618 | 15-03-2025 09:23 | 320 | F6.8802.../2420278 | Alarm Sound Problem Call by : Customer Name :Naveenkumar Contact :8825441215 | Task Start | TRENT LIMITED | Bharath Diesel Sales and Service - Karappakkam | 198 | SPN:1761/14 checked the DEF tank QLT sensor connection found connector intarnal loose connection and removed the connector and pillup the pin and re connect the connector and connect the ikonnect cleaner the pre DTC | Closed | Mr. NandhaGopal
29 | WEST | 211822617 | 15-03-2025 09:23 | 40 | 3H.8951.../2520067 | Leakage Issue | Task Start | SCC Infrastructure Pvt Ltd | Unique Techno Services Pvt Ltd. - Bhavnagar | 287 | Rocker cover bolt found broken so need to be replace. A Check Dry - close(150h) | Closed | Amit Sandlya
30 | WEST | 211822602 | 15-03-2025 08:35 | 82.5 | 5H.8901.../2420853 | Starting/Stopping Issue | Closed | Civil Aviation Department Gujarat | Unique Techno Services Pvt Ltd. - Bhavnagar | 2.46 | DG starting issue due low battery voltage. The power input to the battery charger was checked and found to be 0VAC, so power was supplied from the customer's auto panel, which charged the battery and the engine started running properly. | Closed | Amit Sandlya
28 | North | 211822596 | 15-03-2025 07:19 | 30 | 3H.8902.../2420810 | Voltage Fluctuation | Closed | Parashar Filling Station Reliance B. P. Mobility Limited. | Pratap Diesels Pvt. Ltd. - JAIPUR | 333.3 | Glass fuse found faulty of AVR Card so replace the same & resolved the Issue | Closed | Gourav Sharma
35 | WEST | 211822843 | 15/3/2025 | 30KVA | 30 | Sync | Open | NNR Biofuels Ltd | Mahalaxmi Diesels - Kolhapur | CC | Engineer visited on site for speed biasing issue so checked the continuity from terminal to ECU connector found OK. No cross continuity. Checked the biasing voltage on terminal & same voltage found ECU connector but RPM is not changing wrt biasing voltage. Flashed the ECU but problem is same. | OPEN | Jagdeep Saini
31 | WEST | 211822078 | 14-03-2025 19:04 | 25 | GP3.8702.../2420338 | Starting Issue red Lamo alam Automation issue Call By Customer Name :- Arun Katara Mobile No :- 8233959219 | Closed | Ramesh J. Raval. | Unique Techno Services Pvt Ltd. - Ahmedabad | 93 | SPN/FMI- 157/14, Connected iKonnect tool and checked PRV count and found 38, so set it to 0. Tightened all panel wire, engine running smoothly. | Closed | Amit Sandlya
12 | South Zone | 211822008 | 14-03-2025 18:03 | 200 | 6H.8435.../2420194 | Tripping issue Call by : Customer Name :Vignesh Contact : 9080484849 | Closed | HOTEL SRI ASHVIK | Madurai Electro Controls - Ramanathapuram | 89 | 1761/16, 516166/0 error code top up the def clear the code. | Closed | Mr. NandhaGopal
4 | East | 211821995 | 14-03-2025 17:46 | 7.5 | D3.8305.../2400088 | Voltage problem Call by : Customer Name : SarojBabu Contact : 7008906695 | Task Start | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - BHUBANESWAR | 48 | Visit Pending | OPEN | Ujjwal Das
11 | South Zone | 211821921 | 14-03-2025 17:20 | 20 | GP3.8601.../2420961 | Satrting Issue Cntroll Panel Call By Customer Name : Vishal Devkate Number : 9049072755 | Task Start | SREE LAKSHMI ENGINEERING WORKS | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 24 | Battery voltage drop issue. Reason for Battery charger fuse blown condition so Automatically battery voltage dropped condition while auto mode | Closed | Mr. NandhaGopal
48 | South Zone | 211821894 | 14-03-2025 17:15 | 2.8 | AP1.7003.../2400079 | Starting Problem Call by : Customer Name :Tata Consultancy Services Contact :9633313401 | Cancelled | Tata Consultancy Services 1 | G-Care Diesels Private Limited - Ernakulam |  | Cancelled | Cancelled | Mr. Sanjaimon S
69 | South Zone | 211821767 | 14-03-2025 16:05 | 0 | T4.8941.../2520169 | Air Inlight Pipe Not Ok | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the dg noticed the air intake pipe for aftercool connecting pipe not ok | Task Start | Mr. NandhaGopal
10 | South Zone | 211821691 | 14-03-2025 15:55 | 58.5 | T4.8941.../2421984 | Starting Problem Call by : Customer Name : Lobsang Contact : 9845008938 | Task Start | Sera Jey Monastery | Surya Power Services - Kushalanagara | 11 | XDBK 3 point 1C2 wire loose connection so tight,after start running ok | Closed | Mr. Anil Kumar H G
9 | South Zone | 211821679 | 14-03-2025 15:52 | 25 | GP3.8702.../2420200 | Staring Problem Call by :Customer Name : Umesh Contact : 9535842614 | Closed | K. M. E. S. Institution of Education. | Prasad Power Engineers - Karakala | 49 | Airlock issue due to low fuel level. | Closed | Mr. Anil Kumar H G
8 | South Zone | 211821623 | 14-03-2025 15:35 | 200 | 6H.8435.../2420044 | Starting/Stopping Issue | Closed | CANARA BANK | G-Care Diesels Private Limited - Calicut | 100 | DG battery not charging check the site found battery charger input ac supply not connected customer side pannel board.informed to customer for connecting cable. | Closed | Mr. Sanjaimon S
55 | South Zone | 211821583 | 14-03-2025 15:13 | 35 | 3H.8902.../2520147 | . | Task Start | KALA GENSET PVT LTD | Surya Power Services - Peenya, Bangalore | LR | Wiring harness connector lock damage, need to replace the harness | Task Start | Mr. Anil Kumar H G
54 | South Zone | 211821572 | 14-03-2025 15:07 | 25 | GP3.8702.../2420284 | Silencer Issue. Call By Customer Name :- Deeksha . Mobile No :-9449138242 | Task Start | Kiran S. J. | Prasad Power Engineers - Chikmagalore | 110 | found the abnormal sound, it's comes from expansion bellow stud broken. So we remove the clading, waiting for the further plan of action | Task Start | Mr. Anil Kumar H G
31 | South Zone | 211821504 | 14-03-2025 14:49 | 125.4 | 4H.8041.../2420387 | Umber Lamp on Alarm & Maintenance Due Alarm Issue & Red light On Alarm . Call By Customer. Name:-Pranav Patil Mobile No.:-7269825555 | Open | NATIONAL HIGHWAYS INFRA PROJECTS PRIVATE LIMITED | KALA Care Global LLP - Belagavi | NA | Visit pending | Open | Mr. Anil Kumar H G
7 | South Zone | 211821458 | 14-03-2025 14:19 | 250 | F6.8842.C4../2420101 | Starting Problem Call by : Customer Name : Ramesh Contact : 8328190432 | Task Start | Appidi Usha Kiran | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 16 | Checked the problem is self motor not rotating so replaced new self motor and started the dg set in manual and auto mode running condition is ok | Closed | Mr. MD Saleem
39 | WEST | 211821423 | 14-03-2025 14:03 | 160 | 6H.8475.../2420358 | fuel issue | Closed | M/s Purushottam Narayan Gadgil Saraf & Jewellers | Mahalaxmi Diesels - Kolhapur | 12 | Fuel level sensor was placed in a wrong direction so level was not showing properly , changed the direction and issue solved. | Closed | Jagdeep Saini
5 | East | 211821445 | 14-03-2025 14:03 | 10 | GP3.8301.../2420063 | Amber lamp Alarm issue Call By Customer Name :- Saurabh Rai Mobile No :- 7008755713 | Open | SAINIK MINING AND ALLIED SERVICES LIMITED | Gangpur Sales and Services - Jharsuguda | 58 | Visit Pending | OPEN | Ujjwal Das
10 | WEST | 211821403 | 14-03-2025 13:34 | 160 | 6H.8475.../2420148 | servicing | Cancelled | ELECTRO - DIP | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | cancelled | Closed | Jagdeep Saini
29 | North | 211821329 | 14-03-2025 13:09 | 250 | F6.8841.../2420301 | Error code | Closed | Jai Parkash Hospital | SAAN Royal Power Solutions Private Limited - Mandi | 87 | SPN/FMI- 516166/0 ; Remove the code & resolve the Issue | Closed | Ved Prakash Gupta
6 | South Zone | 211821306 | 14-03-2025 13:08 | 20 | GP3.8601.../2420470 | Starting/Stopping Issue | Task Start | M. Chinna Swamy | Surya Power Services - Bangalore | 34 | As per costomer complent engine not starting visited the site and checked the engine said control selector switch wire is loose after that connect the wire started the engine test run found ok | Closed | Mr. Anil Kumar H G
6 | East | 211821128 | 14-03-2025 12:12 | 82.5 | 5H.8901.../2420101 | Starting/Stopping Issue | Closed | Gopal Krishna Garg | K.C. Diesel Services - SILIGURI | 88 | SE found starting problem for air locked in fuel line , also found code SPN 516166, FMI 0 after that release the air in fuel line and clear the code issue resolved. | CLOSED | Prosanjit saha
26 | East | 211821128 | 14-03-2025 12:12 | 82.5 | 5H.8901.../2420101 | Starting/Stopping Issue | Closed | Gopal Krishna Garg | K.C. Diesel Services - SILIGURI | 88 | SE found starting problem for air locked in fuel line , also found code SPN 516166, FMI 0 after that release the air in fuel line and clear the code issue resolved. | CLOSED | Prosanjit saha
5 | South Zone | 211821118 | 14-03-2025 12:03 | 15 | GP3.8501.../2420053 | Voltage Problem Call by : Customer Name :Mahesh Contact :9578274149 | Completed | S. R. A. Agencies | Bharath Diesel Sales and Service - Tiruchirappalli | 2202 | Check the DG set charging alternator output voltage is high 15.35 voltage DC, and also charging alternator over heat, so removed the charging alternator but customer not a approval, so informed the customer not using on DG set | Closed | Mr. NandhaGopal
68 | South Zone | 211821095 | 14-03-2025 11:54 | 0 | T4.8941.../2520175 | DIESEL RETURN HOSE DAMAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Fuel return hose damage | Closed | Mr. NandhaGopal
78 | South Zone | 211821065 | 14-03-2025 11:48 | 25 | GP3.8702.../2420256 | INSTANCE ID:- 100771241 SITE ID:- CALL BY CUSTOMER\\ DG ISSUE:-STARTING ISSUE NAME:-POOJA MAM NUMBER:-7022114929 | Task Start | Axis Bank Ltd | Surya Power Services - Mysuru | 32 | Gear casing broken | Task Start | Mr. Anil Kumar H G
47 | South Zone | 211821079 | 14-03-2025 11:45 | 25 | GP3.8702.../2520162 | Under voltage issue | Open | NP ENTERPRISES | KALA Care Global LLP - Bagalkote |  | Cancelled | Cancelled | Mr. Anil Kumar H G
4 | South Zone | 211821075 | 14-03-2025 11:43 | 40 | 3H.8951.../2420987 | Starting/Stopping Issue | Task Start | NS INC | Surya Power Services - Kalyan Nagar | 94 | Air lock issue, fuel suction side, so remove the suction tube and again refitted. | Closed | Mr. Anil Kumar H G
65 | South Zone | 211821072 | 14-03-2025 11:42 | 25 | GP3.8702.../2420174 | Starting issue Call by customer Name:Harikrishnank . Number :9606114234 | Task Start | Mark Facility Management Service | Bharath Diesel Sales and Service - Karappakkam | 2659 | SPN-110/16 and emargency stop sw activated find the loose connection in control panel to canopy connecter and remove the connecter and clean the connecter refitted and started | Closed | Mr. NandhaGopal
3 | South Zone | 211821037 | 14-03-2025 11:29 | 82.5 | 5H.8901.../2420194 | Starting Problem Call by : Customer Name : Vinod Contact : 9676384067 | Closed | Maxvission Super Speciality Eye Hospital | Powerlinks Infra Tech Pvt Ltd - L B Nagar | 31 | Under speed alarm,so checking fuel level is ok so found fuel pipe benzo bolt copper washer damaged so replaced new washerr and then fitted diesel filter. checking leakages no found so started the engine starting and running conditions is good | Closed | Mr. MD Saleem
2 | South Zone | 211821031 | 14-03-2025 11:23 | 125.4 | 4H.8042.C4../2420533 | Load problem Call by : Customer Name : Shishir Kumar Contact : 8884517180 | Closed | Srinivasa enterprises | Surya Power Services - Peenya, Bangalore | 18 | 3031/14 error code shown in display so cleared the DTC | Closed | Mr. Anil Kumar H G
12 | WEST | 211821005 | 14-03-2025 11:22 | 15 | GP3.8501.../2421493 | Inspection/Maintenance | Cancelled | YASH PETROLEUM | Mahalaxmi Diesels - Solapur |  | cancelled | Closed | Jagdeep Saini
30 | North | 211820983 | 14-03-2025 11:10 | 30 | 3H.8902.../2421981 | AMF Panel not working,not working - 518937 | Open | ICICI Bank Limited | SAAN Royal Power Solutions Private Limited - Zirakpur | 20.05 | AMF pannel Issue ; same escalated to GOEM | Open | Ved Prakash Gupta
13 | WEST | 211820783 | 14-03-2025 10:18 | 7.5 | D3.8305.../2400085 | engine not taking load | Cancelled | B. T. Kadlag Constructions Pvt. Ltd | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | cancelled | Closed | Jagdeep Saini
37 | WEST | 211820539 | 14-03-2025 10:07 | 40 | 3H.8951.../2420140 | Automation Issue Call by customer Name :Sujeet Vale .. Numbe 7030586942 | Closed | Siddhi Wheels Pvt. Ltd. | Mahalaxmi Diesels - Solapur | 73 | Emergency button was pressed by the customer so educate the customer . | Closed | Jagdeep Saini
27 | East | 211820360 | 14-03-2025 10:07 | 25 | GP3.8702.../2520122 | DG Starting issue | Open | ATC Telecom Infrastructure Private Limited | Gangpur Sales and Services - BHUBANESWAR |  | Update Pending | CLOSED | Ujjwal Das
1 | South Zone | 211820260 | 14-03-2025 09:53 | 400 | DV8.8542.C4../2420053 | ECU Alarm Issue Call By Service Dealer Name - Rahil Number - 9035054801 | Task Start | Rodic Consultants Pvt Ltd | Prasad Power Engineers - Chikmagalore | 123 | DEF level low | Closed | Mr. Anil Kumar H G
74 | South Zone | 211820226 | 14-03-2025 09:51 | 20 | GP3.8601.../2421496 | Leakage Issue | Completed | KASDHURI JEWELLERY | Bharath Diesel Sales and Service - Pudukottai | 20 | Diesel leakage in leak off pipe return side union thread damage condition so Diesel leakage in leak off pipe , so replaced the new leak off pipe hose | Closed | Mr. NandhaGopal
31 | North | 211819580 | 13-03-2025 21:58 | 40 | 3H.8951.../2421474 | Starting/Stopping Issue | Closed | Mr. RAHIL PATLOO | Suraj Motor Store - Srinagar | 620 | SPN/FMI-637/2 ; Related to crank sensor ; no issue found in sensor but battery volatge found low (9.1 v) Mains supply disconnected to Charger so connected the same , Issue resolved after charging | Closed | Ved Prakash Gupta
32 | North | 211819228 | 13-03-2025 17:30 | 15 | GP3.8501.../2420659 | Starting Issue Call By Customer Name :-Ressan Ran Number:- 9002207788 | Open | M. H. Joinery Machines | Suraj Motor Store - Srinagar |  | Visit Pending | Open | Ved Prakash Gupta
62 | South Zone | 211819117 | 13-03-2025 16:49 | 58.5 | T4.8941.../2422121 | KRM issue Call by : Customer Name : Ganeshan Contact : 9952106615 | Open | GOOGLE COLLECTION | Bharath Diesel Sales and Service - Dharmapuri |  | Visit pending | Open | Mr. NandhaGopal
15 | WEST | 211819018 | 13-03-2025 16:27 | 500 | DV8.8501.C4../2420178 | servicing | Cancelled | ARM MANUFACTURING CORPORATION | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | cancelled | Closed | Jagdeep Saini
1 | North | 211818910 | 13-03-2025 15:59 | 320 | F6.8802.../2420325 | Trip_Genset_High_Voltage | Task Start | Ekam Elite Realtors | Megatron Engineers - Amritsar | 5 | SPN/FMI-3031/14 & 516166/0 ; clear the code & resolve the Issue | Closed | Ved Prakash Gupta
60 | South Zone | 211818852 | 13-03-2025 15:45 | 160 | 6H.8475.../2420041 | Abnormal Sound Issue. Starting Issue. Call By Service Dealer Name :- Indumati Mobile No :-8925873034 | Closed | NOVITIUM LABS PVT LTD | Bharath Diesel Sales and Service - Chennai | 108 | V-belt found loose, so tighten the same | Closed | Mr. NandhaGopal
44 | WEST | 211818743 | 13-03-2025 15:22 | 5.5 | CC1.1013.../2500030 | under speed alarm | Closed | powertek Ideas (P) Ltd | Mahalaxmi Diesels - Dharashiv | 1 | Dg not start due to airlock issue remove air lock issue solved. | Closed | Jagdeep Saini
2 | North | 211818756 | 13-03-2025 15:17 | 58.5 | T4.8941.../2520498 | CONTROLAR PROBLEM | Task Start | PIYANO SOUND INDUSTRIES | Paluck Technologies Ltd. - Ghaziabad | 0.1(LR) | Controller found fault y (not giving output from pin no. 3)so replace the same & resolve the Issue | Closed | Kapil Solanki
11 | East | 211818675 | 13-03-2025 14:59 | 30 | 3H.8902.../2420406 | Power supply issue Called by customer Name: Samdudra Number : 8638978401 | cancelled | Samdudra shaan Bhardwaj | Hibreed Engineering Pvt. Ltd. - Guwahati |  | Postponed Visit - Work load, SR cancelled | CANCELLED | Ujjwal Das
3 | North | 211818664 | 13-03-2025 14:54 | 125.4 | 4H.8041.../2320120 | Genset Trip | Open | Sundeep Electrodes Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 340 | Starting Issue due to Air locked found in Fuel line ; NRV found faulty so replace the same & resolve the Issue | Closed | Kapil Solanki
64 | South Zone | 211818654 | 13-03-2025 14:49 | 250 | F6.8841.../2420358 | Starting Issue Call By Service Dealer Name :- Kanimori Mobile No :- 7722070833 | Task Start | Prakash Silks & Sarees Pvt. Ltd. | Bharath Diesel Sales and Service - Kanchipuram | 44 | Battery low voltage 2vdc battery charger out put wire 2A and 1c1 wiring connector ferule lug as loose condition | Closed | Mr. NandhaGopal
4 | North | 211818572 | 13-03-2025 14:25 | 125.4 | 4H.8041.../2420488 | Genset Trip | Open | Pioneer Steels | SAAN Royal Power Solutions Private Limited - Rohtak | 135 | DG running fine on site without load but tripped on load due to found unbalance so same communicated to customer | Closed | Ved Prakash Gupta
5 | North | 211818553 | 13-03-2025 14:21 | 40 | 3H.8951.../2520323 | KRM Issue Email By-OEM Name-Rohit Gupta | Open | TARUN DUA | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Visit Pending | Open | Gourav Sharma
18 | WEST | 211818514 | 13-03-2025 14:02 | 30 | 3H.8902.../2421573 | Red alarm ,under frequency and protect lamp issue Call By Customer Name:- Akshay Kakde No:-9822302005 | Cancelled | Royal Construction & Developer | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | cancelled | Closed | Jagdeep Saini
6 | North | 211818476 | 13-03-2025 13:50 | 125.4 | 4H.8042.C4../2420692 | Leakage Issue | Task Start | Bharat Tech and Engineering | Suraj Moters Stores - Leh |  | Visit Pending | Open | Ved Prakash Gupta
7 | North | 211818445 | 13-03-2025 13:45 | 750 | DV2.8501.C4../2420048 | Tripping issue Call By Customer Name :- Anand Mobile No :-9911311755 | Completed | St. Mark's Sr. Sec. Public School, | OVN Industries Private Limited - New Delhi | 938.2 | SR Opened for service ; completed | Closed | Kapil Solanki
22 | WEST | 211818446 | 13-03-2025 13:45 | 30 | 3H.8902.../2421292 | dg set not start in auto | Cancelled | Shree Sai Enterprises. | Mahalaxmi Diesels - Goa |  | cancelled | Closed | Jagdeep Saini
12 | East | 211818336 | 13-03-2025 13:22 | 40 | 3H.8951.../2420118 | Voltage Fluctuation | Task Start | Ravi Ranjan Singh. | Globalline India Services Private Limited - Gaya | 743 | SE visited and found voltage fluctuation due to load unbalancing no issue in DG R-49A, Y- 20A, B- 2 A | CLOSED | Prabhakar Kumar
20 | WEST | 211818337 | 13-03-2025 13:22 | 250 | F6.8841.../2420283 | :DG Not working | Cancelled | RELIANCE PROJECTS & PROPERTY MANAGEMENT SERVICES LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Choufulla,Daund |  | cancelled | Closed | Jagdeep Saini
9 | East | 211818284 | 13-03-2025 13:15 | 20 | GP3.8601.../2420200 | Starting Issue. Call By Customer Name :- Manoj Kumar Shahu Mobile No :-9337393659 | Closed | KALPANA RIVERVIEW B BLOCK WELFARE SOCIETY | Gangpur Sales and Services - BHUBANESWAR | 17 | SE found engine not starting due to emergency switch pressed | CLOSED | Ujjwal Das
28 | East | 211818284 | 13-03-2025 13:15 | 20 | GP3.8601.../2420200 | Starting Issue. Call By Customer Name :- Manoj Kumar Shahu Mobile No :-9337393659 | Closed | KALPANA RIVERVIEW B BLOCK WELFARE SOCIETY | Gangpur Sales and Services - BHUBANESWAR | 17 | SE found engine not starting due to emergency switch pressed | CLOSED | Ujjwal Das
53 | South Zone | 211818285 | 13-03-2025 13:15 | 160 | 6H.8475.../2420183 | Adblue leakage issue Call by customer Name:Pandurang Number :9480934157 | Task Start | Channa Basaweshwar Public School. | KALA Care Global LLP - Kalaburagi | 115 | Adblue leakage from suppy pipe, need to replace the pipe | Task Start | Mr. Anil Kumar H G
8 | North | 211818271 | 13-03-2025 13:10 | 320 | F6.8802.../2420060 | STARTING ISSUE CALL BY CUSTOMER NAME-Ashmeet NUMBER-9958622967 | Open | Rudra Construction | Gen Powers - Nabha,Patiala |  | Visit Pending | Open | Ved Prakash Gupta
46 | WEST | 211818259 | 13-03-2025 12:51 | 125.4 | 4H.8042.C4../2420133 | Air Leakage from the Throttle Valve Gasket | Task Start | JAKSON & COMPANY | Unique Techno Services Pvt Ltd. - Vapi | LR | Air leakage from CAC pipe gasket so replaced it. | Closed | Amit Sandlya
59 | South Zone | 211818096 | 13-03-2025 12:26 | 125.4 | 4H.8042.C4../2420823 | Lamp On Alarm & KRM Not Working Call by : Dealer Dealer No :9677095740 Customer name :Mr. Anbu Customer number :9940611204 | Open | Kinugawa Rubber India Private Limited | Bharath Diesel Sales and Service - Chennai | 15 | SPN 516166 FMI 0, clear the DTC | Closed | Mr. NandhaGopal
9 | North | 211818046 | 13-03-2025 12:23 | 125.4 | 4H.8042.C4../2520106 | Abnormal Sound Issue Call By Service Dealer Name:- Deepak Sharma No:-9811664261 | Task Start | Atlas Power & Equipments | SAAN Royal Power Solutions Private Limited - Sonipat | 78.32 | SPN/FMI-1761/16 AdBlue level low , Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
10 | North | 211818030 | 13-03-2025 12:16 | 125.4 | 4H.8042.C4../2420951 | KRM Issue Call By Customer Name :-Vijay Kumar Sharma Mobile No:-9718211355 | Closed | AVON COATINGS | Paluck Technologies Ltd. - Faridabad | 24.26 | KRM parameter was not showing correct parameter on App so corrected the same & resolve the Issue | Closed | Kapil Solanki
11 | North | 211818001 | 13-03-2025 12:11 | 125.4 | 4H.8042.C4../2420571 | KRM Issue Call By Customer Name :-Vijay Kumar Sharma Mobile No:-9718211355 | Closed | AVON COATINGS | Paluck Technologies Ltd. - Faridabad | 14 | KRM parameter was not showing correct parameter on App so corrected the same & resolve the Issue | Closed | Kapil Solanki
13 | East | 211817979 | 13-03-2025 12:07 | 10 | GP3.8301.../2420161 | Electrical Problems | Task Start | Siddharth Kumar | HACS Engineering and Tech Private Limited - Dhanbad |  | Update Pending | OPEN | Prabhakar Kumar
56 | South Zone | 211817846 | 13-03-2025 11:39 | 160 | 6H.8475.../2420391 | Oil Leakage Problem Call by : Customer Name :Rajesh Khanna Contact :9787884041 Dealer Contact No:9790033065 | Task Start | KPT Blue Metal KPT RMC | Bharath Diesel Sales and Service - Arni | 103 | INSPECTED THE SITE AND NOTICED THE BELT GOT FAILURE DUE TO COOLENT LEAKAGE OVER THE BELT SO THAT THE BELT GOT FAILURE SO THAT REPLACED THE NEW BELT AND ISSUE RESOLVED | Closed | Mr. NandhaGopal
12 | North | 211817814 | 13-03-2025 11:31 | 125.4 | 4H.8042.C4../2420343 | Genset Trip | Closed | ALLAHABAD CONSTRUCTION & DEVELOPERS ASSOCIATES | S.S. Enterprises - Allahabad | 30 | Fuel Level sensor found defective ; Check the supply to guage found ok ; flash the controller but issue remains same so replace the same & resolve the issue | Closed | Sudhir Awasthi
58 | South Zone | 211817749 | 13-03-2025 11:22 | 500 | DV8.8501.C4../2320070 | Battery Voltage Low Alarm Issue. Call By Customer. Name:-Karthik . Mobile No.;-9148660589 | Open | Unitherm Engineers Limited | Bharath Diesel Sales and Service - Chennai | 167 | Battery neg wire wire loose, so tighten the same | Closed | Mr. NandhaGopal
13 | North | 211817699 | 13-03-2025 11:08 | 125.4 | 4H.8042.C4../2420365 | Coolant Leakage issue Call By Service Dealer . Name:-Amarjit Mobile No.:- 9044754132 | Closed | MAHAGAURI CERMICS | Espiem Engines & Machines (P) Limited - Aligarh | 136 | Coolant Leakage from Radiator hose bottom side du to clamp found loose so tightened the same & resolve the Issue | Closed | Sudhir Awasthi
14 | North | 211817681 | 13-03-2025 11:06 | 160 | 6H.8475.../2420029 | Leakage Issue | Open | Sahyog Engineering Industries | SAAN Royal Power Solutions Private Limited - Rohtak | 216 | Coolant leakage found from recovery bottle due to cap found in open condition on site,corrected the same,top-up coolant in radiator & check belt condition , found ok | Closed | Ved Prakash Gupta
15 | North | 211817694 | 13-03-2025 11:04 | 82.5 | 5H.8901.../2320024 | starting problem Call By Customer Name :- harshwardhan Number :- 8700373053 | Closed | FLY BY NIGHT | Paluck Technologies Ltd. - Faridabad | 403 | engine stopped with emergency alarm ; re-connected all the connections & resolve the Issue | Closed | Kapil Solanki
23 | WEST | 211817641 | 13-03-2025 10:54 | 58.5 | T4.8941.../2421349 | Fuel Consumption Issue & Preventive Maintenance Call by customer Name : Aniket Sir Number : 9082650709 | Cancelled | Sttar Technologies | Transcreek Engineers Pvt. Ltd. - Panvel |  | cancelled | Closed | Jagdeep Saini
14 | East | 211817613 | 13-03-2025 10:52 | 15 | GP3.8501.../2420999 | Starting/Stopping Issue | Completed | LALL CONSTRUCTION INDIA LTD | Globalline India Services Private Limited - Motihari |  | DG not starting due to sweep stuck alarm so checked and reconnected the FIP actuator connector after that started DG started normaly and checked for 2-3 time found no issue. | CLOSED | Prabhakar Kumar
25 | WEST | 211817562 | 13-03-2025 10:42 | 58.5 | T4.8941.../2421607 | INSTANCE ID:- 100777022 SITE ID:-0018873 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-Anand Bhangire NUMBER:-9834828264 | Cancelled | ASCEND TELECOM | Mahalaxmi Diesels - Solapur |  | cancelled | Closed | Jagdeep Saini
16 | North | 211817547 | 13-03-2025 10:38 | 82.5 | 5H.8901.../2320021 | Oil Leakage issue Call By Customer. Name:-Aprana Mobile No.:- 8700480471 | Closed | CRMK Select | Vidyut Engineers - Noida | 231.31 | Oil Leakage found from sump so tightened all the sump bolts & re-start the DG , Oil leakage issue resolved | Closed | Kapil Solanki
17 | North | 211817456 | 13-03-2025 10:21 | 25 | GP3.8702.../2520255 | Load Tripping Issue Email By-KGD Name-Rajeev Mathur | Open | OSS. Construction Pvt. Ltd. | Excel Diesel Private Limited - Faizabad |  | Visit Pending | Open | Sudhir Awasthi
18 | North | 211817439 | 13-03-2025 10:16 | 125.4 | 4H.8042.C4../2420694 | Under Speed Alaram Issue Call by customer Name :Bhupendra Thakur Number:7860629092 | Closed | Vishwasamudra Engg Pvt, Jammu | Suraj Motor Store - Jammu | 1179 | SPN/FMI-4095/1 ; Related to DEF so clean the DEF line & remove the code,issue resolved | Closed | Ved Prakash Gupta
19 | North | 211817376 | 13-03-2025 10:05 | 625 | DV0.8501.C4../2420079 | Tripping Issue Call By Customer Name :- Devendra Saini Mobile No :- 8053353744 | Task Start | HPL ELECTRIC & POWER LTD | SAAN Royal Power Solutions Private Limited - Sonipat | 229.2 | SPN/FMI-5786/3 & 3469/3 ; Check low pressure pipes of Fuel line found ok,check the continuity to FIP & common rail connector,found ok,remove the code & run the DG,issue resolved | Closed | Ved Prakash Gupta
20 | North | 211817370 | 13-03-2025 10:00 | 20 | GP3.8601.../2420034 | Ideal gear issue | Task Start | Mata Mohandai Oswal Public Senior Secondary School | Gen Powers - PATIALA | 138.48 | Update Pending | Open | Ved Prakash Gupta
32 | WEST | 211817321 | 13-03-2025 09:53 | 125.4 | 4H.8042.C4../2420589 | Starting/Stopping Issue | Closed | KP. Energy | Unique Techno Services Pvt Ltd. - Gandhidham | 743 | SPN/FMI-520528/31(Inducement Related error code), Checked the DEF line for any chock up found OK. Cleared the DTC . | Closed | Amit Sandlya
75 | South Zone | 211817282 | 13-03-2025 09:37 | 20 | GP3.8601.../2422035 | Starting Problem Call by : Dealer Customer name :Raj Sekar Customer number :9443629074 Dealer No:9790033065 | Task Start | Rajkumar Contractor, | Bharath Diesel Sales and Service - Thiruvannamalai | 7 | engine lop switch alarm indicated, lop switch wiring harness loose connection then properly tighten | Closed | Mr. NandhaGopal
45 | WEST | 211817248 | 13-03-2025 09:27 | 58.5 | T4.8941.../2422101 | Starting/Stopping Issue | Closed | Hotal Ramayana | KALA Care Global LLP - Parbhani | 50 | R phase fuse burn change the fuse , so change the fuse , issue solved. | Closed | Jagdeep Saini
21 | North | 211816573 | 2025-12-03 23:33 | 320 | F6.8802.../2420279 | Electrical Problems | Open | Orchid Hospitality Services Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 724 | DG tripped in night due to running on over-load so same communicated to customer;No issue found in DG | Closed | Ved Prakash Gupta
22 | North | 211816465 | 2025-12-03 20:17 | 57 | T4.8941.../2320167 | Oil Leakage Issue Call By Customer Name:-Vijay Kumar . No:-8178326207 | Closed | WITTY BRAINS SOFTWARE TECHNOLOGIES (P) LTD. | Vidyut Engineers - Noida | 171.12 | Fuel leakage found from Injectors return line so tightened the bolt & resolved the Issue Update Pending | Open | Kapil Solanki
23 | North | 211816418 | 2025-12-03 19:01 | 15 | GP3.8501.../2420379 | Dg issue | Open | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Under Cancellation-work will be done under KOEL AMC | Cancelled | Kapil Solanki
24 | North | 211816415 | 2025-12-03 19:00 | 15 | GP3.8501.../2420006 | Dg issue | Open | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Under Cancellation-work will be done under KOEL AMC | Cancelled | Kapil Solanki
15 | East | 211816332 | 2025-12-03 18:24 | 15 | GP3.8501.../2422111 | Trip_Genset_Low_Voltage | Open | CIVILEC | Globalline India Services Private Limited - Arrah |  | SR opened by mistake, so cancelled | CANCELLED | Prabhakar Kumar
46 | South Zone | 211816085 | 2025-12-03 17:37 | 250 | F6.8842.C4../2420022 | Automatic start not working | Task Start | Adishwar Auto Diagnostics Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | Cancelled | Cancelled | Mr. MD Saleem
25 | North | 211815375 | 2025-12-03 16:51 | 25 | GP3.8702.../2421452 | Oil sensor faulty | Closed | SINGHLA SCIENTIFIC INDUSTRIES | SAAN Royal Power Solutions Private Limited - Ambala | 1(LR) | Reached at site for CC & found low oil pressure alarm,check the voltage supply to sensor found ok,oil level also found ok on controller,remove the oil filter & found coolant mixed with oil,same communicated to GOEM | Open | Ved Prakash Gupta
16 | WEST | 211815355 | 2025-12-03 16:47 | 25 | GP3.8702.../2421466 | Tripping issue Call by customer Name:Tejas Number :9726976708 | Open | Blue Corporate House | Unique Techno Services Pvt Ltd. - Surat | NA | Customer side issue but he is not agree so today SE on site. | Closed
33 | WEST | 211815355 | 2025-12-03 16:47 | 25 | GP3.8702.../2421466 | Tripping issue Call by customer Name:Tejas Number :9726976708 | Closed | Blue Corporate House | Unique Techno Services Pvt Ltd. - Surat | 33 | SE visited on site and apart from unbalanced load, no other problems were found.R Phage Current- 12A , Y-0A and B- 18.2A. | Closed | Amit Sandlya
45 | South Zone | 211815151 | 2025-12-03 16:05 | 15 | GP3.8501.../2421754 | maintenance due Alarm issue Call By Customer Name :- RAISON RAISON No:-9988707666 | Cancelled | JUNGLE BOOK DAIRY FARM | EMKAY MOTORS - Pathanamthitta |  | Cancelled | Cancelled | Mr. Sanjaimon S
1 | East | 211815000 | 2025-12-03 15:51 | 30 | 3H.8902.../2420087 | Starting/Stopping Issue | Task Start | Indian Army | Green Powerline - Tezpur | 242 | SE visited and found battery charging failure alarm so checked charging altenator voltage found Ok (13.91) so checked fuse its continuity ok but found minute loose connection after fixing issue resolved | CLOSED | Ujjwal Das
26 | South Zone | 211815026 | 2025-12-03 15:49 | 30 | 3H.8902.../2421919 | Power supply Issue Call By Customer Name :- Robin .. Mobile No :- 9019907550 | Task Start | Gokul Power Services | KALA Care Global LLP - Belagavi | NA | MCB wire loose. Wire comes from mains | Task Start | Mr. Anil Kumar H G
9 | South Zone | 211814908 | 2025-12-03 15:29 | 20 | GP3.8601.../2420118 | Starting/Stopping Issue | Task Start | Riya Electricals | Electro Controls - Kattappana | 38 | Charging Alternator fuse damaged replace it | Closed | Mr. Sanjaimon S
17 | WEST | 211814897 | 2025-12-03 15:27 | 500 | DV8.9313.../2420040 | Starting/Stopping Issue | Open | Powercare | Unique Techno Services Pvt Ltd. - Surat |  | Given for cancellation | Closed
26 | North | 211814857 | 2025-12-03 15:14 | 125.4 | 4H.8042.C4../2421132 | Red Lamp On alarm Issue. Call By Customer. Name:-Vinay Mobile No.:-9415273465 | Cancelled | Mr. Anmol Gupta | Deep Jyoti Electricals and Services - Shahjahanpur |  | Under Cancellation | Cancelled | Sudhir Awasthi
27 | North | 211814823 | 2025-12-03 15:06 | 125.4 | 4H.8041.../2420478 | Starting/Stopping Issue | Closed | The Shahnai Resort. | Pratap Diesels Pvt. Ltd. - Alwar | 116 | SPN/FMI-516166/0 ECU Malfunction alarm occurred ;reset the same & resolve the Issue | Closed | Gourav Sharma
28 | North | 211814770 | 2025-12-03 14:54 | 82.5 | 5H.8901.../2320070 | Display Issue. Call By Customer. Name:-Dipak Singh Mobile No.:-8929895150 | Closed | Gen Power Generator | Vidyut Engineers - New Delhi | 41 | Controller Programming done due to DEF temp. & level alarm occurred | Closed | Kapil Solanki
2 | East | 211814771 | 2025-12-03 14:53 | 30 | 3H.8902.../2421637 | MIL LAMP ON ALARM ISSUE Email By-KGD Name-Power Generators | Open | Shree Balaji Minerals | M T Enterprises - Bomdila | 269 | Update pending at dealer end | OPEN | Ujjwal Das
16 | East | 211814771 | 2025-12-03 14:53 | 30 | 3H.8902.../2421637 | MIL LAMP ON ALARM ISSUE Email By-KGD Name-Power Generators | Open | Shree Balaji Minerals | M T Enterprises - Bomdila | 269 | Update pending at dealer end | OPEN | Ujjwal Das
11 | East | 211814771 | 2025-12-03 14:53 | 30 | 3H.8902.../2421637 | MIL LAMP ON ALARM ISSUE Email By-KGD Name-Power Generators | Open | Shree Balaji Minerals | M T Enterprises - Bomdila | 302 | EGR valve replaced-Customer load is below 20% and maxi. time customer operate DG on unbalance load this was first time so replaced on goodwill basis. | OPEN | Ujjwal Das
29 | North | 211814761 | 2025-12-03 14:52 | 125.4 | 4H.8041.../2320198 | Amber Lamp Alarm Lod Issue And Tripping Issue Call By Customer Name :- Mobile No :- | Closed | BKDJ Packagings Pvt. LTD | Paluck Technologies Ltd. - Gurgaon | 487.34 | Maintenance alarm due occurred so reset the same & resolve the Issue | Closed | Kapil Solanki
30 | North | 211814735 | 2025-12-03 14:45 | 125.4 | 4H.8041.../2320200 | Error Code Issue Call By Customer Name :- Mishra Mobile No :- 9671012574 | Closed | NCC LImited | SAAN Royal Power Solutions Private Limited - Sonipat | 1070 | SPN/FMI-51/5 & 516166/0 Related to ITV &ECU malfunctioning ; re-fit the connector and remove the code,issue resolved | Closed | Ved Prakash Gupta
31 | North | 211814671 | 2025-12-03 14:30 | 200 | 6H.8435.../2420008 | Rpm Issue Call By Customer Name :- Mukesh Sharma Mobile No :-9664286430 | Closed | AASHA DREAMESTATE LLP | Pratap Diesels Pvt. Ltd. - Alwar | 246 | SPN/FMI-5461/8 & 1761/16 ; open the Dosing module & clean DEF line with hot water & remove the code & resolve the Issue | Closed | Gourav Sharma
18 | South Zone | 211814695 | 2025-12-03 14:30 | 40 | 3H.8951.../2421155 | Genset Trip | Task Start | Local Self Government Department Kerala | G-Care Diesels Private Limited - Malappuram | 23 | Found under speed alarm in event log but SE run the DG 3-4 time no alarm found dg running ok, So checked the wiring harness found ok. Fuel line ok,then flash the ECU | Closed | Mr. Sanjaimon S
32 | North | 211814658 | 2025-12-03 14:24 | 58.5 | T4.8941.../2423209 | Abnormal sound issue Called by customer Name : AMAN MANGO Number : 7042592677 | Closed | CASSA LIVING FURNITUR & FURISHERS LTD | OVN Industries Private Limited - New Delhi | 31.9 | Customer raised complaint as abnormal sound but no such issue observed on site | Closed | Kapil Solanki
19 | South Zone | 211814484 | 2025-12-03 13:52 | 20 | GP3.8601.../2420792 | Starting Problem Call by : Customer Name :Manikandan Contact :8075912463 | Task Start | FABLO INNOVATIONS | G-Care Diesels Private Limited - Malappuram | 64 | Starting engine running time minor leakage from radiator intercooler hose clip so thighten the same,then start engine running performance found ok. Taken load trail also. | Closed | Mr. Sanjaimon S
30 | North | 211814470 | 2025-12-03 13:45 | 200 | 6H.8435.../2320023 | Starting Issue Call By Customer Name : Sanjay Kumar Number : 9870949533 | Open | Maxwel Exporters | R K Engineers - Meerut | 118 | Emergency stop alarm occurred due to connector found loose so tightened the same & resolve the Issue | Closed | Sudhir Awasthi
31 | North | 211814395 | 2025-12-03 13:26 | 40 | 3H.8951.../2420594 | Door lock issue Called by customer Name : Ankit Number : 9899883355 | Open | SR. Power Engineers | Vidyut Engineers - Noida | 18.4 | Canopy door lock issue,bolt on lock found loose so tightened the same & resolve the Issue | Closed | Kapil Solanki
16 | WEST | 211814381 | 45994.5563 | 40 | 3H.8951.../2520549 | Oil Leakage observed from gallery plug. | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from crankcase gallary plug . so tighten using k sealant | Closed | Jagdeep Saini
3 | East | 211814337 | 2025-12-03 13:13 | 320 | F6.8802.../2420151 | Fuel Injector issue call By customer Name:Suraj Kumar Number:9135346666 | Task Start | Usha Diesels. | Globalline India Services Private Limited - Muzaffarpur | 67 | DG having low fuel level and customer side no one was able to open the fuel tank cap so he created SR for site visit. For opening the cap. | CLOSED | Prabhakar Kumar
5 | South Zone | 211814303 | 2025-12-03 13:01 | 0 | 6H.8438.C4../2520002 | Add Blue Leakage | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the site noticed the adblue leak for Supply model adaptor damage outlet connecter damage | Task Start | Mr. NandhaGopal
32 | North | 211814300 | 2025-12-03 13:00 | 160 | 6H.8475.../2420387 | Starting issue Call By Customer Name:- devendra No:-8199890856 | Task Start | POONAM DAYAL | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 20 | Starting issue due to battry voltage found low,battery was not charging due to connection found loose so tightened the same & resolve the Issue | Closed | Kapil Solanki
14 | WEST | 211814238 | 2025-12-03 12:46 | 750 | DV2.8501.C4../2420057 | Abnormal sound in Alternator.. Email By KGD Name:- Vishal Raut | Completed | Nyati Hotels & Resorts Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 46.41 | Customer complaint- Abnormal noise was coming from DG. So SE went to the site and found that the DG vibrates slightly while doing stop at 1000 RMP. Other than this no problem was found | Closed
4 | East | 211814087 | 2025-12-03 12:19 | 10 | GP3.8301.../2420176 | Starting issue Called by customer Name :Ksankupar Number : 6009034651 | Task Start | Jordan Minor Seminary | Hibreed Engineering Pvt. Ltd. - Nagaon | 2 | DG not starting due to sweep stuck issue found proper voltage (5V in 3 pin and 12 V in 2 pin) continuity from the ECU found OK so open Allen Bolt and move the rack to and fro then checked and found issue resolved. | CLOSED | Ujjwal Das
39 | South Zone | 211814044 | 2025-12-03 12:11 | 200 | 6H.8435.../2420168 | Starting Problem Call by : Customer Name : Raj sheker Contact : 9640038116 | Task Start | Ayati Constructions & Estates LLP | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | Cancelled | Cancelled | Mr. MD Saleem
5 | East | 211814028 | 2025-12-03 12:02 | 15 | GP3.8501.../2420828 | Starting issue Call by customer Name:Mrigen Baishya Number :9365284505 | Open | UDAY BAISHYA | Hibreed Engineering Pvt. Ltd. - Guwahati |  | update pending | OPEN | Ujjwal Das
8 | East | 211814028 | 2025-12-03 12:02 | 15 | GP3.8501.../2420828 | Starting issue Call by customer Name:Mrigen Baishya Number :9365284505 | Open | UDAY BAISHYA | Hibreed Engineering Pvt. Ltd. - Guwahati | 355 | SE found engine not starting due to emergency switch loose connection and also fan belt loose after that tight the emergency switch connection also tightening the fan belt | OPEN | Ujjwal Das
42 | North | 211813995 | 2025-12-03 11:54 | 58.5 | T4.8941.../2520338 | Starting issue Call by customer Name:Mr. Rinku Madan Number :9873551088 | Closed | D V Enterprises | Pratap Diesels Pvt. Ltd. - Bhiwadi | 2.3 | SPN/FMI-516166/0 ;Amber lamp on ; remove the DTC & resolve the Issue | Closed | Gourav Sharma
6 | East | 211813992 | 2025-12-03 11:53 | 20 | GP3.8601.../2420013 | Starting Issue. Call By Customer. Name:-Shambhu Kumar Mobile No.:-9958349222 | Task Start | Mr. Nirmal Jee. | Globalline India Services Private Limited - Sasaram | 21 | DG not starting on the Automode due to mains sensing fuse got blown out, so replaced the fuse issue resolved, and found controller display got burning spot. | CLOSED | Prabhakar Kumar
15 | WEST | 211813967 | 2025-12-03 11:51 | 200 | 6H.8435.../2420162 | Starting Issue Call By Customer. Name:-Praveen Shelar Mobile No.:- 9860257839 | Task Start | Secure Matrix Constro Engineering Solution | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 122 | DG starting problem So checked and found that feed pump was not starting after overriding the controller. Checked feed pump power supply - 0VDC. On further analysis found that feed pump relay was on but there was no power output from the relay switch point so it was replaced. | Closed
33 | North | 211813941 | 2025-12-03 11:50 | 625 | DV0.8501.C4../2420038 | Fuel Sensor Issue Call By Customer Name :- Sattyam Jaiswal Mobile No :- 8571967956 | Task Start | Inpest India Pvt. Ltd. | R K Engineers - Muzaffarnagar | 182 | Fuel sensor replaced due to same found faulty | Closed | Sudhir Awasthi
43 | WEST | 211813907 | 2025-12-03 11:42 | 30 | 3H.8902.../2421292 | Starting Issue. Call By Customer. Name:-Gopal Shaha Mobile No.:-7397960014 | Closed | Shree Sai Enterprises. | Mahalaxmi Diesels - Goa | 7 | customer side lvm issue . | Closed | Jagdeep Saini
64 | South Zone | 211813893 | 2025-12-03 11:36 | 58.5 | T4.8941.../2421305 | Starting issue And Tripping issue Call By customer Name:Pawan Kumar Number:9972194591 | Closed | Udupi Skanda | Surya Power Services - Kalyan Nagar | 134 | DG not starting check and found 2B wire loose, tighten | Closed | Mr. Anil Kumar H G
43 | North | 211813861 | 2025-12-03 11:35 | 30 | 3H.8902.../2421409 | low fuel alarm issue Call by Customer Name :Ajay Kumar NO:8437379111 | Task Start | Head Master Corporate Office C/o. Gillz Beauty & Wellness Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Zirakpur | 23 | Low Fuel level alarm , Open the guage & re-fitted ,Issue resolved | Closed | Ved Prakash Gupta
34 | North | 211813885 | 2025-12-03 11:31 | 82.5 | 5H.8901.../2420532 | Starting issue Call by customer Name:Satvir Number :7417527464 | Task Start | Shri Siddhi Vinayak Creation Pvt Ltd | Deep Jyoti Electricals and Services - Bareilly | 151.33 | Auto starting issue , DC fuse burnt ,change the fuse & resolve the Issue | Closed | Sudhir Awasthi
14 | South Zone | 211813849 | 2025-12-03 11:28 | 82.5 | 5H.8901.../2420228 | Adblue Low Problem Call by : Customer Name :Rajesh Contact :9751834582 Dealer Contact No:9843129330 | Completed | HOTEL GOWRIKKRISHNA | Electro Controls-Tirupur | 71.45 | Adblue low top up the same | Closed | Mr. Sanjaimon S
35 | North | 211813825 | 2025-12-03 11:26 | 125.4 | 4H.8042.C4../2420693 | Voltage Fluctuation Issue & White smock issue Call By Customer Name :- Kamal Panday Mobile No :-9811408710 | Task Start | Amar Jyoti Charitable Trust | Vidyut Engineers - New Delhi | 21 | On load white smoke occurs from DG,DG was running on 12 KW,Check the fuel condition,found ok,check the DM & that also working properly,re-fitted the DM & again run on load at 31 KW,advised customer to run DG on much load | Closed | Kapil Solanki
36 | North | 211813817 | 2025-12-03 11:23 | 125.4 | 4H.8042.C4../2420691 | Starting Issue Call By KGD Name :- Manav Agarwal Mobile No :- 7817023671 | Task Start | PWD GOPESHWAR | GLOBALVISION POWER SOLUTIONS PVT LTD - Srinagar | 2.13 | Battery Voltage found low,mains supply connected to charger,showing AdBlue temp. high alarm , reset the code | Closed | Sudhir Awasthi
37 | North | 211813761 | 2025-12-03 11:06 | 20 | GP3.1021.../2420337 | INSTANCE ID:-100777474 SITE ID:-I-UE-ABDD-ENB-0926 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-ANKIT PAL NUMBER:-8726055959 | Task Start | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | Visit pending | open | Sudhir Awasthi
7 | East | 211813741 | 2025-12-03 11:02 | 82.5 | 5H.8901.../2420566 | Heating and white smoke issue called by customer Name : niraj number : 9128915905 | Open | KALYAN JEWELLERS.. | HACS Engineering and Tech Private Limited - Deoghar |  | Visit pending | OPEN | Prabhakar Kumar
17 | East | 211813741 | 2025-12-03 11:02 | 82.5 | 5H.8901.../2420566 | Heating and white smoke issue called by customer Name : niraj number : 9128915905 | Open | KALYAN JEWELLERS.. | HACS Engineering and Tech Private Limited - Deoghar |  | SR cancel work done on previous SR(coolant leakage due to clamp loose) | CANCELLED | Prabhakar Kumar
38 | North | 211813728 | 2025-12-03 10:58 | 125.4 | 4H.8042.C4../2420489 | Error Code Issue Call By Service Dealer Name :- Pushpendra Kumar Mobile No :- 9536236142 | Task Start | Somti Power Solutions | Espiem Engines & Machines (P) Limited - Aligarh | 350 | Update Pending | open | Sudhir Awasthi
33 | North | 211813692 | 2025-12-03 10:50 | 320 | F6.8802.../2420279 | Tripping Issue. Call By Customer. Name:-Hafiz Mobile No.:-8683881288 | Open | Orchid Hospitality Services Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 709 | SPN/FMI-1761/16 & 516166/0 ;Top-up the AdBlue & remove the code & resolve the Issue | Closed | Ved Prakash Gupta
11 | South Zone | 211813661 | 2025-12-03 10:46 | 25 | GP3.8702.../2421176 | Oil Leakage Issue Call by : Dealer Name :Arjun Contact :9745000854 | Task Start | Flash Generator Hires | Electro Controls - Palakkad | na | SE said oil consumption is more so remove the turbocharger taken to service dealer again refitted now it is in under observation. | Task Start | Mr. Sanjaimon S
34 | North | 211813597 | 2025-12-03 10:20 | 125.4 | 4H.8042.C4../2520020 | Emergency Stop issue and Door lock issue Call By Customer Name :- Shubham Number :- 9958033547 | Task Start | ELEDECO FAIRWAY RESERVE | Paluck Technologies Ltd. - Gurgaon | 218.15 | Emergency Stop activated on site & door lock issue ; release & fix respectively & resolve the Issue | Closed | Kapil Solanki
8 | East | 211813578 | 2025-12-03 10:17 | 82.5 | 5H.8901.../2420453 | Amber lamp on alarm issue Called by customer Name : BIKASH Number : 9874144042 | Open | GOURISARIA JEWELERS LLP | HACS Engineering and Tech Private Limited - Bokaro |  | SR will cancelled no issue in DG | CANCELLED | Prabhakar Kumar
35 | North | 211813576 | 2025-12-03 10:16 | 40 | 3H.8951.../2420431 | Shut Down Alaram Issue Call By Customer Name : Mohit Sir Number : 9838987576 | Task Start | Arihant Machinery Store | Vidyut Engineers - Noida | 233.7 | Emergency Stop activated on site ; release & resolve the Issue (Service Due) | Closed | Kapil Solanki
40 | South Zone | 211813526 | 2025-12-03 10:04 | 20 | GP3.8601.../2421255 | Starting Problem Call by : Customer Name : A Sainath Contact : 6301161295 | Task Start | sainath | Powerlinks Infra Tech Pvt Ltd - Warangal | 42 | checked engine found low fuel level. Mobile dg operating installation not proper. so we have suggested to customer maintain fuel level and proper installation, before starting engine body earthing, battery charging compulsory maintain ofter refill fuel started the engine taken load trails performence found ok | Closed | Mr. MD Saleem
36 | North | 211813517 | 2025-12-03 10:02 |  | 3H.8902.../2520063 | ENGINE OVER HEATING | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | 3(LR) | SPN/FMI 110/0, 110/16, 110/3 High Coolant temp. Alarm ;replace the Coolant Temp. sensor but issue remains same ,check water pump , found rusty , replace the same but issue remains same | open | Gourav Sharma
37 | North | 211813442 | 2025-12-03 09:45 | 320 | F6.8802.../2420179 | Tripping Issue. Call By Customer. name:- Zakir Mobile No.:-7895999777 | Task Start | St. Marys Academy. | R K Engineers - Meerut |  | Under Cancellation | Cancelled | Sudhir Awasthi
3 | WEST | 211813438 | 2025-12-03 09:44 | 200 | 6H.8435.../2420160 | Abnormal Sound Issue And Baring Issue Call By customer. Name:-Utkarsh Agarwal Mobile No.:- 9137649351 | Task Start | Mahamaya Polymers Pvt Ltd | Transcreek Engineers Pvt. Ltd. - Ambernath | 54 | V belt found in loose condition tight the belt. | Closed
6 | South Zone | 211813414 | 2025-12-03 09:29 | 0 | DV8.8501.C4../2420167 | Hose Replacement | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the dg noticed the coolant leak for engine block to A bank EGT coolant supply hose conneting L bent connecter threed not ok ,so coolent leak | Task Start | Mr. NandhaGopal
9 | East | 211813362 | 2025-12-03 09:04 | 20 | GP3.8604.../2420180 | INSTANCE ID:-100742007 SITE ID:- I-BR-AGIN-ENB-9022 CALL BY CUSTOMER// DG ISSUE:- DG OUT ALRAM ISSUE/START FAIL ALRAM NAME:- RATESH NUMBER:- 8340233128 | Cancelled | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | SR will cancelled no issue in DG | CANCELLED | Prabhakar Kumar
63 | South Zone | 211812736 | 2025-11-03 19:26 | 25 | GP3.8702.../2520071 | CLECARING PROBLEM Call by : Customer Name :Rajesh Contact :9110886046 | Task Start | SNR Tyres | Surya Power Services - Kalyan Nagar | 11 | neutral wire lug cut that reason voltage fluctuation then extra lug crimping lug | Closed | Mr. Anil Kumar H G
34 | South Zone | 211812710 | 2025-11-03 18:47 | 15 | GP3.8501.../2420086 | Trip_Genset_Low_Voltage | Open | T. Savithri | Madhu Engineering Sales & Service -Poonamallee,Chennai | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal
2 | WEST | 211812621 | 2025-11-03 18:16 | 250 | F6.8841.../2420215 | Starting Problem Call by : Customer Name :Hanumant Contact :7760370861 PANKAJ 7760370861 | Task Start | Krisala Buildtech LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 2007 | Radiator and air filter found chocked engine in construction site area , B check was not compeleed so warranty rejected from ASE site . | Closed
38 | North | 211812620 | 2025-11-03 18:16 | 625 | DV0.8501.C4../2420079 | Fuel Alarm Issue Call By Customer Name:-Devendra Saini No:-8053353744 | Task Start | HPL ELECTRIC & POWER LTD | SAAN Royal Power Solutions Private Limited - Sonipat | 229.2 | SPN/FMI-5786/3 & 3469/3 ; Check low pressure pipes of Fuel line found ok,check the continuity to FIP & common rail connector,found ok,remove the code & run the DG,issue resolved | Closed | Ved Prakash Gupta
1 | East | 211812634 | 2025-11-03 18:13 | 30 | 3H.8902.../2421029 | Starting Issue. Call By customer. Name:-Kiran Nedi Mobile No.:-6001165366 | Open | M/S Bahari Satra Parichalana Samittee | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 49 | visit pending | OPEN | Ujjwal Das
10 | East | 211812634 | 2025-11-03 18:13 | 30 | 3H.8902.../2421029 | Starting Issue. Call By customer. Name:-Kiran Nedi Mobile No.:-6001165366 | Open | M/S Bahari Satra Parichalana Samittee | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 49 | Update pending at dealer end | OPEN | Ujjwal Das
18 | East | 211812634 | 2025-11-03 18:13 | 30 | 3H.8902.../2421029 | Starting Issue. Call By customer. Name:-Kiran Nedi Mobile No.:-6001165366 | Open | M/S Bahari Satra Parichalana Samittee | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 49 | DG not Starting due to fuel restriction by fuel filter- found choked so replaced both fuel filter proper update pending | OPEN | Ujjwal Das
39 | North | 211812586 | 2025-11-03 18:03 | 125.4 | 4H.8041.../2420050 | Red Lamp Alarm Issue Call By Customer Name :-Raghuvi Kumar Mobile No :- 8076404542 | Closed | International Automotive Components | Paluck Technologies Ltd. - Faridabad |  | No Issue found on site | Closed | Kapil Solanki
2 | East | 211812323 | 2025-11-03 17:52 | 15 | GP3.8501.../2320023 | Starting Issue Call by customer Name :Megha singh Number :8981346902 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | Globalline India Services Private Limited - Muzaffarpur |  | visit pending | OPEN | Prabhakar Kumar
11 | East | 211812323 | 2025-11-03 17:52 | 15 | GP3.8501.../2320023 | Starting Issue Call by customer Name :Megha singh Number :8981346902 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | Globalline India Services Private Limited - Muzaffarpur |  | visit pending | OPEN | Prabhakar Kumar
19 | East | 211812323 | 2025-11-03 17:52 | 15 | GP3.8501.../2320023 | Starting Issue Call by customer Name :Megha singh Number :8981346902 | cancelled | GHL. Pharma & Diagnostic Pvt. Ltd. | Globalline India Services Private Limited - Muzaffarpur |  | SR opened by mistake, so cancelled | CANCELLED | Prabhakar Kumar
40 | North | 211812215 | 2025-11-03 17:49 | 160 | 6H.8475.../2420032 | Red lamp alarm issue Called by customer Name : Harish Number : 9958019312 | Closed | Airpack Compressor Teknologies Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 250 | Maintainance due alarm occurred so reset the same & resolve the Issue | Closed | Kapil Solanki
20 | South Zone | 211812048 | 2025-11-03 17:48 | 320 | F6.8802.../2420306 | Display problem Call by : Customer Name :Anshif Contact :7994741181 | Closed | SHOBHIKA WEDDINGS EDAPPAL LLP | G-Care Diesels Private Limited - Malappuram | 154 | Engine fuel gauge variation issue fuel gauge remove and clean after fitting fuel gauge and controller showing correct inform the customer fuel gauge and controller showing correct engine working found ok | Closed | Mr. Sanjaimon S
41 | North | 211812138 | 2025-11-03 17:46 | 58.5 | T4.8941.../2423102 | Starting Issue. Call By Customer. Name:-Nirbhay Singh Mobile No.:-8840798410 | Completed | Das Nursing Home | Espiem Engines & Machines (P) Limited - Farukhabad | 13 | Injector No. 1 connector removed and fitted Update Pending | open | Sudhir Awasthi
20 | WEST | 211811392 | 2025-11-03 16:44 | 125.4 | 4H.8042.C4../2420790 | Error Code issue call by customer Name:Sandip Number:9425145362 | Closed | NEHA AUTOMOBILES | Shree Engineering Service - Chhatarpur | 129 | SPN/FMI- 516166/0, So cleared the error code. | Closed
27 | South Zone | 211811388 | 2025-11-03 16:44 | 58.5 | T4.8941.../2421030 | starting issue Call By Customer Name :vikarm Number :9380955058 | Closed | KALYANI SWEETS | KALA Care Global LLP - Belagavi | 81.1 | SE found battery terminal open condition so connect the same. Inform customer also. | Closed | Mr. Anil Kumar H G
8 | South Zone | 211811360 | 2025-11-03 16:39 | 125.4 | 4H.8041.../2420692 | Starting issue and Tripping issue Call by customer Name:Sathigen Number:7397752898 | Closed | Sree Muragan Educational Trust. | Bharath Diesel Sales and Service - Salem | 33 | 4095/2,1 error code so checked the connection found ok. So clear the DTC now running ok. | Closed | Mr. NandhaGopal
55 | South Zone | 211811245 | 2025-11-03 16:14 | 500 | DV8.8501.C4../2420206 | Fuel leakage issue Call By Service Dealer Name :- Munipal Number :- 7722070511 | Closed | MYHNA MEADOWS | Surya Power Services - Bangalore | 7 | Arrest the leakage from fuel drain, tighten the drain bolt | Closed | Mr. Anil Kumar H G
30 | South Zone | 211811189 | 2025-11-03 16:01 | 20 | GP3.8601.../2420552 | Under voltage alarm issue Call by Service Dealer Name :Wasim NO:7899015698 | Task Start | Dr. Achar | KALA Care Global LLP - Hospet | 24 | 2791/14 Error code. So checked the EGR connector found ok then flash the ECU issue resolved | Closed | Mr. Anil Kumar H G
52 | South Zone | 211811181 | 2025-11-03 16:00 | 250 | F6.8841.../2420360 | Coolant Leakage Problem Call by : Customer Name : Rajashekar reddy Contact : 9866893289 | Task Start | Sterling Services. | Ultimate Power Source - Chittoor | 33 | Oil leakage from exhaust side | Task Start | Mr. NandhaGopal
17 | WEST | 211811179 | 45964.666 | 0 | T4.8941.../2520607 | Oil leakage | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Oil leakage from Main oil gallery to Fuel pump supply pipe banjo bolt , change the washer | Closed | Jagdeep Saini
24 | North | 211811160 | 2025-11-03 15:53 | 160 | 6H.8475.../2420024 | Maintenance Due Alarm Issue. Call By Customer. Name:-Tarun .. Mobile No.:-9315743664 | Task Start | Tool Room Engineers LLP | Paluck Technologies Ltd. - Faridabad | 251 | Maintenance due alarm, reset the alarm V-belt loose tightness the belt then issue resolve | Closed | Kapil Solanki
1 | WEST | 211811162 | 2025-11-03 15:53 | 125.4 | 4H.8042.C4../2420036 | Starting Issue Call By Customer Name :- Ankush Varyani Mobile No :-8379939614 | Task Start | Ankush Varyani | KALA Care Global LLP - Latur | 53 | Battey discharged due to battery charger connection from mains was not done . | Closed
3 | East | 211810987 | 2025-11-03 15:18 | 82.5 | 5H.8901.../2420566 | Automation Issue Call By Customer Name : Janamemjoy Sir Number : 6296521161 | Task Start | KALYAN JEWELLERS.. | HACS Engineering and Tech Private Limited - Deoghar | 16 | visit pending | OPEN | Prabhakar Kumar
12 | East | 211810987 | 2025-11-03 15:18 | 82.5 | 5H.8901.../2420566 | Automation Issue Call By Customer Name : Janamemjoy Sir Number : 6296521161 | Task Start | KALYAN JEWELLERS.. | HACS Engineering and Tech Private Limited - Deoghar | 16 | No issue in DG was running in mannual mode properly, autopannel side issue due to loose connection after fixing issue resolved | OPEN | Prabhakar Kumar
35 | South Zone | 211810980 | 2025-11-03 15:17 | 15 | GP3.8501.../2420086 | Starting Issue Call by customer Name :Balu jai Ram Number:9444147979 | Closed | T. Savithri | Madhu Engineering Sales & Service -Poonamallee,Chennai | 50 | Airlock issue in fuel line. | Closed | Mr. NandhaGopal
25 | North | 211810928 | 2025-11-03 15:06 | 20 | GP3.8601.../2320003 | Red Lamp On Alarm Issue . Call By Customer. Name:-Mayank Mobile No.:-8527468008 | Task Start | SPA. Yoga Private Limited | Vidyut Engineers - Noida | 31 | Found fuel level low, after fill the fuel reset the alarm then issue resolve & Educate the customer maintain the fuel level | Closed | Kapil Solanki
24 | North | 211810837 | 2025-11-03 14:59 | 320 | F6.8802.../2420302 | Battery Charge Issue Call By Customer Name : Himanshu Sir Number : 7903822757 | Task Start | Narayan Construction | Vidyut Engineers - New Delhi | 1 | Starting issue due to battery voltage found low(10.2 V) , battery charger was found in off condition in customer's pannel , corrected the same & resolve the Issue | Closed | Kapil Solanki
21 | South Zone | 211810756 | 2025-11-03 14:34 | 250 | F6.8842.C4../2420110 | Coolant Leakage Problem Call by : Customer Name :Rafek Contact :8157945948 | Closed | P M S A Memorial Malappuram District Co Operative Hospital Limited | G-Care Diesels Private Limited - Malappuram | 90 | Coolant leakage from supply module pipe hose clip. So replace the hose clip. Taken trail for one hrs no leakage found. | Closed | Mr. Sanjaimon S
36 | North | 211810693 | 2025-11-03 14:26 | 15 | GP3.8501.../2420094 | fuel leakage issue Called by customer Name : KD Number : 9813667297 | Open | Dhani Power Solutions | SAAN Royal Power Solutions Private Limited - Rohtak |  | Update Pending | Open | Ved Prakash Gupta
62 | South Zone | 211810676 | 2025-11-03 14:26 | 30 | 3H.8902.../2420201 | voltage not coming properly | Closed | Axis Bank Ltd | Sri Manjunath Technical Services - Vijaywada | 5.31 | found low voltage due to dg nutral connector failed so bypass the nutral then found voltage is ok | Closed | Mr. MD Saleem
37 | North | 211810641 | 2025-11-03 14:21 | 250 | F6.8841.../2420017 | Error Code Issue Call By Customer Name :- Sunil . Number :- 7833021724 | Task Start | Greenberry Hotels And Residency India Private Limited | SAAN Royal Power Solutions Private Limited - Shimla | 154.42 | Update Pending | Open | Ved Prakash Gupta
26 | North | 211810652 | 2025-11-03 14:18 | 25 | GP3.8702.../2420910 | Over Heating Issue Call By Customer Name :-PRAMUDIT MEHROTRA Mobile No :-9519430000 | Completed | Girija Shankar Mehrotra & Sons | Deep Jyoti Electricals and Services - Shahjahanpur | 695 | Expension bellow damage replace the Bellow | Closed | Sudhir Awasthi
18 | WEST | 211810620 | 2025-11-03 14:11 | 160 | 6H.8475.../2420369 | Under speed alarm issue Called by customer Name : Kaushik Number : 9723338082 | Closed | Bharti Marketing | Unique Techno Services Pvt Ltd. - Vapi | 52 | Found the V bolt loose and tightened it. | Closed
10 | East | 211782405 | 2025-11-03 13:59 | 625 | DV0.8501.C4../2420160 | Starting Issue Email By - GOEM Name - Saktimay Satpathy | Closed | RUNGTA SONS PVT LTD. | Gangpur Sales and Services - Keonjhar | 83 | SE found Engine not start due to low level Urea after that top up the urea issue resolved. | CLOSED | Ujjwal Das
1 | South Zone | 211810496 | 2025-11-03 13:44 | 160 | 6H.8475.../2420366 | Fuel Sensor Call by : KGD Contact :9677095740 Customer name :Mr. Balamurugan Customer number :9994173931 | Open | Athulya Assisted Living | Bharath Diesel Sales and Service - Chennai | 3 | Fuel level variation shown in display so SE remove the fuel level sensor checked the sensor and again refitted issue resovle. | Closed | Mr. NandhaGopal
1 | WEST | 211810472 | 2025-11-03 13:41 | 125.4 | 4H.8041.../2420541 | Battery under voltage issue Call by customer Name :Mahesh jagtap Number:9930262638 | Completed | VIJAY SALES (INDIA) PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 455 | Charging alternator fuse found burn so change the fuse . | Closed | Jagdeep Saini
61 | South Zone | 211810300 | 2025-11-03 13:26 | 30 | 3H.8902.../2421878 | Oil leakage | Task Start | ATC Telecom Infrastructure Private Limited | Surya Power Services - Billekahalli | 2 | oil leakage from pump to breather hose due TO oem plant not proper over tight the clamp ,so New oil Pipe Replaced Done, | Closed | Mr. Anil Kumar H G
27 | North | 211810217 | 2025-11-03 13:10 |  | 4H.8052.C4../2520014 | LINE REJECTION | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-1 | SPN/FMI 51/0 Throttle valve jammed, replace the same after that issue resolve | Closed | Gourav sharma
4 | East | 211810184 | 2025-11-03 13:05 | 200 | 6H.8438.C4../2420034 | Start fail alarm issue Call by Customer Name :Arun Prakash NO:9312288780 | Task Start | Ultratech Cement Limited | Hibreed Engineering Pvt. Ltd. - Nagaon | 21 | Found charging failure alarm so SE checked found fuse burn so replaced the fuse and also found 516166 ECU flt code to cleared the code. | CLOSED | Ujjwal Das
38 | North | 211810181 | 2025-11-03 13:04 | 82.5 | 5H.8901.../2420722 | Automation Issue Call By Customer Name - Deepak No - 9350958638 | Closed | GOYAL SONS ZAVERI PVT LTD | SAAN Royal Power Solutions Private Limited - Hisar | 108 | Control panel 1C2 wire found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
39 | North | 211810170 | 2025-11-03 13:00 | 82.5 | 5H.8901.../2420193 | door issue Call By Customer Name :-amit kumar Number:- 9812720091 | Closed | Atmosphere I. N. C. | SAAN Royal Power Solutions Private Limited - Panipat | 39.41 | Door lock issue due to door not fixed in catcher so fix the catcher & resolve the Issue | Closed | Ved Prakash Gupta
54 | South Zone | 211810137 | 2025-11-03 12:56 | 25 | GP3.8702.../2420866 | Starting Problem Call by : Customer Name : Anil Contact : 9849415927 | Closed | M/S SMART KIDS INDIA INNOVATIONS | Sri Manjunath Technical Services - Vijaywada | 15 | Start the DG are not starting problem.Observed the safety unit showing Device Bat Low Vlt alarm.So check the(XDBK4) 2A sening B connector problem. Set the 2A sening wiring after start the DG and observed the DG running condition is ok No leakages. | Closed | Mr. MD Saleem
28 | North | 211810133 | 2025-11-03 12:54 | 15 | GP3.8501.../2422083 | Umber lamp Alarm issue Call by customer Name:Hardik JI Number:9897047137 | Task Start | KP GROUP OF ENGINEERS | R K Engineers - Saharanpur | 18 | SPN/FMI 2802/3 Show in the KRM but when Engineer visit the site found no any issue trail on load the dg about 30 min. | Closed | Sudhir Awasthi
25 | North | 211810133 | 2025-11-03 12:54 | 15 | GP3.8501.../2422083 | Umber lamp Alarm issue Call by customer Name:Hardik JI Number:9897047137 | Task Start | KP GROUP OF ENGINEERS | R K Engineers - Saharanpur | 18 | Amber lamp on occurred & customer reset controller before engineer visited the site , run the DG for 20 minutes but no such Issue observed | Closed | Sudhir Awasthi
26 | North | 211810112 | 2025-11-03 12:49 | 125.4 | 4H.8041.../2420559 | Tripping / starting problem. Call By Customer Name :-vikesh Number:- 7732963832 | Closed | GRJ. Distributors and Developers Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 311 | Controller not operating check & clean the on/off selector switch & on the controller , Issue resolved | Closed | Gourav sharma
21 | WEST | 211810048 | 2025-11-03 12:43 | 125.4 | 4H.8041.../2420340 | Nutral Wire Burn Issue And Power Supply Issue Call By Customer Name :- Surendar Mobile No :-9893163287 | Task Start | Hotel Isabel Palace | Shree Engineering Service - Chhatarpur | 113 | 250Ams mains contactor newtral point has burnt out so it needs to be replaced. A Check was not completed so warranty rejected from ASE side. | Closed
2 | WEST | 211809986 | 2025-11-03 12:31 | 82.5 | 5H.8901.../2420771 | Controller issue Call By Customer Name :- Sumay Mobile No:-8551064583 | Task Start | Umiya Nakshatra Heights | Transcreek Engineers Pvt. Ltd. - Ambernath | 18 | krm data on mobile apps did not showing then removed krm unit and & krm sim card ok then refitment sim card & krm unit ok | Closed | Jagdeep Saini
27 | North | 211809944 | 2025-11-03 12:28 | 45 | 3H.8951.../2520060 | Load issue and Mid lamp alarm issue Call by customer Name - VIVEK GUPTA No - 9140961872 | Open | Field Marshal Agency | Excel Diesel Private Limited - Faizabad |  | Visit pending | open | Sudhir Awasthi
60 | South Zone | 211809942 | 2025-11-03 12:26 | 25 | GP3.8702.../2421357 | DG Expension below silver boby broken | Open | ATC Telecom Infrastructure Private Limited | Surya Power Services - Peenya, Bangalore | 2 | silencer glading is broken so refitted the glading and started the DG working condition | Closed | Mr. Anil Kumar H G
53 | South Zone | 211809893 | 2025-11-03 12:10 | 125.4 | 4H.8042.C4../2420578 | Spn No Alarm Issue Call By Customer Name:-CHI Impex CHI Impex No:-9964140079 | Closed | CHI Impex | Surya Power Services - Peenya, Bangalore | 20 | As per customer complaint Alarm issue. Visited the site observed wiring connection issues. After reconnected and connected to iconnect tool Ecu flashing Finally started the dg observed on running condition found working is satisfactory. | Closed | Mr. Anil Kumar H G
29 | North | 211809891 | 2025-11-03 12:08 | 250 | F6.8841.../2320006 | Starting issue Call by customer Name: Pravin Gard Number:9818577517 | Task Start | Katyayani Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi | 162 | SPN/FMI 100/2, 100/3, 110/4, 102/5 , 168/3 7026/7 3031/14 Clar the DTC but we when check the KRM Show the SPN/FMI 168/3 | Closed | Gourav sharma
3 | WEST | 211809804 | 2025-11-03 12:00 | 5.5 | CC1.1013.../2400577 | Starting Issue Call By Customer Name :- Kokle .. Mobile No :- 7722000641 | Task Start | Mahaveer Traders | Mahalaxmi Diesels - Satara | 336 | Maintainance due alarm need to do oil servicing . | Closed | Jagdeep Saini
30 | North | 211809791 | 2025-11-03 11:54 | 58.5 | T4.8941.../2520243 | Black Smoke issue Call By Customer Name :- Mohamad Shanawaz Mobile No:-9015771786 | Task Start | ICON GENERATOR SERVICE | Vidyut Engineers - Noida | 7 | Wrong report SR | Closed | Kapil Solanki
16 | South Zone | 211809703 | 2025-11-03 11:33 | 82.5 | 5H.8901.../2420824 | Voltage Problem Call by : Customer Name :Melvin Contact :8157082049 | Closed | PR TIJO THOMAS | G-Care Diesels Private Limited - Ernakulam | 271 | Dg starting normaly no abnormal sound available load normal voltage normal, found error code issue SPN 6595 FMI 0, clear the error code, no voltage issue found , customer issue is home Air conditioner auto start not working properly, then checked other equipment all good, dg load normal, advice to contact AC service team. | Closed | Mr. Sanjaimon S
40 | North | 211809717 | 2025-11-03 11:31 | 125.4 | 4H.8041.../2420774 | Starting Issue Call By Customer Name:-Kaptan .. No:-9728131084 | Open | I. B. School | SAAN Royal Power Solutions Private Limited - Rohtak |  | Starting issue due to Battery found faulty ; in one cell , gravity found 0 so send the same for testing | Closed | Ved Prakash Gupta
31 | North | 211809692 | 2025-11-03 11:28 | 20 | GP3.8601.../2421343 | Oil leakage Issue. Call By Customer Name :- Guarav Ahuja Mobile No :- 9599195910 | Closed | AHUJA PLASTIC UDYOG | Paluck Technologies Ltd. - Faridabad | 6.8 | Coolant leakage from radiator hose clamp tightness the same then issue resolve | Closed | Kapil Solanki
14 | East | 211809663 | 2025-11-03 11:23 | 20 | GP3.8601.../2421581 | Starting issue Called by customer Name : Ahmed Number : 9864010774 | Closed | M/S HP RANGIA TOWN | Hibreed Engineering Pvt. Ltd. - Guwahati | 42 | DG not starting showing charging failure so checked and found the Charging allternater fuse loose and dust deposition so cleaned properly then started found OK. | CLOSED | Ujjwal Das
13 | South zone | 211809594 | 2025-11-03 11:06 | 82.5 | 5H.8901.../2420124 | Starting Problem Call by : Customer Name :Vemburaj Contact :9952453447 | Closed | VALLI VILAS JEWELLERY | Bharath Diesel Sales and Service - Pattanur | 77 | check and found start relay wire loose connection 2A wire and Battery charger negtive wire loose contdtion no Battery charger voltage 11.5 wiring correction ok battery charger working good 13.2 | Closed | Mr. NandhaGopal
41 | North | 211809572 | 2025-11-03 10:53 | 40 | 3H.8951.../2420452 | Oil Leakage issue Call By Customer Name :- Rajan Mobile No :- 7087023689 | Task Start | Bangali Hotel & Restaurant. | Megatron Engineers - Pathankot | 4.22 | Lube Oil leakage found from turbo drain pipe due to bolt found loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta
4 | WEST | 211809543 | 2025-11-03 10:51 | 45 | 3H.8951.../2520235 | Starting Issue Call By Customer Name - Rohit Number - 8454989218 | Closed | Jagannath Gangaram Pednekar Jewellers Dapoli | Mahalaxmi Diesels - Karad | 16 | Battery charger output voltage was not stable it decreases , due to low battery voltage float type battery was placed , need to change the battery charger. | Closed
52 | South Zone | 211809512 | 2025-11-03 10:40 | 58.5 | T4.8941.../2421246 | Automation Issue Call by Service Dealer Name :Vishawa NO:9035054793 | Task Start | SAGAYI INTERNATION RESORT | Prasad Power Engineers - Hassan | 21 | Visited the site found automation issue due to controller wiring loose connection then re correct the all wiring connections then start the engine running condition is good | Closed | Mr. Anil Kumar H G
4 | WEST | 211809495 | 2025-11-03 10:38 | 400 | DV8.8542.C4../2420125 | High Consumption Issue Email By KGD Name:-Samadhan Payghan | Task Start | Jayshree Pistons Pvt. Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 92 | DEF Level low so top up b bank , need to top up a bank . | Closed | Jagdeep Saini
42 | North | 211809442 | 2025-11-03 10:30 | 30 | 3H.8902.../2420105 | DG not starting-518012 | Completed | ICICI Bank Limited | Megatron Engineers - Amritsar |  | Visit Pending | Open | Ved Prakash Gupta
43 | North | 211809456 | 2025-11-03 10:28 | 125.4 | 4H.8041.../2420441 | Urea Related Issue Call By Customer Name:-Vijay Sharma No:-9858683215 | Completed | Speedo Garments | Suraj Motor Store - Jammu | 139 | problem due to fuel line & DEF line chocked so clean the DEF line with Hot water & clean fuel line , Issue resolved | Closed | Ved Prakash Gupta
44 | North | 211809404 | 2025-11-03 10:22 | 320 | F6.8802.../2420004 | Emergency Stop Alarm & Lock Issue. Call by Customer. Name:- Somveer Mobile No.:-8708612594 | Open | Fresenius Kabi India Private Limited | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 232 | Emergency Stop alarm occurred constantly & no such issue found in its switch ; even after bypass the supply from controller(Pin No. - 3) alarm occurs, so flash the controller & resolve the Issue | Closed | Ved Prakash Gupta
33 | South Zone | 211809386 | 2025-11-03 10:07 | 125.4 | 4H.8041.../2420560 | ENGINE NOT STARTING | Task Start | Amrit Medicare P. Ltd. | Madhu Engineering Sales & Service - Teynampet,Chennai | LR | (SPN-157 and Fmi-14).so checked fuel system and NRV is not working so replaced but same problem IMV stuck found | Task Start | Mr. NandhaGopal
5 | WEST | 211809346 | 2025-11-03 10:02 | 58.5 | T4.8941.../2520438 | Tripping issue Called by customer Name : Suraj patil Number : 9011031362 | Closed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 1 | Customer use external fuel tank , do not use kirlokar tank , so as per customer requirement change the parameter , fuel level disable. | Closed | Jagdeep Saini
6 | WEST | 211809341 | 2025-11-03 10:00 | 58.5 | T4.8941.../2520105 | Tripping issue Called by customer Name : Suraj patil Number : 9011031362 | Closed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 1 | Customer use external fuel tank , do not use kirlokar tank , so as per customer requirement change the parameter , fuel level disable. | Closed | Jagdeep Saini
19 | South zone | 211809319 | 2025-11-03 09:57 | 58.5 | T4.8941.../2423026 | Low voltage issue Call by : Customer Name : Venkatesh Contact :9952897054 | Completed | ANNAM RESTAURANT | Bharath Diesel Sales and Service - Karur | 7 | Inspected the Customer site Low voltage problem so check the DG voltage 354 volts phase to phase , check the engine RPM 1500 so As per Kirloskar AO instructions AVR voltage adjusting for 412 voltage started and checked with load found ok | Closed | Mr. NandhaGopal
7 | WEST | 211809305 | 2025-11-03 09:55 | 30 | 3H.8902.../2420773 | Hunting Issue Email By - KGD Name -Surekha Auti | Task Start | Shree Lakshminarayan Petroleum | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati | 300 | No issue with dg customer side problem. | Closed | Jagdeep Saini
32 | North | 211809309 | 2025-11-03 09:55 | 320 | F6.8802.../2420135 | LINE REJECTION | Closed | Krishna Enterprises. | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-17 | found fan pully damage interchange with other engine then issue resolve | Closed | Gourav sharma
59 | South Zone | 211809295 | 2025-11-03 09:51 | 58.5 | T4.8941.../2421057 | Starting Issue Call By Customer Name - Sonam .. Number - 7590844281 | Task Start | Rato Dratsang | Prasad Power Engineers - Sirsi | 1.25 | DG not starting check the panel board found wire is cut. joint the wire | Closed | Mr. Anil Kumar H G
33 | North | 211809259 | 2025-11-03 09:35 | 20 | GP3.8604.../2420159 | INSTANCE ID:-100742282 SITE ID:- I-RJ-CHMU-ENB-G004 CALL BY CUSTOMER// DG ISSUE:- DG LOW FUEL ALRAM ISSUE NAME:- Manish Kumar NUMBER:- 6350491536 | Task Start | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - JAIPUR | 28 | Low fuel level, after topup the fuel then issue resolve Educate the customer kindly maintain the fuel level | Closed | Gourav sharma
5 | East | 211809227 | 2025-11-03 09:17 | 20 | GP3.8604.../2420062 | INSTANCE ID:-100740972 SITE ID:-I-BR-SIMR-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG AUTOMATION /AIR FAULTY NAME:- Anuj Kumar NUMBER:- 8084447706 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | update pending | OPEN | Prabhakar Kumar
12 | East | 211793838 | 2025-11-03 09:17 | 25 | GP3.8702.../2520123 | Dg not Start | Closed | ATC Telecom Infrastructure Private Limited | Gangpur Sales and Services - BHUBANESWAR | 45 | SE found engine cranking but not start &show alram fail to start check the fuel line then check all conector & retight all wiring conection found all r normally but issue not solved then found 2C fuse wire loose then tight the wire issue resolved. | CLOSED | Ujjwal Das
13 | East | 211809227 | 2025-11-03 09:17 | 20 | GP3.8604.../2420062 | INSTANCE ID:-100740972 SITE ID:-I-BR-SIMR-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG AUTOMATION /AIR FAULTY NAME:- Anuj Kumar NUMBER:- 8084447706 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | Update pending at dealer end | OPEN | Prabhakar Kumar
20 | East | 211809227 | 2025-11-03 09:17 | 20 | GP3.8604.../2420062 | INSTANCE ID:-100740972 SITE ID:-I-BR-SIMR-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG AUTOMATION /AIR FAULTY NAME:- Anuj Kumar NUMBER:- 8084447706 | cancelled | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | Customer need Service SR cancelled | CANCELLED | Prabhakar Kumar
28 | North | 211809195 | 2025-11-03 09:01 | 250 | F6.8841.../2420286 | Low Fuel Alarm issue Call By Customer Name :- Baldev Mobile No:9414188539 | Task Start | Bala Ji Enterprises | Rajdhani Diesels and Electricals - Barmer |  | Visit pending | open | Gourav sharma
34 | North | 211809189 | 2025-11-03 08:54 | 320 | F6.8802.../2420330 | fan belt sound issue Call By Customer Name :-dhanjeet pandy Number:- 9650712290 | Closed | Hirohama India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 131 | found charging alternator fan belt adjusting bolt loose tightness the same | Closed | Gourav sharma
29 | North | 211809161 | 2025-11-03 08:26 | 20 | GP3.8601.../2421061 | Power Supply Issue Call By Customer Name :- Varsha Sharma Number :- 8955776137 | Task Start | Anand Shankar Mall. | Pratap Diesels Pvt. Ltd. - BIKANER | 54 | VMR output issue due to installation of earthing was not proper,Update pending | open | Gourav sharma
35 | North | 211809171 | 2025-11-03 08:11 | 30 | 3H.8902.../2420994 | Starting Issue And Shut Down Alarm Call By Customer Name :- Indrajeet Singh Mobile No:-7678668937 | Closed | SR. Power Engineers | OVN Industries Private Limited - New Delhi | 10 | Fuel tank Empty topup the fuel remove the air then issue resolve, Educate the customer For maintain the fuel level | Closed | Kapil Solanki
4 | South Zone | 211809127 | 2025-11-03 07:35 | 125 | 4H.8052.C4../2520058 | CAC HOSE FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | CAC hose damage Change the new CAC hose fixing done | Closed | Mr. NandhaGopal
19 | WEST | 211809825 | 2025-11-03 | 125 | 4H.8042.C4../2420654 | CC SR | Task Start | Mr. Badal Sahani | Unique Techno Services Pvt Ltd. - Baroda | LR | SPN/FMI- 520528/31(Inducement related DM2) DG started but after some time stopped due to the above error code. Tightened all the wire connections of relay board and refited the ignition relay wire. Now DG is running smoothly. | OPEN | Amit sandlya
8 | WEST | 211808483 | 2025-10-03 19:44 | 58.5 | T4.8941.../2520413 | Tripping issue Called by customer Name : Ganesh Number : 9011031362 | Closed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 1 | Customer use external fuel tank , do not use kirlokar tank , so as per customer requirement change the parameter , fuel level disable. | Closed | Jagdeep Saini
9 | WEST | 211808482 | 2025-10-03 19:43 | 58.5 | T4.8941.../2422638 | Tripping issue Called by customer Name : Ganesh Number : 9011031362 | Closed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 1 | Customer use external fuel tank , do not use kirlokar tank , so as per customer requirement change the parameter , fuel level disable. | Closed | Jagdeep Saini
10 | WEST | 211808481 | 2025-10-03 19:42 | 58.5 | T4.8941.../2520410 | Tripping issue Called by customer Name : Ganesh Number : 9011031362 | Closed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 1 | Customer use external fuel tank , do not use kirlokar tank , so as per customer requirement change the parameter , fuel level disable. | Closed | Jagdeep Saini
13 | East | 211786670 | 2025-10-03 19:36 | 10 | GP3.8301.../2420058 | Red lamp Alarm issue Call By Customer Name :- Saurabh Rai Mobile No :-7008755713 | Cancelled | SAINIK MINING AND ALLIED SERVICES LIMITED | Gangpur Sales and Services - Jharsuguda | 38 | SR cancelled on telephonic communication resolved | CANCELLED | Ujjwal Das
19 | East | 211808463 | 2025-10-03 19:14 | 30 | 3H.8902.../2420332 | Starting Issue Call By Customer Name:-Dilip Prasad No:-8453091307 | Open | M/s. Purbanchal Safety Glass Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati |  | visit pending | OPEN | Ujjwal Das
6 | East | 211808463 | 2025-10-03 19:14 | 30 | 3H.8902.../2420332 | Starting Issue Call By Customer Name:-Dilip Prasad No:-8453091307 | Closed | M/s. Purbanchal Safety Glass Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 1 | update pending | OPEN | Ujjwal Das
14 | East | 211808463 | 2025-10-03 19:14 | 30 | 3H.8902.../2420332 | Starting Issue Call By Customer Name:-Dilip Prasad No:-8453091307 | Closed | M/s. Purbanchal Safety Glass Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 1 | Update pending at dealer end | OPEN | Ujjwal Das
21 | East | 211808463 | 2025-10-03 19:14 | 30 | 3H.8902.../2420332 | Starting Issue Call By Customer Name:-Dilip Prasad No:-8453091307 | Closed | M/s. Purbanchal Safety Glass Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 1 | EGR 2791/18 code pop on display checked voltage at EGR found OK so flashed the ECU code cleared. | CLOSED | Ujjwal Das
13 | NORTH | 211808441 | 2025-10-03 19:04 | 15 | GP3.8501.../2421610 | Earthing Issue Call By Customer Name:-Shivam Sing No:-8887878304 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | Espiem Engines & Machines (P) Limited - KANPUR | 33 | Customer side machin issue | Closed | Sudhir Awasthi
12 | NORTH | 211808441 | 2025-10-03 19:04 | 15 | GP3.8501.../2421610 | Earthing Issue Call By Customer Name:-Shivam Sing No:-8887878304 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | Espiem Engines & Machines (P) Limited - KANPUR | 33 | Customer raised complaint as starting issue but on site no such Issue observed | Closed | Sudhir Awasthi
58 | South Zone | 211808280 | 2025-10-03 18:01 | 82.5 | 5H.8901.../2420476 | Low Oil Pressure Problem Call by : Customer Name :Jayaprakash Contact :8778523191 | Task Start | KALYAN JEWELLERS INDIA LTD | Madhu Engineering Sales & Service -Poonamallee,Chennai | 600 | Oil leakage from sump also from rocker cover side so tighten the bolt and applied K-sealant. | Closed | Mr. NandhaGopal
13 | NORTH | 211808216 | 2025-10-03 17:47 | 200 | 6H.8435.../2420093 | Dg issue | Task Start | RELIANCE PROJECTS & PROPERTY MANAGEMENT SERVICES LIMITED | Espiem Engines & Machines (P) Limited - Aligarh | 295 | Voltage found low so set-up from 230 V to 240 V per phase as per customer demand & maintainance due alarm occurred so reset the same | Closed | Sudhir Awasthi
20 | East | 211808170 | 2025-10-03 17:37 | 125.4 | 4H.8042.C4../2420985 | Red Lamp Larm issue And umber lamp alarm issue Call By Customer Name :-Tanmay Chakravati Number:- 9147732491 | Task Start | Metro Retail Pvt. Ltd. | HACS Engineering and Tech Private Limited - Deoghar | 30 | visit pending | OPEN | Prabhakar Kumar
7 | East | 211808170 | 2025-10-03 17:37 | 125.4 | 4H.8042.C4../2420985 | Red Lamp Larm issue And umber lamp alarm issue Call By Customer Name :-Tanmay Chakravati Number:- 9147732491 | Task Start | Metro Retail Pvt. Ltd. | HACS Engineering and Tech Private Limited - Deoghar | 30 | Under speed alarm so SE reconnected the fuel suction line properly after that cranked the DG started and resolved issue raised due to the air lock issue | CLOSED | Prabhakar Kumar
51 | South Zone | 211808074 | 2025-10-03 17:18 | 160 | 6H.8475.../2420067 | Voltage Issue And abnormal Sound Issue Call by Customer Name Dipak . NO:9108134071 | Task Start | EBO MART PRIVATE LIMITED | Surya Power Services - Bommasandra, Bangalore | 86 | Visit the site check the engine problem is v belt is not working properly after adjusting the V belt coundtion after checking the engine oil level ok,top upthe radiator coolant,fuel hose all wiring connection, check the ECU and GCU connection,DEF level ok, SCR connection after start the engine running coundtion ok but coustomer required dg input voltage 230 required after adjusting the voltage in AVR aft put on the load dg running coundtion ok found ok | Closed | Mr. Anil Kumar H G
14 | NORTH | 211807956 | 2025-10-03 17:12 | 20 | GP3.8601.../2420707 | Error Code Issue Call By Customer Name :Rishabh Mittal Number : 8860588605 | Open | Rahul Sir | Vidyut Engineers - New Delhi |  | Cancelled-PM Cancelled by Admin | Cancelled | Kapil Solanki
50 | South Zone | 211807950 | 2025-10-03 17:12 | 20 | GP3.8601.../2420900 | Controler pannel problem Call by : Customer Name : Prudhvi Contact : 9885166655 | Task Start | Sri Rama Nilayam | Sri Manjunath Technical Services - Narasaraopet | 25 | attend the site check the engine oil level found ok, checked the fuel pipes condition found ok, checked the dg control panel board, found relay cord bolt damaged | Closed | Mr. MD Saleem
7 | South Zone | 211807406 | 2025-10-03 16:48 | 40 | 3H.8951.../2420971 | Starting Problem Call by : Customer Name : Gopinath Contact : 9047176459 | Task Start | Sri Velavan Stores. | Bharath Diesel Sales and Service - Puducherry | 18 | Battery charger Ac input line disconnected from the EB panel it's caused the battery voltage getting down so reconnected the Battery charger ac input line done and checked the charger working and charging found ok. Started the engine running found ok. | Closed | Mr. NandhaGopal
11 | WEST | 211807384 | 2025-10-03 16:45 | 20 | GP3.1021.../2420213 | CPH Test Requried | Cancelled | Reliance Jio Infocomm Limited | Mahalaxmi Diesels - Satara |  | cancelled | Closed | Jagdeep Saini
21 | East | 211807344 | 2025-10-03 16:36 | 20 | GP3.8601.../2420741 | Alarm issue Call By Customer Name :- Amit Mobile No :-8929151618 | Open | AAROHI HOSPITALITY | Globalline India Services Private Limited - Purnia | 87 | visit pending | OPEN | Prabhakar Kumar
11 | East | 211788282 | 2025-10-03 16:36 | 30 | 3H.8902.../2421343 | Genset Trip | Closed | MANOJ KUMAR | Gangpur Sales and Services - Berhampur | 143 | SE found no issue in DG, DG was running properly | CLOSED | Ujjwal Das
14 | NORTH | 211807195 | 2025-10-03 16:17 | 125.4 | 4H.8041.../2420745 | Amber lamp alarm Call By Customer Name :- YOGENDER KUMAR Mobile No :-9958440104 | Open | JAIN GENERATOR HIRING CO.. | Paluck Technologies Ltd. - Faridabad |  | Visit pending | open | Kapil Solanki
5 | WEST | 211807163 | 2025-10-03 16:09 | 15 | GP3.8501.../2420649 | Starting Issue Call by Customer Name Mr.nagesh patil NO:9890350077 | Task Start | New Tanishka Cake Cafe | Mahalaxmi Diesels - Pandharpur | 144 | Oil level increased due to diesel mix in oil , pushrod , valve found ok , may be fuel pump oil seal damage and internal issue , change the fuel pump , issue solved. | Closed | Failed Part Required
22 | East | 211807161 | 2025-10-03 16:08 | 25 | GP3.8702.../2421760 | Coolant Leakage issue Call By Customer Name :- Roshan Kumar Mobile No :-7610000230 | Task Start | ISC. Projects Pvt. Ltd. | HACS Engineering and Tech Private Limited - Hazaribagh | 181 | Coolant seepage found at thermostat outlet hose due to clamp loose after tightening issue resolved | CLOSED | Prabhakar Kumar
15 | NORTH | 211807147 | 2025-10-03 16:03 | 125.4 | 4H.8042.C4../2420555 | MCB Lamp & Red lamp alarm Issue. Call By customer. Name:-Mahendra .. Mobile No.:-9050314400 | Closed | ASHWANI COATING INDIA PVT LTD | Paluck Technologies Ltd. - Gurgaon | 16 | Def level low, topup the def then issue resolve | Closed | Kapil Solanki
16 | NORTH | 211807084 | 2025-10-03 15:59 | 200 | 6H.8435.../2320029 | Call By Customer Name :- .vijay . Mobile No :-7836802304 | Closed | KMSP. Industries | Paluck Technologies Ltd. - Ghaziabad | 292 | SPN/FMI 3364/8, 1761/15, 4094/2 Found coolant in DEF tank so, clean the Def tank, Change the Supply module filter | Closed | Kapil Solanki
15 | NORTH | 211807075 | 2025-10-03 15:56 | 45 | 3H.8951.../2420715 | AMF panel Problem Call by : Customer Name : Ravikumar Contact : 9441335332 | Open | Ravi kumar | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi
16 | NORTH | 211807072 | 2025-10-03 15:55 | 58.5 | T4.8941.../2422321 | Oil Consumption Issue & Black Smoke Issue Call By Customer Name- Raju Number-9212005372 | Task Start | RAJU GENERATORS | OVN Industries Private Limited - New Delhi | 477 | Visit pending | open | Kapil Solanki
3 | South zone | 211807045 | 2025-10-03 15:51 | 20 | GP3.8601.../2520252 | Low Voltage issue Call By Customer Name :- Abhishek Mobile No:-9986012881 | Task Start | Abhishek . | Surya Power Services - Billekahalli | 2 | Battery voltage low as the customer not given charging supply | Closed | Mr. Anil Kumar H G
49 | South Zone | 211807032 | 2025-10-03 15:45 | 20 | GP3.8601.../2421172 | Starting Problem (Accident Damage) Call by : Customer Name :Akhil Krishnan Contact :9745890844 | Task Close | Favourite Construction P Ltd | Electro Controls - Thiruvananthapuram | 30 | REACHED SITE CHECKED DG.THIS IS CONSTRUCTION SITE.DURING TRANSPORTATION OF MATERIALS.A DUMBER TRUCK HITTED ON THE CANOPY SIDE.INSPECTED THE ENGINE , ALTERNATOR . VISUALLY THE ENGINE &ALTERNATOR IS OK.CAN'T OPEN THE CONTROLLER SIDE DOOR BECAUSE THE DOOR IS ALSO DAMAGED DUE TO THE IMPACT DIDN'T START THE ENGINE.CLEARLY INTIMATED CUSTOMER THAT THE CANOPY DAMAGE WILL NOT COVER UNDER WARRANTY BECAUSE IT IS AN EXTERNAL DAMAGE | Closed | Mr. Sanjaimon S
17 | NORTH | 211806928 | 2025-10-03 15:31 | 500 | DV8.8501.C4../2420020 | Tripping Issue Call By Customer Name :- Ajay Mobile No :-9958214785 | Open | ESQUIRE TECH.. | Vidyut Engineers - New Delhi |  | Cancelled-Approved by ASM | Cancelled | Kapil Solanki
6 | WEST | 211806888 | 2025-10-03 15:19 | 125 | 4H.8052.C4../2520030 | Air lock issue | Closed | Malabar Gold. . | Transcreek Engineers Pvt. Ltd. - Panvel | 0.4 | Metal particals found in NRV suction line , clean the NRV and check , NRV working properly so refitted it . | Closed
33 | NORTH | 211806760 | 2025-10-03 15:00 | 250 | F6.8842.C4../2520005 | Starting Issue And ECU Amber Lamp Change Alarm Call By Customer Name :- Sher singh Mobile No:-8477942701 | Closed | K.G.N. Cold Storage | Deep Jyoti Electricals and Services - Bareilly | 114 | Low def level topup the def clear the code then issue resolve | Closed | Sudhir Awasthi
37 | South Zone | 211806705 | 2025-10-03 14:53 | 40 | 3H.8951.../2420257 | Fuel Leakage from DG,dg oil lekage -517750 | Open | ICICI Bank Limited | Powerlinks Infra Tech Pvt Ltd - Khammam | Cancelled | Cancelled | Cancelled | Mr. MD Saleem
18 | NORTH | 211806679 | 2025-10-03 14:44 | 750 | DV2.8501.C4../2420052 | Starting Issue Call By Customer Name :Fuleshwar Sir Number :8130181206 | Task Start | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 8 | self starter not working then self starter dismentle and check Direct with battery but self starter not working need to be repair or replace | open | Kapil Solanki
25 | South Zone | 211806595 | 2025-10-03 14:18 | 5.5 | CC1.1013.../2400231 | Frequency Issue. Call By customer. Name:-Gagan Mobile No.:-8867485919 | Task Start | SKY ENTERPRISES | KALA Care Global LLP - Belagavi | 14 | MPU wire Cut, corrected the same | Closed | Mr. Anil Kumar H G
48 | South Zone | 211806563 | 2025-10-03 14:14 | 250 | F6.8842.C4../2420105 | Leakage Issue | Closed | SRI ASHWIN MAHAL SRI KUMARAN HALL | Electro Controls-Coimbatore 2 | 11 | Visited the site observed the fuel leakage from fuel return pipe side so retighted the same ofter started the engine fuel leakage arrested Engine running performance normal | Closed | Mr. Sanjaimon S
19 | NORTH | 211806543 | 2025-10-03 14:10 | 750 | DV2.8501.C4../2420173 | INSTANCE ID :-100789729 SITE ID :-INUW080079 CALL BY CUSTOMER// DG ISSUE :-DG ALARM PROBLEM NAME :- KARAN SHARMA NUMBER :-7906702750 | Closed | Vodafone | R K Engineers - Meerut | 151 | 4 number injector wiring male female connector proper joint with pvc tap and canopy door lock adjust | Closed | Sudhir Awasthi
2 | East | 211806539 | 2025-10-03 14:09 | 15 | GP3.8501.../2422013 | Mobil Leakage issue Call by customer Name:Yuvraj yadav Number:919546260175 | Task Start | DILIP KUMAR SAHA | Globalline India Services Private Limited - Purnia | 144 | Visit pending | OPEN | Prabhakar Kumar
20 | NORTH | 211806553 | 2025-10-03 14:09 | 20 | GP3.8601.../2320039 | Battery Issue Call BY Customer Name :- Mohmmad Wali No :- 9128000020 | Task Start | Mohammad Wali | Vidyut Engineers - Noida | 1389 | Found no any issue in DG | Closed | Kapil Solanki
17 | NORTH | 211806553 | 2025-10-03 14:09 | 20 | GP3.8601.../2320039 | Battery Issue Call BY Customer Name :- Mohmmad Wali No :- 9128000020 | Task Start | Mohammad Wali | Vidyut Engineers - Noida | 1389 | Customer raised complaint as battery issue but no such issue found in DG,run DG for 30 minutes & start/Stop multiple times,red lamp alarm occurred without any code so reset the same & resolve the Issue | Closed | Kapil Solanki
21 | NORTH | 211806551 | 2025-10-03 14:08 | 57 | T4.8941.../2320053 | Starting/Stopping Issue | Task Start | Shivalik Hospital | Paluck Technologies Ltd. - Faridabad | 139 | SPN/FMI 157/14, 2802/4 Clear the DTC then issue resolve trail on load found no any issue | Closed | Kapil Solanki
18 | NORTH | 211806519 | 2025-10-03 14:01 | 200 | 6H.8435.../2420244 | Starting Issue Call By Customer Name:-Vikas Pathania No:-8595901440 | Task Start | RELIANCE PROJECTS & PROPERTY MANAGEMENT SERVICES LIMITED | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki
10 | South Zone | 211806522 | 2025-10-03 14:01 | 25 | GP3.8702.../2421956 | Alarm problem Call by : Customer Name :Shaji Contact :8157803753 | Task Start | THAMARAKULAM KALLUR MUSLIM JAMA ATH | Electro Controls - Mavalikara | 15 | 2791/18, 5838/1 flash the ECU. Issue resolved | Closed | Mr. Sanjaimon S
29 | South zone | 211806409 | 2025-10-03 13:48 | 25 | GP3.8702.../2421497 | AMF Panel Problem Call by : Customer Name :Peddi Reddy Narayana Reddy p Contact :9686652225 | Closed | Peddi Reddy Narayana Reddy p | Surya Power Services - Kalyan Nagar | 44 | auto mode issue due to control panel sensing wiring issue so rectified the issue and tested on auto mode engine running in normal conditions. Also checked oil coolant belt battery distilled water wiring harness are normal. | Closed | Mr. Anil Kumar H G
7 | WEST | 211806466 | 2025-10-03 13:45 | 30 | 3H.8902.../2421750 | Starting Issue Call By Service Dealer Name :- Rushikesh Mobile No :9960098075 | Closed | SHREE SADGURU BUILDERS & DEVELOPERS | Transcreek Engineers Pvt. Ltd. - Wadkhal | 1 | controller 1 and 2 pin connection found loose so tight the connection | Closed
34 | NORTH | 211806425 | 2025-10-03 13:34 | 750 | DV2.8501.C4../2420003 | Starting/Stopping Issue | Closed | BHABANI COLORS PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Alwar | 234 | Coolant level low topup the 8lit coolant, Low electrolite level topup the electrolite after that issue resolve | Closed | Gourav Sharma
12 | WEST | 211806357 | 2025-10-03 13:22 | 200 | 6H.8435.../2420035 | Coolant Leakage Issue Call By Customer Name:-Virendra Kumar No:-9725270303 | Task Start | Ashish Brass Components Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Jamnagar | 64 | The coolant in the reservoir tank was above the H level, so the coolant overflowed from the tank, SE drained some amount of coolant. Apart from this, no problems were found on the site. | Closed | Amit sandlya
19 | NORTH | 211806337 | 2025-10-03 13:15 | 20 | GP3.1021.../2420470 | INSTANCE ID :-100784739 SITE ID :-I-UE-GKPR-ENB-G013 CALL BY CUSTOMER// DG ISSUE :-DG STARTTING PROBLEM NAME :- ASHWIN KUMAR NUMBER :-8299599398 | Open | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur |  | Visit pending | open | Sudhir Awasthi
3 | South Zone | 211806217 | 2025-10-03 12:58 | 0 | DV0.8501.C4../2420165 | Oil hose replacement | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Oil hose missing in engine. | Closed | Mr. NandhaGopal
32 | South zone | 211806141 | 2025-10-03 12:55 | 10 | GP3.8301.../2420596 | Starting Problem Call by : Customer Name : Mukunda Contact : 9154395264 | Closed | karur vysya bank | Ultimate Power Source - Kadappa | 1 | engine starting not working battery discharged removed the battery service center and charging | Closed | Mr. NandhaGopal
47 | South Zone | 211806119 | 2025-10-03 12:54 | 20 | GP3.8601.../2420920 | Genset Trip | Closed | Manoj Vaibhav Gems N. Jewellers Ltd. | Laxmi Diesels - Srikakulam | 167 | Inspected the DG and found that the engine tripping was due to an unequal load distribution. After that shared the equal load and advised to customer how to maintain it to prevent further engine tripping and also ensure that customer distribute the load equally to avoid any future issues. | Closed | Mr. MD Saleem
37 | North | 211806134 | 2025-10-03 12:52 | 250 | F6.8841.../2420072 | Starting issue Call By Customer Name :-Gautam Mobile No :-7052442465 | Open | A. P. Concast | SAAN Royal Power Solutions Private Limited - Zirakpur | 84.36 | Visit Pending | Open | Ved Prakash Gupta
29 | South Zone | 211806078 | 2025-10-03 12:45 | 15 | GP3.8501.../2420142 | Coolant Lekage Issue Call By Customer Name :- Samir . Mobile No :- 9986177785 | Task Start | Ashwini Hospital. | KALA Care Global LLP - Hospet | NA | Visit pending | Task Start | Mr. Anil Kumar H G
20 | NORTH | 211806039 | 2025-10-03 12:36 | 20 | GP3.1021.../2420275 | INSTANCE ID:-100777774 SITE ID:- I-UE-FZAD-ENB-0186 CALL BY CUSTOMER// DG ISSUE:- DG STARTING /SMOKING ISSUE NAME:- Madan NUMBER:- 9621704752 | Open | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Faizabad | 1334 | as per customer 's complaint ,we attend the site and found that DG trip due to high temperature and v belt broken so change the v belt. Engine oil level found too below from the low level. Engine oil found fully burnt.Service has been done of this asset & DG running fluently on site | Closed | Sudhir Awasthi
38 | North | 211805977 | 2025-10-03 12:27 | 320 | F6.8802.../2420325 | Trip_Genset_High_Voltage | Task Start | Ekam Elite Realtors | Megatron Engineers - Amritsar | 4 | DG tripping issue with Gen Over Voltage alarm due to DG producing high voltage (274 V per phase) so reduce the same to 239 V per phase & run the DG,Issue resolved | Closed | Ved Prakash Gupta
11 | WEST | 211805974 | 2025-10-03 12:25 | 58.5 | T4.8941.../2520384 | Tripping issue Called by customer Name : Ganesh Number : 9011031395 | Closed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 1 | Customer use external fuel tank , do not use kirlokar tank , so as per customer requirement change the parameter , fuel level disable. | Closed
10 | WEST | 211805948 | 2025-10-03 12:22 | 160 | 6H.8475.../2420135 | Phase issue Call By Customer Name :- Vijay Mobile No:-8788422579 | Closed | V. R. Pawar Sarees. | Mahalaxmi Diesels - Solapur | 45 | No issue with dg. | Closed
2 | South Zone | 211805921 | 2025-10-03 12:15 | 20 | GP3.8601.../2420183 | Automatically changa manual mode in Genset.. | Completed | Thogai Murugan Builders | Bharath Diesel Sales and Service - Karur | 147 | Checked engine automatic change the manual mode so check the EB line linked in R And Y phase so correct the EB line in customer scope,start the engine some times error code found SPN 2791 FMI 14 and SPN 2802 FMI 4 so As per Kirloskar AO instructions Flash the R550 CPCB IV+ 20 KVA | Closed | Mr. NandhaGopal
9 | WEST | 211805917 | 2025-10-03 12:13 | 30 | 3H.8902.../2420180 | Coolant Leakage Problem Call by : Customer Name :Rajesh Contact :7708341090 | Task Start | L & T CONSTRUCTION. | Transcreek Engineers Pvt. Ltd. - Boisar |  | Radiator found broken , so customer repair it , | Closed
8 | WEST | 211805836 | 2025-10-03 12:00 | 125.4 | 4H.8042.C4../2420771 | Red Lamp Alarm Issue Call By Customer Name :- Mr. Narasinha Mhetre Mobile No :-8308753600 | Closed | Rani Laxmibai Mulinchi Sainiki Shala & Jr. College | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 29 | Adblue level low so top up adblue. | Closed
3 | East | 211805820 | 2025-10-03 11:58 | 125.4 | 4H.8042.C4../2420945 | Preventew MAintance And Error Code Issue Call by Customer Name NO: | Task Start | Nexgen. | HACS Engineering and Tech Private Limited - Ranchi | 52 | Low DEF level alarm SPN: 1761,FMI: 16 and ECU flt 516166 alarm, so cleared the code issue resolved | CLOSED | Prabhakar Kumar
13 | WEST | 211805784 | 2025-10-03 11:52 | 125.4 | 4H.8042.C4../2420840 | Starting Issue Email By KGD Name:-Harshad patel | Cancelled | DHANUSHYA INFRACON PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Mahesana |  | Cancelled | Closed | Amit sandlya
46 | South Zone | 211805667 | 2025-10-03 11:29 | 160 | 6H.8475.../2420111 | Belt failure | Closed | KVR AUTOMALL PRIVATE LIMITED | G-Care Diesels Private Limited - Kannur | 1150 | Attended above the DG set. Checked the general condition. Replaced with engine fan belt. After adjusted fan belt tension. Start and check any abnormal sound. D G set has working found ok. | Closed | Mr. Sanjaimon S
12 | WEST | 211805664 | 2025-10-03 11:28 | 5.5 | CC1.1013.../2400192 | Starting/Stopping Issue | Closed | HOTEL AISHWARYA BIRYANI HOUSE | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 15 | Wire cutted by rat , so new wire fitted by the enginner | Closed
45 | South Zone | 211805671 | 2025-10-03 11:22 | 15 | GP3.8501.../2520183 | Red Alarm issue Call By Customer Name :-Raghu . Mobile No :-7975022191 | Closed | sri panchalingeshwara kissan seva kendra ravishankar | Surya Power Services - Mandya | 55 | Wiring loose collection tight check all engine run the engine found okay | Closed | Mr. Anil Kumar H G
44 | South Zone | 211805646 | 2025-10-03 11:21 | 5.5 | CC1.1013.../2400327 | Other-Under speed alarm | Closed | Ratnm Infra | Bharath Diesel Sales and Service - Chennai | 612 | found engine is shutdown at without load, found under Speed alarm on the controller, Found exhaust side strainer is blockage, due to this case back pressure apply on the engine then reduce the engine speed, then removed and cleaned the exhaust side strainer, | Closed | Mr. NandhaGopal
35 | NORTH | 211805591 | 2025-10-03 11:11 | 125.4 | 4H.8041.../2320043 | Leakage Issue | Closed | Trafag Controls India Pvt Limited | Paluck Technologies Ltd. - Gurgaon | 342 | Oil leakage from flywheel site | Open | Kapil Solanki
39 | North | 211805572 | 2025-10-03 11:08 | 200 | 6H.8435.../2420079 | Leakage Issue | Open | M/s Neeraj Tyagi Contractor | SAAN Royal Power Solutions Private Limited - Rohtak | 617 | SPN/FMI-1761/16 ; AdBlue level found low , Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
4 | East | 211805499 | 2025-10-03 11:03 | 15 | GP3.8501.../2420548 | Starting Problem Call by : Customer Name :Mohammed Jaffer Contact :9791064557 | Open | Shiv Sankar Diesels | Hibreed Engineering Pvt. Ltd. - Guwahati | 220 | SE is on site update pending | OPEN | Ujjwal Das
8 | East | 211805499 | 2025-10-03 11:03 | 15 | GP3.8501.../2420548 | Starting Problem Call by : Customer Name :Mohammed Jaffer Contact :9791064557 | Open | Shiv Sankar Diesels | Hibreed Engineering Pvt. Ltd. - Guwahati | 220 | SE found under speed alarm after sometime of DG operation so he disable the MPU and activated by the alternator then found ok, need visit for proper inspection of loose connection | OPEN | Ujjwal Das
23 | South Zone | 211805494 | 2025-10-03 11:00 | 30 | 3H.8902.../2420966 | Automation Issue Call By Customer Name :- Mallikarjuna Mobile No :- 8217032405 | Task Start | Pampapathi | KALA Care Global LLP - Ballari | 257 | Mains unhealthy supply from EB , clear the issue and clear the all alarms and DG running is working under good condition.. | Task Start | Mr. Anil Kumar H G
38 | South Zone | 211805490 | 2025-10-03 10:59 | 250 | F6.8842.C4../2420022 | AMF panel problem Call by : Customer Name : Girish Contact : 9948977010 | Task Start | Adishwar Auto Diagnostics Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 122 | As per customer complaint auto connections not connecting by customer end and EB cables three core available but required 4 core so advise this customer to kindly replace the cable immediately... | Closed | Mr. MD Saleem
22 | NORTH | 211805311 | 2025-10-03 10:52 | 25 | GP3.8702.../2421212 | Starting/Stopping Issue | Closed | KOREA ENGINEERING AND CLEAN TECHNOLOGY CO INDIA [P] LTD | Vidyut Engineers - Noida | 120 | SPN/FMI 2791/18 flash the file then issue resolve | Closed | Kapil Solanki
43 | South Zone | 211805022 | 2025-10-03 10:42 | 5.5 | CC1.1013.../2400084 | Starting Problem Call by : Customer Name :Sajeesh Contact :7736874116 | Closed | EMPOWER | Bharath Diesel Sales and Service - Karappakkam | 129 | Visit the site checked the generator event log found under speed tripping showing in the controller and adjust the factory settings for 3050RPM and run with load found normal.checked the oil level found normal checked the Fuel filter condition found normal. Started the generator run with load found normal. | Closed | Mr. NandhaGopal
14 | WEST | 211805018 | 2025-10-03 10:41 | 750 | DV2.8501.C4../2420116 | KRM NOT WORKING | Closed | GALAXY SURFACTANTS LIMITED | Unique Techno Services Pvt Ltd. - Ankleshwar | 6.17 | KRM was not capturing data correctly so replaced it. | Closed | Amit sandlya | Failed Part
15 | WEST | 211805033 | 2025-10-03 10:39 | 750 | DV2.8501.C4../2420070 | KRM NOT WORKING | Closed | Galaxy Surfactants Limited. | Unique Techno Services Pvt Ltd. - Ankleshwar | 5.5 | KRM was not capturing data correctly so replaced it. | Closed | Amit sandlya
16 | WEST | 211805005 | 2025-10-03 10:37 | 750 | DV2.8501.C4../2420164 | KRM not working | Closed | GALAXY SURFACTANTS LIMITED | Unique Techno Services Pvt Ltd. - Ankleshwar | 9.17 | KRM was not capturing data correctly so replaced it. | Closed | Amit sandlya
21 | South zone | 211804978 | 2025-10-03 10:34 | 25 | GP3.8702.../2420647 | Starting Problem Call by : Customer Name :Thomas PO Contact :9447328506 | Closed | Star Tyres. | G-Care Diesels Private Limited - Ernakulam | 6 | error code found SPN 97 FMI 5 , WATER IN FUEL, clear error code | Closed | Mr. Sanjaimon S
23 | NORTH | 211804970 | 2025-10-03 10:30 | 500 | DV8.8501.C4../2320052 | Tripping issue Call By Customer Name :-Lalit Kumar Number:- 9999286305 | Closed | NATIONAL TRUST FOR THE HANDICAPPED | Vidyut Engineers - New Delhi | 7 | Generator reverse power alarm | open | Kapil Solanki
21 | NORTH | 211804964 | 2025-10-03 10:28 | 20 | GP3.8601.../2520129 | Automation Issues And Fuel Consumption Issue Call By Customer Name :- Bijin Mobile No:-8447314401 | Closed | Modern Constructions | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | Mains sensing wire connection found loose in pannel so connected the same & resolve the Auto starting issue | Closed | Kapil Solanki
45 | North | 211804911 | 2025-10-03 10:14 | 50 | T4.8941.../2420878 | Starting/Stopping Issue | Closed | JUBILANT FOOD WORKS LIMITED | SAAN Royal Power Solutions Private Limited - Ambala | 274 | Starting issue due to 2A & 2C wire found loose on Relay (at 12RB1 from mains supply) so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
13 | WEST | 211804881 | 2025-10-03 10:09 | 25 | GP3.8702.../2421323 | Automation Issue Call By Customer Name :- Sanket . Mobile No 9561843880 | Closed | Kanifnath Enterprises.. | KALA Care Global LLP - Ahmednagar | 295 | SPN 2791 FMI 18 ( ECU Inducement ) Engine Exhaust Gas Recirculation , check connection found ok connect ikonnect and clear error code. | Closed
40 | North | 211804755 | 2025-10-03 09:56 | 15 | GP3.8501.../2421370 | Starting issue Call By Customer Name :- Nihal Singh Mobile No:-8413089770 | Open | BHARAT GENERAL STORE | Suraj Motor Store - kathua |  | Visit Pending | Open | Ved Prakash Gupta
42 | South Zone | 211804683 | 2025-10-03 09:44 | 125.4 | 4H.8042.C4../2520067 | Genset Trip | Closed | BMH Care Hospital Limited | G-Care Diesels Private Limited - Ernakulam | 4 | Customer side load issue | Closed | Mr. Sanjaimon S
22 | South Zone | 211804670 | 2025-10-03 09:36 | 15 | GP3.8501.../2420360 | Starting Problem Call by : Customer Name :Liji Contact :7736044493 | Task Start | Mr. Jayapalan. | G-Care Diesels Private Limited - Thrissur | 19 | Attended the site checked DG with the presence of customer representative, found low battery charge,so removed the battery and bring it to the tata green battery shop for test report. | Task Start | Mr. Sanjaimon S
36 | NORTH | 211804645 | 2025-10-03 09:33 | 320 | F6.8802.../2320057 | Starting/Stopping Issue | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 319 | SPN/FMI 168/3, 520527/16, 4365/2 Check the panel wiring found all ok, then check the WIF sensor connector found Red & Black wire voltage- 26v, Red & Grey 6v then check Black to grey 20v | open | Kapil Solanki
22 | NORTH | 211804661 | 2025-10-03 09:28 | 25 | GP3.8702.../2421414 | Current issue Call By Customer Name :- Shiv Singh Mobile No:-8858571492 | Task Start | CRYSCON INFRA PVT LTD | Paluck Technologies Ltd. - Faridabad | 425 | Control pannel MCB neutral wire connector found defective so replace the same & resolve the Issue | Closed | Kapil Solanki | Failed Part
41 | South Zone | 211804615 | 2025-10-03 08:52 | 320 | F6.8802.../2420166 | Genset Trip | Closed | SURYA VASTHRALAYAM PRIVATE LIMITED | G-Care Diesels Private Limited - Kannur | 108 | Visited above the site customer complained about high temperature check coolant level belt condition and temperature sensor connector found engine side working normal condition. Found hot air duct not provided at site and discussed with ASE Godson and informed customer to provide hot air duct | Closed | Mr. Sanjaimon S
28 | South Zone | 211804592 | 2025-10-03 07:45 | 25 | GP3.8702.../2421229 | Load Issue Call By Customer Name :- Bandayya swami Number :- 9380640995 | Task Start | THE RAICHUR AGRICULTURAL PRODUCE MARKETING & PROCESSING CO-OPERATIVE SOCIETY LIMITED | KALA Care Global LLP - Hospet | NA | Visit pending | Task Start | Mr. Anil Kumar H G
23 | NORTH | 211804538 | 2025-10-03 06:51 | 160 | 6H.8475.../2420025 | Trip Issue & Display Showing wrong details. Call By Customer Name :- Mustak No :- 9058614379 | Task Start | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki
13 | South Zone | 211804277 | 2025-10-03 01:28 | 200 | 6H.8435.../2420129 | Starting Issue Call By Customer Name :- Satish Kumar No :- 9940545076 | Task Start | MANGO HILL HOTELS | Electro Controls-Coimbatore 2 | 12 | Visited the site found the error code (4225/1) on the display tempering Grp warning.Removed the NOx sensor, cleaned it and refitted it.After starting the engine, observed that the error code had disappeared.However checked the battery terminal voltage, it showed around 11.5V.After connecting the charging alternator the voltage at idle condition was 21.4V.We need to check the condition of the charging alternator and take a decision accordingly. charging alternator will be replace | Task Start | Mr. Sanjaimon S
18 | WEST | 211805845 | 2025-10-03 | 125 | 4H.8042.C4../2420055 | CC SR | Task Start | Vande Mataram Vidyapeeth | Unique Techno Services Pvt Ltd. - Surat | LR | SPN/FMI- 520528/31(Inducement related DM2) DG started but after some time stopped due to the above error code. Tightened all the wire connections of relay board and refited the ignition relay wire. Now DG is running smoothly. | OPEN | Amit sandlya
1 | North | 211803940 | 2025-09-03 17:48 | 20 | GP3.1021.../2420389 | INSTANCE ID:-100784748 SITE ID:-I-UE-ABDD-ENB-0950 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-SHARAD KUMAR NUMBER:-8887532150 | Open | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad | 152 | Relay card replaced ; UpdatePending | open | Sudhir Awasthi
1 | North | 211803931 | 2025-09-03 16:37 | 57 | T4.8941.../2420122 | Maintenance due alarm aarha lekin service hi gye | Open | Bansal Children Hospital | Pratap Diesels Pvt. Ltd. - Bhiwadi | 374 | Found Maintenance due alarm, reset the alarm after issue resolve | Closed | Gourav Sharma
17 | South Zone | 211803930 | 2025-09-03 16:32 | 500 | DV8.8501.C4../2420224 | line rejection | Task Start | Family Wedding Centre | G-Care Diesels Private Limited - Malappuram | LR | DG not starting, found wire loose in interface box, also final filter not working so change the filter, DG running OK | Closed | Mr. Sanjaimon S
1 | East | 211803927 | 2025-09-03 16:31 | 82.5 | 5H.8901.../2420562 | Starting and tripping Issue Called by Customer Name: Aniket No: 7462011929 | Task Start | KALYAN JEWELLERS INDIA LTD | Globalline India Services Private Limited - Patna | 99 | DG starts sometime and sometime fail to start showing underspeed / no alarm or fault code, so SE checked fuel line properly but the same issue and then byepass the primary filter but same problem so, connected IKonnect found Common rail Pressure OK, and on overriding it observered that controllers show value of DEF and all other paramets value some time so Checked Ignition relay found 12 V at relay 4 no. wire which was Ok then Check Contiuity of its switch oint which was not Ok so it found that the IGNItion relay faulty after replacing it issue resolved. | CLOSED | Prabhakar Kumar
17 | WEST | 211803903 | 2025-09-03 15:47 | 15 | GP3.8501.../2421273 | UBDER SPEED ALARAM CALL BY CUSTOMER NAME-HIRENDRA NUMBER-9726148090 | Cancelled | Maa Shakti Petroleum. | Unique Techno Services Pvt Ltd. - Baroda |  | Cancelled | Closed | Amit sandlya
50 | South | 211803900 | 2025-09-03 15:39 | 200 | 6H.8435.../2420074 | Starting/Stopping Issue | Task Start | MS. Power Systems | Surya Power Services - Bangalore | 43.21 | observe the abnormal sound through v belt, retight the v belt tension | Closed | Mr. Anil Kumar H G
5 | East | 211803890 | 2025-09-03 15:23 | 40 | 3H.8951.../2420018 | Starting Issue Email By KGD Name:-SUNRISE POWER | Task Start | R. K. Dayal Nursing Home & Resarch Center. | Globalline India Services Private Limited - Muzaffarpur | 95 | SE visited and found Emergency switch alarm so checked and found emergency switch was pressed | CLOSED | Prabhakar Kumar
41 | North | 211803883 | 2025-09-03 15:09 | 30 | 3H.8902.../2421995 | Genset Trip | Task Start | THE CLASSIC ESTATE | Suraj Motor Store - Srinagar | 94.25 | Visit Pending | Open | Ved Prakash Gupta
42 | North | 211803882 | 2025-09-03 15:07 | 20 | GP3.8601.../2421115 | Electrical Problems | Task Start | HILAL BAKERY.. | Suraj Motor Store - Srinagar | 32 | Visit Pending | Open | Ved Prakash Gupta
2 | North | 211803856 | 2025-09-03 14:20 | 40 | 3H.8951.../2421296 | Starting Issue. Call By Customer. Name:-Vishal Diwan Mobile No.:-9235777777 | Open | Vishal Dewan | Espiem Engines & Machines (P) Limited - KANPUR |  | Under Cancellation | Cancelled | Sudhir Awasthi
49 | South | 211803818 | 2025-09-03 12:58 | 25 | GP3.8702.../2420120 | Preventive Maintenance Call by : Customer Name : Dr.Jyothi Rani Contact : 9493815959 | Open | Jyothi Hospital. | Powerlinks Infra Tech Pvt Ltd - Madinaguda | NA | Visit pending | Open | Mr. MD Saleem
2 | North | 211803771 | 2025-09-03 12:09 | 20 | GP3.8601.../2520120 | Tripping issue Called by customer Name : GEETANSH Number : 8949104180 | Task Start | Vishwakarma Auto Parts Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 3 | Unbalance load, Balance the load after that issue resolve | Closed | Kapil Solanki
3 | North | 211803741 | 2025-09-03 11:25 | 58.5 | 6H.9840.../2420005 | Red Lamp ON Alarm Issue Call By Customer Name :- Ravindar Mobile No :- 9811211463 | Task Start | Rathoure Metal Smelting | Paluck Technologies Ltd. - Faridabad | 43.38 | Starting Issue due to Battery Voltage found low during cranking(6V) ; battery replaced | Closed | Kapil Solanki
48 | South | 211803739 | 2025-09-03 11:23 | 15 | GP3.8501.../2420593 | Starting Problem &Alarm Problem Call by : Customer Name :HABEEB Contact :9544469935 | Open | SMILE HYPERMARKET | G-Care Diesels Private Limited - Kannur | NA | Visit pending | Open | Mr. Sanjaimon S
3 | North | 211803733 | 2025-09-03 11:01 | 82.5 | 5H.8901.../2320078 | Battery Issue. Call By Customer. Name:-Shoukit Khan Mobile No.:-7827824447 | Task Start | Pragya Components Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 750 | Battery issue, One cell not showing the gravity | open | Kapil Solanki
6 | East | 211803715 | 2025-09-03 10:07 | 15 | GP3.8501.../2421464 | Mobil Leakage Issue Call By Customer Name :- Ram Kumar Mobile No :- 9693244802 | Task Start | M.S Interprices | Globalline India Services Private Limited - Biharsharif | 133 | No issue in DG need to cancel SR | CANCELLED | Prabhakar Kumar
43 | North | 211803705 | 2025-09-03 09:40 | 82.5 | 5H.8901.../2420804 | Under Speed Alarm Issue Call By Customer Name :-Naveen Mobile No :- 8222894142 | Open | FAIRMOUNT HOTELS PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Sonipat | 1164 | Under Cancellation-ServiceDue | Cancelled | Ved Prakash Gupta
12 | South zone | 211803703 | 2025-09-03 09:23 | 25 | GP3.8702.../2421569 | Starting/Stopping Issue | Task Start | Malabar Petroleum | G-Care Diesels Private Limited - Calicut | 38 | Battery voltage low, fiited the float battery, | Closed | Mr. Sanjaimon S
47 | South | 211803428 | 2025-08-03 22:27 | 125.4 | 4H.8042.C4../2421129 | Genset Trip | Open | ST JOSEPHS CHURCH | Prasad Power Engineers - Udupi | NA | Visit pending | Open | Mr. Anil Kumar H G
45 | South zone | 211803401 | 2025-08-03 20:27 | 20 | GP3.8601.../2421626 | Starting issue And supply issue Call by customer Name:SELVAM SELVAM Number:9029398604 | Closed | ALAGARMALAIYYAN ENTERPRISES | Bharath Diesel Sales and Service - Tiruchirappalli | 34 | Starting Problem Checked Found Red Lamp On Alarm Emergency Switch Activated Due to Emergency Switch 11B Wire Connector Side Remove Condition So Engine Trip, 11B Wire Reconnected and Tightened, All Wire Connection Tightened, Started the Engine Running Performance ok, Output Voltage Normal, Safety Checking and Load on Checked ok, | Closed | Mr. NandhaGopal
46 | South | 211803124 | 2025-08-03 17:44 | 30 | 3H.8902.../2421509 | Inspection/Maintenance | Open | Badri Menz Fashion | KALA Care Global LLP - Hospet | NA | Visit pending | Open | Mr. Anil Kumar H G
1 | North | 211803082 | 2025-08-03 17:30 | 45 | 3H.8951.../2420204 | oil sensor issue meter sensor issue and rusting issue call by customer name:J P Chaudhary number:9461177331 | Task Start | J P AYURVEDA AND PANCHKARMA HOSPITAL | Pratap Diesels Pvt. Ltd. - Sri Ganganagar | 20 | Fuel level not proper show fuel percentage variation then check the resistance, when 19%-25% fuel then show 150-165 Ohm, then check the wiring found ok then change the new sensor found same problem then check the directly in controller then issue was same then check with another controller found ok then issue resolve | Closed | Gourav Sharma
44 | South zone | 211803071 | 2025-08-03 17:23 | 20 | GP3.8601.../2420754 | Under Speed Problem Call by : Customer Name :Mohan Contact :8489545417 | Closed | R. K. Textiles | Bharath Diesel Sales and Service - Salem | 22 | Inspected the engine error is 970/31 emergency stop error, so check the emergency not pressed emergency button ferule no 11 is loosely so retightened the cable after start and run the engine running satisfaction ok, site auto on off working properly ok | Closed | Mr. NandhaGopal
44 | North | 211802319 | 2025-08-03 16:42 | 625 | DV0.8501.C4../2420011 | high temperature and abnormal sound issue Call by customer Name:Subhash Mukharjee Number: 9813080609 | Cancelled | HILTON CONVEYORS | SAAN Royal Power Solutions Private Limited - Sonipat | 265.35 | Under Cancellation-ServiceDue | Cancelled | Ved Prakash Gupta
36 | South Zone | 211802328 | 2025-08-03 16:42 | 20 | GP3.8601.../2421997 | AIR INLET HOSE COMPLAINT | Task Start | KUMARAN TILES | Madurai Electro Controls - Rajapalayam | LR | This engine commissioning work. This engine complaint is above 30 to 40 amps to pull out the intake manifold hose. 30 to 40amps low air flow this engine to complaint. | Task Start | Mr. NandhaGopal | Load study
2 | North | 211802310 | 2025-08-03 16:39 | 5.5 | CC1.1013.../2400316 | Supply issue Called by Customer Name :Ambika prasad nayak Number:8018792160 | Task Start | SHRI TEJA ENTERPRISES | Pratap Diesels Pvt. Ltd. - BIKANER |  | Cancelled-SR opened by mistake | Cancelled | Gourav Sharma
15 | South Zone | 211802250 | 2025-08-03 16:29 | 20 | GP3.8601.../2421973 | STARTER FAILURE | Task Start | Vaishakh PK | G-Care Diesels Private Limited - Calicut | LR | Site visited for genset commissioning and after detailed inpection found that coolant level is very low in radiator and discuss the matter with power com sales team and as per their instructions 5ltr coolant filled in the radiator then checked every connection and other parameters,then started the genset but unfortunately an spark found from the starting motor and checked and found that it's stuck condition then discuss the matter with the ASM Sanja sir,and as per his instructions decided to fix a new starting motor,and before fixing starting motor just tried to rotate the engine manually,but the engine was stuck and would not rotate.And due to this situation it's unable to take further actions on site.The genset will need to be dismantled and removed for further investigation,but the customer is making issue in site,and he is requesting for replacement for a new genset, waiting for HO and OEM team decision. | Task Start | Mr. Sanjaimon S | Details required
4 | North | 211802232 | 2025-08-03 16:22 | 82.5 | 5H.8901.../2420602 | Starting Issue Call By Customer Name :-Jetendra Singh Mobile No :-7007904997 | Closed | EXCEL POWER GROUP, | S. R Engines Sales And Service - LUCKNOW | 15 | Found Emergency Switch wire was loose so, tightness the same then issue resolve | Closed | Sudhir Awasthi
45 | South | 211802212 | 2025-08-03 16:20 | 58.5 | T4.8941.../2421833 | Starting/Stopping Issue | Task Start | Jagannatha Padmavathi Conventions | Ultimate Power Source - Ananthapuramu | 3.1 | Battery level low, charging supply not given by the customer | Closed | Mr. NandhaGopal
44 | South | 211802104 | 2025-08-03 16:07 | 30 | 3H.8902.../2421522 | Starting/Stopping Issue | Open | G C INDUSTRIES | KALA Care Global LLP - Hospet | NA | Visit pending | Open | Mr. Anil Kumar H G
12 | South Zone | 211802008 | 2025-08-03 16:01 | 15 | GP3.8501.../2422051 | Trip_Genset_Low_Voltage | Task Start | SRI VENKATRAMANA TRANSPORTS | Electro Controls-Coimbatore 2 | 2.11 | Main Alternator failure suspected winding failure today Engineer remove the alternator and taken to workshop for futher investigation | Task Start | Mr. Sanjaimon S
43 | South | 211802023 | 2025-08-03 15:58 | 40 | 3H.8951.../2421767 | Starting Issue Call By Customer Name :-SURESH Mobile No :-9743122512 | Open | SURESH MADIWALAR | KALA Care Global LLP - Belagavi | NA | Visit pending | Open | Mr. Anil Kumar H G
20 | North | 211801964 | 2025-08-03 15:53 | 125.4 | 4H.8041.../2420037 | Automation Issue Call By Customer Name :- Rajeev Sharma Mobile No :-7838640263 | Open | Karuna Hospital | Vidyut Engineers - New Delhi |  | Visit Pending | Open | Kapil Solanki
21 | North | 211801947 | 2025-08-03 15:48 | 500 | DV8.8501.C4../2420105 | Controller Faulty | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 81 | Controller display found faulty so replace the same & resolve the Issue | Closed | Kapil Solanki | Mail to SD
32 | South Zone | 211801934 | 2025-08-03 15:43 | 25 | GP3.8702.../2421440 | Oil Leakage Issue Call By Customer Name :- Kiran Mobile No :- 7899119442 | Task Start | Bijapur DG Power Controls | KALA Care Global LLP - Vijayapura | 78 | Oil leakage issue found in oil filling cap side minor leakage so tighten the properly issue resolve. SR is closed manually | Closed | Mr. Anil Kumar H G
45 | North | 211801930 | 2025-08-03 15:41 | 62.5 | T4.8941.../2420176 | Starting/Stopping Issue | Closed | Murti Shri Durga Bhawani Hetuwali Trust | SAAN Royal Power Solutions Private Limited - Karnal | 9.5 | Engine crank but failed to start without any code on controller or i-koneect so flash the ECU & run the DG , Issue resolved | Closed | Ved Prakash Gupta | ECU faults
46 | North | 211801903 | 2025-08-03 15:37 | 250 | F6.8842.C4../2420079 | THROTTTLE VALVE ISSUE | Task Start | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - kathua | LR(1) | ITV was not working so replace from other DG & trial taken,Issue resolved | Closed | Ved Prakash Gupta
47 | North | 211801920 | 2025-08-03 15:36 | 40 | 3H.8951.../2420357 | AUTO STARTING ISSUE | Closed | Dr. Vineets Healtcare Centre | SAAN Royal Power Solutions Private Limited - Zirakpur | 98 | Fuel leakage found on fuel pump return line so change the washer & fuse found faulty of mains Red phase so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
15 | South zone | 211801911 | 2025-08-03 15:33 | 125.4 | 4H.8042.C4../2520073 | Error code issue | Closed | Raisha Technodesign Pvt. Ltd. | Ultimate Power Source - Hosur | 7 | Checked found battery negative connection not proper in control panel ,for the ecu communication wire. dg trip also communication fault. Corrected the wiring. Remove error code. Started the dg with load 4 hrs .found problem rectified | Closed | Mr. NandhaGopal
20 | WEST | 211801676 | 2025-08-03 14:50 | 125.4 | 4H.8042.C4../2420131 | Starting Issue Call By Customer Name :- Lxminataya ... Mobile No :- 8319389125 | Closed | M/s. Trishul Constructions | Shree Engineering Service - Satna | 499.33 | Low DEF level. | Closed | Vijay patil
42 | South | 211801637 | 2025-08-03 14:38 | 45 | 3H.8951.../2520493 | Need to Start the DG | Open | Chandana Medical Distrisutor Retail and Wholesales | Surya Power Services - Billekahalli | NA | Visit pending | Open | Mr. Anil Kumar H G
5 | North | 211801473 | 2025-08-03 14:05 | 40 | 3H.8951.../2421406 | Tripping issue Call By Customer Name :-SANJAY RANKA Number:- 9799322642 | Closed | SANJAY KUMAR RANKA & MEENA RANKA | Pratap Diesels Pvt. Ltd. - Bhilwara | 7 | Unbalance load, Educate the customer for balance the load | Closed | Gourav Sharma
1 | North | 211801405 | 2025-08-03 13:50 | 30 | 3H.8902.../2320058 | Starting/Stopping Issue | Open | ORIENT APPARTMENT | SAAN Royal Power Solutions Private Limited - Sonipat | 150.14 | Starting Issue due to 32 amp MCB found tripped so corrected the same & resolve the Issue | Closed | Ved Prakash Gupta
6 | North | 211801401 | 2025-08-03 13:48 | 30 | 3H.8902.../2320050 | Starting/Stopping Issue | Cancelled | Hindustan Fuels | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Cancelled- Problem solve in telephonic discussion | Cancelled | Kapil Solanki
41 | South | 211801380 | 2025-08-03 13:43 | 82.5 | 5H.8901.../2420320 | Starting Issue Call By Customer Name :- Yogesh Shah Mobile No :-7066731148 | Task Start | Chandukaka Saraf And Sons Private Limited | KALA Care Global LLP - Belagavi | 120 | Coolant level low, | Closed | Mr. Anil Kumar H G
22 | North | 211801358 | 2025-08-03 13:35 | 7.5 | D3.8305.../2400035 | Starting/Stopping Issue | Open | M/s. Transrail Lighting Ltd. | BSES (I) Pvt. Ltd. - Dungarpur |  | Visit Pending | Open | Gourav Sharma
7 | North | 211801287 | 2025-08-03 13:27 | 45 | 3H.8951.../2420811 | Starting/Stopping Issue | Closed | ACME ELECTRICAL & INDUSTRIAL CO | S. R Engines Sales And Service - LUCKNOW | 36 | Found Controller show the Under speed alarm, so tightness the panel wiring then isssue resolve | Closed | Sudhir Awasthi
7 | East | 211801311 | 2025-08-03 13:25 | 500 | DV8.8501.C4../2420383 | Starting/Stopping Issue | Closed | BIRAT BASUMATRY | Green Powerline - Dhemaji | 16 | SPN 3364 FMI 8, as per the DSM sheet checked the Adblue Concentration found 32.12 which found ok checked DEF tank connector voltage continuity all found ok check CAN L &H found ok also found DEF ok so cleared code issue but again found on starting so flashed ECU then issue resolved. | CLOSED | Ujjwal Das | ECU fault cjeck
4 | North | 211801292 | 2025-08-03 13:19 | 20 | GP3.8601.../2520121 | complain | Task Start | ICICI Bank | Excel Diesel Private Limited - Sultanpur | LR | Visit pending | open | Sudhir Awasthi
23 | North | 211801211 | 2025-08-03 13:00 | 400 | DV8.8542.C4../2420086 | Engine sent back | Task Start | Apollo Hospitals (Indraprastha Medical Corporation Ltd.) | Vidyut Engineers - Noida |  | Visit Pending | Open | Kapil Solanki
2 | North | 211801207 | 2025-08-03 12:59 | 58.5 | T4.8941.../2421275 | Exhaust Fan problem Call by : Customer Name : Jitendra Kumar Contact : 8187997454 | Task Start | J. P. C. Infratech Pvt. Ltd.. | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta
21 | WEST | 211801197 | 45872.5361 | 20 | GP3.1021.../2420262 | INSTANCE ID :-100750592 SITE ID :-I-MH-LOAR-ENB-G001 CALL BY CUSTOMER// DG ISSUE :-DG CONTCTOR FULT NAME :-ramkirshna Ambure . NUMBER :-9309769264 | Cancelled | Reliance Jio Infocomm Limited | Dicksons Engineering Co.Pvt.Ltd. - Akola |  | cancelled | Closed | Jagdeep Saini
40 | South | 211801110 | 2025-08-03 12:30 | 30 | 3H.8902.../2421830 | Display Issue Call By Customer Name :- Sushat Sir Mobile No :- 7022063506 | Open | NF. Power Tech Engineers | Prasad Power Engineers - Chithradurga | NA | Visit pending | Open | Mr. NandhaGopal
8 | North | 211801100 | 2025-08-03 12:26 | 20 | GP3.1021.../2420377 | INSTANCE ID :-100779502 SITE ID :- I-UE-HMPR-ENB-G003 CALL BY CUSTOMER// DG ISSUE :-DG CONTROLER FULT NAME :-dev shakti Tiwar NUMBER :-7905701384 | Open | Reliance Jio Infocomm Limited | Espiem Engines & Machines (P) Limited - Banda |  | Cancelled | Cancelled | Sudhir Awasthi
24 | North | 211801058 | 2025-08-03 12:20 | 250 | F6.8841.../2420392 | Abnormal sound issue | Closed | RAMESH KALRA | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 57 | SPN/FMI-1761/16 ; AdBlue Level found low Top-up the same & resolve the Issue | Closed | Kapil Solanki
39 | South | 211801050 | 2025-08-03 12:18 | 30 | 3H.8902.../2421321 | Hinges brocken | Task Start | Bhaskar associates | G-Care Diesels Private Limited - Calicut | 282.98 | Door hinges faulty door not working properly.so replaced hinge | Closed | Mr. Sanjaimon S
3 | North | 211801016 | 2025-08-03 12:11 | 20 | GP3.8601.../2420231 | Starting/Stopping Issue | Closed | M/s. Kuber Rice Mills | Gen Powers - PATIALA | 58 | Maintenance due alarm occurred so reset the same & top-up some battery water | Closed | Ved Prakash Gupta
43 | South zone | 211800999 | 2025-08-03 12:06 | 125.4 | 4H.8041.../2421021 | Tripping Problem Call by : Customer Name :Prasanth Contact :9894022398 | Completed | Anuradha Jewwllery Palace | Ultimate Power Source - Krishnagiri | 93 | Check the engine. Adbule level low. Refiled the adbule. After that started the engine running ok. | Closed | Mr. NandhaGopal
4 | North | 211800900 | 2025-08-03 11:47 | 50 | T4.8941.../2423319 | AC Alternator Faulty | Task Start | BHARTI AIRTEL LTD. | SAAN Royal Power Solutions Private Limited - Sonipat | 1.3 | DG Alternator load cable found loose & smoke comes out from alternator so tightened the same & run the DG on for 1 hour,No Issue found | Closed | Ved Prakash Gupta
42 | South zone | 211800854 | 2025-08-03 11:35 | 58.5 | T4.8941.../2520015 | Error code | Closed | Rathnaa Reliable Foods | Bharath Diesel Sales and Service - Dharmapuri | 1 | Attend the site start the DG,Alarm mid lamp on.. Error codes is spn 97 FMI 5 P2265 alarm is water in fuel self test and another alaram is Spn 5838 FMI 1 P106A alarm is Egr valve malfunction warning alarm..Both alarm is DG running time only.off the DG.check Fuel tank any water form .No water formed in fuel tank | Closed | Mr. NandhaGopal | Under Observation
9 | North | 211800848 | 2025-08-03 11:34 |  | 3H.8902.../2520063 | line rejection | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-2 | V-belt Loose adjust the belt | Closed | Gourav Sharma
5 | North | 211800840 | 2025-08-03 11:32 | 125.4 | 4H.8042.C4../2420601 | Code Issue SPN : 516166 P1047 ECU fit | Task Start | Bindal Cotex Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 39.55 | SPN/FMI-516166/0 & 1761/16 ;AdBlue Level found low so top-up the same & remove the code | Closed | Ved Prakash Gupta
38 | South | 211800742 | 2025-08-03 11:03 | 250 | F6.8841.../2420192 | Starting issue Call By Service Dealer Name :- Indumati Mobile No :-8925873034 | Task Start | DWARAKA ENGINEERINGS | Bharath Diesel Sales and Service - Chennai | 169 | Low def level, educate the customer to maintain the def level | Closed | Mr. NandhaGopal
37 | South | 211800646 | 2025-08-03 10:49 | 30 | 3H.8902.../2421392 | ENGINE NOT STARTING | Task Start | ATC Telecom Infrastructure Private Limited | Laxmi Diesels - Rajahmundry | LR-14 | observed dg not starting due to battery failure,so removed failure battery and fitted flot battery and checked dg starting ok..sent battery for workshop for checking | Task Start | Mr. MD Saleem
3 | North | 211800569 | 2025-08-03 10:46 | 15 | GP3.8501.../2421278 | Preventive Maintenance Call By Customer Name :- Arvind .. Mobile No :- 9580962108 | Task Start | M/S GIRISH SINGH | S. R Engines Sales And Service - Mau |  | Cancelled-Commercial Decision / FOC | Cancelled | Sudhir Awasthi
41 | South zone | 211800551 | 2025-08-03 10:40 | 200 | 6H.8438.C4../2420073 | Ad blue Error Problem Call by : Customer Name :Nandhakumar Contact :8072062382 | Closed | SHANMUGAM SURESH BABU | Ultimate Power Source - Vellore | 3 | Addblue level low and top up the addblue and coolant leakage arrested and all clamp and hoses condition checked , engine running condition is normal | Closed | Mr. NandhaGopal
6 | North | 211800537 | 2025-08-03 10:35 | 57 | T4.8941.../2320183 | Terminal block faulty | Open | TECHNOCRAT MOULDINGS PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 206 | R-Phase under Voltage alrm occurred due to at A C Alternator R phase terminal block found faulty so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
5 | North | 211800462 | 2025-08-03 10:25 | 5.5 | CC1.1013.../2400528 | Starting/Stopping Issue | Task Start | AARUSHI CONSTRUCTION | Pratap Diesels Pvt. Ltd. - BIKANER | 460 | Update Pending | open | Gourav Sharma
1 | South zone | 211800441 | 2025-08-03 10:17 | 125.4 | 4H.8042.C4../2420804 | error code problem | Closed | ASIA MATCH COMPANYPLIMITED (UNIT : MEENASANKAR MATCH INDUSTRIES ) | Madurai Electro Controls - Sivakasi | 20 | 516166 -1 error code show and clear the error not responding in ECU so flash the ECU and now no error | Closed | Mr. NandhaGopal
14 | South zone | 211800436 | 2025-08-03 10:14 | 15 | GP3.8501.../2421503 | Genset Trip | Closed | Kumaran Metal Store | Bharath Diesel Sales and Service - Puducherry | 6 | battery voltage coming unit reset after dg start stop working ok DG started and tested on load DG performance is normal | Closed | Mr. NandhaGopal
19 | WEST | 211800367 | 2025-08-03 09:57 | 5.5 | CC1.1013.../2400679 | Oil Leakage issue Email by KGD Name - Poonam Shedage | Task Start | Accurate Powertech India Private Limited . | Shree Engineering Service - Raipur | 150.28 | Oil leakage from cylinder head gasket.CC Date- 05-03-2025 & A check open. | Closed
7 | North | 211800372 | 2025-08-03 09:47 | 58.5 | T4.8941.../2420763 | Starting/Stopping Issue | Closed | Kamal Nursing Home | SAAN Royal Power Solutions Private Limited - Rohtak | 2 | Update Pending | Open | Ved Prakash Gupta
25 | North | 211800351 | 2025-08-03 09:42 | 750 | DV2.8501.C4../2420016 | Display Issue Call By Customer Name :- Shubham Chauhan Mobile No :- 7557360832 | Task Start | Jai Mata DI. Generator Service | Vidyut Engineers - Noida |  | Visit Pending | Open | Kapil Solanki
4 | North | 211800280 | 2025-08-03 09:06 | 320 | F6.8802.../2320078 | Leakage Issue | Closed | Solanki Hospital | Pratap Diesels Pvt. Ltd. - Alwar | 192 | found heavy oil leakage from oil filter checked and found oil filter threads difective because after opening the oil filter found filter open with adaptor so, re-fitted adaptor and tighten properly replaced oil filter and top up oil in sump 20 liter upto Max level after trail on load then found ok | Closed | Gourav Sharma
26 | North | 211800304 | 2025-08-03 09:05 | 58.5 | T4.8941.../2420591 | Leakage Issue | Closed | Nidhi Enterprises. | Paluck Technologies Ltd. - Faridabad | 249 | Oil Sump dipstick found outside the sump & Canopy door was not getting close properly so fixed them & resolve the Issue | Closed | Kapil Solanki
27 | North | 211800273 | 2025-08-03 08:24 | 30 | 3H.8902.../2320159 | Starting/Stopping Issue | Closed | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 245 | Starting Issue due to wiring found loose in control pannel on starting Relay so connected the same & resolve the Issue | Closed | Kapil Solanki
1 | South | 211695635 | 2025-08-02 11:09 | 125.4 | 4H.8041.../2420893 | Line Rejection | Task Start | Robust Electric.... | G-Care Diesels Private Limited - Ernakulam | LR | Attended the site, DG works not completed for commissioning. Neutral earthing not provided. Exhaust piping not fitted. Diesel not available and diesel tank cap not removing due to key mismatch. Instructed customer and supplier representative to complete all these works and then inform for commissioning | Task Start | Mr. Sanjaimon S
36 | South | 211799631 | 2025-07-03 21:42 | 25 | GP3.8702.../2421539 | AUTOMECTION ISSUE CALL BY CUSTOMER NAME ;- SURESH MANI MOB NO ;- 9946826721 | Task Start | Suresh k. | G-Care Diesels Private Limited - Kannur | 82 | engine triped issue while running, found emergency stop shutdown alarm in history.then aditional negative supply battery to emergency switch. Then start the engine condition found ok | Task Start | Mr. Sanjaimon S
10 | North | 211799574 | 2025-07-03 20:26 | 57 | T4.8941.../2320063 | Starting/Stopping Issue | Closed | NEW GAGAN GENERATOR | Vidyut Engineers - New Delhi | 1382 | found SPN:634,FMI 3, then connect the I-konnect & reset the alarm | Closed | Kapil Solanki
11 | North | 211799527 | 2025-07-03 19:31 | 58.5 | T4.8941.../2420591 | Oil leakage issue Call By Customer Name :-Soni singh Mobile No :-9310057666 | Closed | Nidhi Enterprises. | Paluck Technologies Ltd. - Faridabad | 103 | Wrong report by Customer | Closed | Kapil Solanki
12 | North | 211799358 | 2025-07-03 18:06 | 750 | DV2.8501.C4../2420014 | Maintenance Due Alaram Issue Call by Customer. Name:-Vijay Kumar Mobile No.:-9795586504 | Closed | Bharat Petroleum Corporation Ltd | Paluck Technologies Ltd. - Ghaziabad | 511 | Maintenance due alarm, reset the alarm & service due | Closed | Kapil Solanki
35 | South | 211799056 | 2025-07-03 17:20 | 7.5 | D3.8305.../2400190 | Starting Problem Call by : Customer Name : FAVAZ Contact : 7907062609 | Task Start | Dr FAVAZ | G-Care Diesels Private Limited - Thrissur | 8.5 | Checked oil pressure with the mechnical gauge found 3 bar . Oil pressure sensor cleaned fitted it back properly. After that started DG run more Than 30 min . Running performance found normal | Task Start | Mr. Sanjaimon S
13 | North | 211799026 | 2025-07-03 17:17 | 500 | DV8.8501.C4../2320059 | THROTTLE VALVE REPLACE | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 231 | SPN/FMI 51/0 & 51/5 Throttle valve replace after that issue resolve | Closed | Kapil Solanki
51 | South Zone | 211798937 | 2025-07-03 16:53 | 20 | GP3.8601.../2520233 | ENGINE OIL LEAKAGE | Task Start | KARTHIK HM | Prasad Power Engineers - Chikmagalore | LR | Leakage form oil pressure switch, replace the same | Task Start | Mr. Anil Kumar H G
5 | North | 211798913 | 2025-07-03 16:48 | 125.4 | 4H.8041.../2420302 | Diesel lik | Closed | S J RAATH HOTELS PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Bhiwadi | 80 | Fuel leakage from water seprator, adjust with the help of taflon tape | Closed | Gourav Sharma
6 | South zone | 211798876 | 2025-07-03 16:42 | 250 | F6.8842.C4../2420002 | Starting/Stopping Issue | Closed | Ayati Constructions and Estates LLP | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 25 | visited the site no issue found | Closed | Mr. MD Saleem
17 | South zone | 211798829 | 2025-07-03 16:32 | 30 | 3H.8902.../2420827 | Starting Issue Call By Services Delaer Name :- Indumati Mobile No :- 8925873034 | Closed | S. P. Finnacle | Bharath Diesel Sales and Service - Chengalpattu | 20 | engine not starting checked for the battery connect is loose connection is battery fitted ok. | Closed | Mr. NandhaGopal
6 | North | 211798811 | 2025-07-03 16:23 | 125.4 | 4H.8042.C4../2420032 | Starting/Stopping Issue | Closed | BUCON INFRATECH PRIVATE LIMITED | Vidyut Engineers - Noida | 373 | Engine not start, Oil supply pipe leakage Filter to Pump the benjo bolt thread defective & Fuel not suck so, check the NRV found faulty Change the NRV after start the DG found ok | Closed | Kapil Solanki
4 | South zone | 211798256 | 2025-07-03 16:03 | 40 | 3H.8951.../2421760 | Red lamp alarm issue | Closed | ZIGMA TECHNOLOGIES | Surya Power Services - Billekahalli | 2 | SPN 2791 FMI 18, SPN 5838 FMI 1, clear the code and flash the ECU issue resolved | Closed | Mr. Anil Kumar H G
5 | South zone | 211798142 | 2025-07-03 15:59 | 125.4 | 4H.8042.C4../2420264 | Starting Problem Call by : Customer Name : Fiyad Contact : 9497653124 | Closed | C. C. M. K. Memorial Hospital | G-Care Diesels Private Limited - Thrissur | 46 | Attend dg oil level ok, v belt ok, air cleaner element 6H.411.02 ok, battery water & voltage ok, check controller panel side canopy door not close properly, door catcher adjusted & lubrication given, at present of customer representative door open&close properly,engine smoke &sound normal, voltage 238v, safety working properly,dg running found normal Note- advise customer to need kseb supply for battery charger working purpose, | Closed | Mr. Sanjaimon S
8 | North | 211798112 | 2025-07-03 15:52 | 58.5 | T4.8941.../2421209 | Starting Issue Call By Customer Name:-NARINDER GARG No:-9878922199 | Closed | JTL. Industries Limited | SAAN Royal Power Solutions Private Limited - Zirakpur | 22 | Low Fuel Alarm occurred & physically found Fuel Level Low in Tank,communicated to customer for top-up the fuel | Closed | Ved Prakash Gupta
34 | South | 211798074 | 2025-07-03 15:47 | 5.5 | CC1.1013.../2400662 | Starting/Stopping Issue | Open | Accurate Powertech India Private Limited . | Prasad Power Engineers - Tumkur | NA | Visit pending | Open | Mr. Anil Kumar H G
14 | North | 211798028 | 2025-07-03 15:42 | 58.5 | T4.8941.../2423036 | Voltage Fluctuation | Closed | S S Jain Traders | Espiem Engines & Machines (P) Limited - Aligarh | 120 | Found that check the Charging Alternator found fuse was faulty so, replace the same then issue resolve | Closed | Sudhir Awasthi
6 | North | 211798036 | 2025-07-03 15:38 | 58.5 | T4.8941.../2420296 | KRM Issue And Low Voltage Issue Call By Customer Name :- Anish Jain Mobile No:-9867178939 | Closed | 5C Car Care | Paluck Technologies Ltd. - Gurgaon | 178 | Customer raised complaint of low voltage issue but no such issue found on site | Closed | Kapil Solanki
8 | East | 211797965 | 2025-07-03 15:34 | 20 | GP3.8601.../2420165 | Starting Issue Call By KGD Name :- Kumkum Mobile No :-9234456624 | Closed | Ramesh Kumar Kesari | HACS Engineering and Tech Private Limited - Ranchi | 62 | Emergency stop switch alarm so checked for loose connection found Tie also tigthen so cut tie again clean the connector and pressed female connector side pin agian tighted tie properly then resolved the issue | CLOSED | Prabhakar Kumar
15 | North | 211797821 | 2025-07-03 15:03 | 58.5 | T4.8941.../2422836 | Starting/Stopping Issue | Closed | Honey & Dough | OVN Industries Private Limited - New Delhi | 14 | Air lock in fuel line & Emergency switch button was pressed condition so, realease the same | Closed | Kapil Solanki
16 | North | 211797715 | 2025-07-03 14:49 | 40 | 3H.8951.../2420620 | Leakage Issue | Closed | Hotel Amrit Inn | Rajdhani Diesels and Electricals - Jodhpur | 26 | Found battery water low & terminal was loose topup the water & tightness the terminal Service due (CC done on 15/10/2024) | Closed | Gourav Sharma
7 | North | 211797693 | 2025-07-03 14:45 | 25 | GP3.8702.../2421882 | Electrical Problems | Task Start | GURUKRIPA TRADERS | Pratap Diesels Pvt. Ltd. - BIKANER | 11 | Error code Issue Update pending | open | Gourav Sharma
9 | North | 211797507 | 2025-07-03 13:59 | 15 | GP3.8501.../2421502 | CHARGING ALTERNATOR ISSUE | Task Start | Axis Bank Ltd | Gen Powers - PATIALA |  | Visit Pending | Open | Ved Prakash Gupta
8 | South zone | 211797462 | 2025-07-03 13:46 | 125.4 | 4H.8041.../2420321 | Starting/Stopping Issue | Task Start | PRIMEMERIDIAN INFRASTRUCTURE PRIVATE LIMITED | G-Care Diesels Private Limited - Ernakulam | 61 | Found KG645 is not turning on, then checked the dc supply switch found dc supply switch back side removed condition then corrected the dc supply switch and checked now controller is working normally. | Closed | Mr. Sanjaimon S
17 | North | 211797426 | 2025-07-03 13:40 | 125.4 | 4H.8041.../2320090 | Starting/Stopping Issue | Closed | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi | 3393 | Re-Claim so, SR again fill for supply module change | Closed | Kapil Solanki
8 | North | 211797387 | 2025-07-03 13:31 | 58.5 | T4.8941.../2421783 | oil leakage Issue. Call By customer. Name:- Rohitash Jat Mobile No.:-9799589901 | Closed | Rohitash Jat | Pratap Diesels Pvt. Ltd. - Sikar | 186 | Oil leakage found from oil pipe clip so corrected the same & resolve the Issue Update Pending | open | Gourav Sharma
7 | North | 211797369 | 2025-07-03 13:26 | 57 | T4.8941.../2420482 | ALARM ISSUE | Closed | Darshan Power Solutions | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2004 | Found Emergency alarm, Connection was loose tightness the same | Closed | Kapil Solanki
33 | South | 211797347 | 2025-07-03 13:22 | 5.5 | CC1.1013.../2400576 | Starting Issue Call By Customer Name :- Vikas Sir Mobile No :- 6267452730 | Open | Shree Sharda Electricals & Hardware | KALA Care Global LLP - Bagalkote | NA | Visit pending | Open | Mr. Anil Kumar H G
8 | North | 211797356 | 2025-07-03 13:19 | 125.4 | 4H.8042.C4../2420343 | Starting/Stopping Issue | Closed | ALLAHABAD CONSTRUCTION & DEVELOPERS ASSOCIATES | S.S. Enterprises - Allahabad | 29 | DG was not started check & Found fuel sensor was not proper show the reading Check the resistance Found 175 ohm then disconnect the connector after that DG start with alarm | open | Sudhir Awasthi
9 | North | 211797361 | 2025-07-03 13:18 | 320 | F6.8802.../2420135 | line rejection | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-15 | Change the camton wheel & Cam sensor then issue resolve | Closed | Gourav Sharma
40 | South zone | 211797300 | 2025-07-03 13:05 | 35 | 3H.8902.../2422053 | Starting Problem Call by : Customer Name : James Sir Contact : 8606614000 | Task Start | Lillys Kochi | G-Care Diesels Private Limited - Ernakulam | 11 | DG not starting due 2A wire loose connection in interface card. Then tightened the wire and rectified the complaint | Closed | Mr. Sanjaimon S
9 | North | 211797291 | 2025-07-03 13:02 | 125.4 | 4H.8042.C4../2420110 | Starting Issue Call By Customer Name :- Pande Mobile No :- 9911105274 | Closed | SAMSONIC | Paluck Technologies Ltd. - Ghaziabad | 38 | Engine wiring connector (36 Pin) found loose so re-connected the same & resolve the Issue | Closed | Kapil Solanki
9 | East | 211797263 | 2025-07-03 12:58 | 20 | GP3.8601.../2421225 | Starting Issue Call By Customer Name :- Suresh . Mobile No :- 9110032890 | Closed | MUBARAK ALAM | HACS Engineering and Tech Private Limited - Ranchi | 128 | SE visited and found DG not cranking so checked battery voltage found OK but its terminal having rusting so clean it and found the Terminal clamp were loose after tighten issue resolve and loosing issue raised may be customer shifted DG from is initial place. | CLOSED | Prabhakar Kumar
18 | North | 211797246 | 2025-07-03 12:55 | 125 | 4H.8052.C4../2520016 | line rejection | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-2 | SPN/FMI 51/0 ITV jammed so, replace the ITV then issue resolve | Closed | Gourav Sharma
19 | North | 211797198 | 2025-07-03 12:40 | 500 | DV8.8501.C4../2420041 | Electrical Problems | Closed | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 18 | SR open for Synchronization | Closed | Kapil Solanki
20 | North | 211797215 | 2025-07-03 12:38 | 750 | DV2.8501.C4../2420052 | Electrical Problems | Closed | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 8 | SR open for Synchronization | Closed | Kapil Solanki
21 | North | 211797180 | 2025-07-03 12:35 | 82.5 | 5H.8901.../2320078 | Battery Issue And Self Starter Issue Call By Customer Name :- Mohit Sharma Mobile No:-7827824447 | Closed | Pragya Components Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 749 | SPN/FMI 6595/0 Additional dosing chk er DOC choking. Now,reset the alarm | open | Kapil Solanki
22 | North | 211797143 | 2025-07-03 12:31 | 750 | DV2.8501.C4../2420050 | Electrical Problems | Closed | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 9 | SR open for Synchronization | Closed | Kapil Solanki
23 | North | 211797167 | 2025-07-03 12:29 | 40 | 3H.8951.../2420402 | DG Issue | Closed | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 12 | 8 pin relay faulty this reason was d.g set not be start automatic mode so, replace the same then issue resolve | Closed | Kapil Solanki
24 | North | 211797160 | 2025-07-03 12:27 | 40 | 3H.8951.../2420449 | DG Issue | Closed | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 12 | 8 pin relay faulty this reason was d.g set not be start automatic mode so, replace the same then issue resolve | Closed | Kapil Solanki
25 | North | 211797121 | 2025-07-03 12:23 | 15 | GP3.8501.../2420377 | DG Issue | Closed | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 8 | 8 pin relay faulty this reason was d.g set not be start automatic mode so, replace the same then issue resolve | Closed | Kapil Solanki
44 | South Zone | 211797074 | 2025-07-03 12:17 | 200 | 6H.8435.../2420168 | Starting/Stopping Issue | Task Start | Ayati Constructions & Estates LLP | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | Cancelled | Cancelled | Mr. MD Saleem
31 | South zone | 211796976 | 2025-07-03 11:58 | 20 | GP3.8601.../2421456 | Red lamp alarm issue Call by : Customer Name : Gnanavel Contact : 6381441519 | Closed | MINJUR BHAVAN | Madhu Engineering Sales & Service - Kavaraipettai, Chennai | 13 | emergency button wire loosed correct the wiring harness ferrule number 11, tighten the connection. | Closed | Mr. NandhaGopal
32 | South | 211796958 | 2025-07-03 11:55 | 30 | 3H.8902.../2422115 | AVR REPLACE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Flickering issue so replace the AVR | Task Start | Mr. NandhaGopal
10 | North | 211796942 | 2025-07-03 11:50 | 125.4 | 4H.8041.../2420228 | Starting/Stopping Issue | Closed | Harsh Enterprises | SAAN Royal Power Solutions Private Limited - Zirakpur | 358 | Starting Issue due to connections found loose in customer's pannel so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
39 | South zone | 211796918 | 2025-07-03 11:48 | 58.5 | T4.8941.../2423150 | Mil lamp is on and alarm | Closed | Raghamantra Jewellery | Bharath Diesel Sales and Service - Salem | 3 | SPN 2791 AND FMI 18 ERROR CODE SHOWN. CLEARED THE ALARM WITH I KONNECT TOOL. | Closed | Mr. NandhaGopal
11 | North | 211796931 | 2025-07-03 11:45 | 35 | 3H.8902.../2422400 | INSTANCE ID:- 100800877 SITE ID:- CALL BY CUSTOMER:- DG ISSUE:-DG PROBLEM NAME:-BILAL SIR NUMBER:-9797580708 | Closed | Axis Bank Ltd | Suraj Motor Store - Srinagar | 28 | SPN/FMI-157/14 & Battery Voltage found low (9 V)Check the fuel condition in Filter & Tank Fuel found ok , PRV Count found more than 50 so reset the same to 0 & flash the ECU ,Battery Charger found disconnected from mains supply so connected the same & resolve the Issue | Closed | Ved Prakash Gupta
11 | WEST | 211796935 | 45841.4896 | 40 | 3H.8951.../2520478 | LOP issue | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | error code 100/3 ,.low oil pressure sensor alarm, check connection found ok so replace lop sensor | Closed | Jagdeep Saini
10 | East | 211796900 | 2025-07-03 11:44 | 160 | 6H.8475.../2420152 | Leakage Issue | Task Start | Siddartha Construction | HACS Engineering and Tech Private Limited - Hazaribagh | 41 | Radiator under EDO |  | Prabhakar Kumar
12 | North | 211796892 | 2025-07-03 11:40 | 58.5 | T4.8941.../2422479 | Starting/Stopping Issue | Closed | NITIKA TEXTILE.. | SAAN Royal Power Solutions Private Limited - Ambala | 45 | DG Stopping Issue in Auto mode due to mains input R-Phase wire found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
33 | South zone | 211796804 | 2025-07-03 11:18 | 35 | 3H.8902.../2420696 | Starting Issue Call By Customer Name :- Dhananjay . Mobile No :-6305471961 | Task Start | SUN RISE COUNTY RAINBOW APARTMENT | Ultimate Power Source - Kadappa | 1 | display not working battery voltage checked battery discharged removed the battery service center | Closed | Mr. NandhaGopal
13 | North | 211796747 | 2025-07-03 11:12 | 15 | GP3.8501.../2422153 | Starting problem | Task Close | Indian Army | Suraj Moters Stores - Leh | LR(2) | Starting Issue due to MPU found faulty , Voltage on connector found 0 V so replace the same &resolve the Issue | Closed | Ved Prakash Gupta
22 | South zone | 211796759 | 2025-07-03 11:06 | 30 | 3H.8902.../2422380 | Starting Problem Call by : Customer Name : Narayanarao Contact : 9024287904 | Task Start | ICICI Bank | Ultimate Power Source - Nellore | 2 | Auto sensing connection done for auto start | Closed | Mr. NandhaGopal
38 | South zone | 211796752 | 2025-07-03 11:04 | 125.4 | 4H.8041.../2420311 | Starting/Stopping Issue | Open | Nagaveni. | Surya Power Services - Bangalore | 27 | Visited the site and check the engine condition, check the alarm, emergency shutdown, check the emergency switch push button wiring connections, retight the emergency push button wiring connections & reset the alarm & engine started tested auto mode found ok. | Closed | Mr. Anil Kumar H G
9 | South zone | 211796648 | 2025-07-03 10:51 | 30 | 3H.8902.../2421111 | Display Showing "Shut Down" And Alarm Light Blinking Problem Call by : Customer Name :Antony Contact :9496765550 | Open | P. V. S. Mango Bakers | G-Care Diesels Private Limited - Thrissur | 39 | Emergency switch malfunctioning . dismantled and rectified also controller CT cable was disconnected condition connected properly. | Closed | Mr. Sanjaimon S
14 | North | 211796659 | 2025-07-03 10:49 | 40 | 3H.8951.../2420579 | Starting/Stopping Issue | Closed | M/s Fresh & Delicious | SAAN Royal Power Solutions Private Limited - Mandi | 14.1 | R-Phase fuse found blown so replace the same & resolve the Issue | Closed | Ved Prakash Gupta
10 | North | 211796625 | 2025-07-03 10:45 | 125.4 | 4H.8042.C4../2520140 | tHROTTLE VALVE MALFUNCTIONING TO BE CHANGED | Closed | MODI NAGAR PET INDUSTRIES | Paluck Technologies Ltd. - Ghaziabad | LR_12 | SPN/FMI 51/5 ENGINE NOT RUNNING SMOOTHLY ON LOAD CHECKED TO FIND THROTTLE VALVE FAULTY THROTTLE VALVE INTAKE THROTTLE VALVE REPLACED | Closed | Kapil Solanki
15 | North | 211796606 | 2025-07-03 10:42 | 25 | GP3.8702.../2420077 | Genset Trip | Open | BAWA TOTAL SOLUTION | SAAN Royal Power Solutions Private Limited - Hisar |  | Under Cancellation-work will done on Paid basis | Cancelled | Ved Prakash Gupta
11 | North | 211796585 | 2025-07-03 10:39 | 125.4 | 4H.8041.../2320150 | Starting/Stopping Issue | Closed | Alwar Royals | Pratap Diesels Pvt. Ltd. - Alwar | 153 | found XDBK 1,2,3,&4 Connectors loose.tighten all connectors properly and relay board connectors after that issue resolve | Closed | Gourav Sharma
2 | South zone | 211796437 | 2025-07-03 10:10 | 20 | GP3.8601.../2420412 | STARTING ISSUE Call By Customer Name :- Mallik Mobile No :-9972554485 | Closed | REVAMP POWER | Surya Power Services - Kalyan Nagar | 12 | found battery positive terminal cable loose connection then tighten the connection | Closed | Mr. Anil Kumar H G
12 | North | 211796407 | 2025-07-03 10:06 | 82.5 | 5H.8901.../2420128 | Alarm Issue Call By Customer Name - Vijay Sharma Number - 9990431907 | Closed | Amit Industries | Paluck Technologies Ltd. - Faridabad | 33 | Ecu flt alarm 516166/0 reset tha alarm | Closed | Kapil Solanki
10 | North | 211796380 | 2025-07-03 09:54 | 7.5 | D3.8305.../2400166 | Hunting Issue Called By Customer Name - Ashok Tiwari Number - 8175059408 | Closed | MR. ASHOK KUMAR TIWARI | Excel Diesel Private Limited - Sultanpur | 3 | DG 's mounting bolt was broken due to which engine hunting so arranged bolt from customer and fitted and resolved the issue Images not get yet | open | Sudhir Awasthi | Photo Required
23 | South zone | 211796222 | 2025-07-03 08:55 | 125.4 | 4H.8042.C4../2420622 | Amber Lamp On Alarm And MCB Issue Call By Customer Name :- Mithun Kumar Ray Mobile No:-9835545375 | Task Start | PARMAR ELECTRICALS [P] LTD | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 155 | 1761/18, advice customer to maintaion DEF level, clear the code | Closed | Mr. NandhaGopal
16 | North | 211796240 | 2025-07-03 08:48 | 625 | DV0.8501.C4../2420094 | automation issue Call By Customer Name :- naresh Mobile No :- 9872570947 | Closed | St. Joseph Convent School. | Dynamic Engineering Services - Jalandhar | 33 | SPN/FMI-516166/0 ; ECU Malfunction alarm in event Log so reset the same & educated customer not to double tap stop command give to stop DG | Closed | Ved Prakash Gupta
11 | East | 211796220 | 2025-07-03 08:37 | 30 | 3H.8902.../2320171 | Tripping Issue And Protect Lamp On Alarm Issue Call By Customer Name :-Dr Satiranjan .. Mobile No :8709638762 | Closed | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | 200 | DG not cranking showing SPN 637 FMI 2 Crank speed sensor flt sig err so checked it connector voltage found OK 2.5, 2.5, 0 V then checked the continituity of 3 nos. wire from the ECU TO crank sensor found Ok the removed crank sensor and refitted again after clearing found same issue and Also found Pressure relef vlv fault open then tried to connect IKonnect but no, light found in dongle so checked for Voltage at Dongle connector Found 12, 2.5,2.5 at B,C,D with the body but notwith the Neutral A point so tighten Distribution block after that conected Ikonnect cleared the code then cranked DG cranked but again showing Crank sensor code after that flashed the ECU then cranked , DG started but having very uneven and hitting sound from the alternator side so need joint visit with nidec team. | OPEN | Prabhakar Kumar
23 | East | 211796220 | 2025-07-03 08:37 | 30 | 3H.8902.../2320171 | Tripping Issue And Protect Lamp On Alarm Issue Call By Customer Name :-Dr Satiranjan .. Mobile No :8709638762 | Closed | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | 200 | On joint visit with alternator team found coupling disk broken | OPEN | Prabhakar Kumar | Alternator issue
31 | South | 211796210 | 2025-07-03 08:12 | 125.4 | 4H.8041.../2421020 | Starting Problem Call by : Customer Name :ANBU Contact :9952356079 | Task Start | Kothanya Construction. . | Bharath Diesel Sales and Service - Arni | 229.26 | Replaced fuel inlet hoses temporarily changed | Task Start | Mr. NandhaGopal
26 | North | 211795446 | 2025-06-03 22:32 | 125.4 | 4H.8042.C4../2420843 | Starting Issue Call By Customer Name :- Suresh Kumar Sharma No :- 9650555281 | Closed | NEWAGE FORMULATION | Espiem Engines & Machines (P) Limited - Aligarh | 75 | SPN/FMI 3031/14, 4095/1, 516166/0 reset the alarm & flash the file | Closed | Sudhir Awasthi
27 | NORTH | 211795057 | 2025-06-03 18:16 | 30 | 3H.8902.../2421423 | DG not starting,kindly resolve-517060 | Open | ICICI Bank Limited | R K Engineers - Meerut |  | Cancelled-problem solve in tele. Discussion | Cancelled | Sudhir Awasthi
17 | North | 211794172 | 2025-06-03 16:51 | 250 | F6.8841.../2420079 | Leakage Issue | Closed | Krishna Automatics | SAAN Royal Power Solutions Private Limited - Rohtak | 121 | Coolant leakage found near thermo-stat due to clamp found loose of hose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
28 | NORTH | 211794076 | 2025-06-03 16:30 | 58.5 | T4.8941.../2421502 | Power Supplay Issue Call By Customer Name :- Manisha Mam Mobile No :- 9873588552 | Task Start | DIHAAN ENTERPRISES | Vidyut Engineers - New Delhi | 20 | Found 32A MCB was off, On the mcb After start the dg then running found ok | Closed | Kapil Solanki
29 | NORTH | 211794070 | 2025-06-03 16:27 | 125.4 | 4H.8042.C4../2420772 | Starting Issue Call By Customer Name :- Ramesh Mobile No :- 8394887371 | Open | MODERN ELECTRIC COMPANY | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Cancelled-problem solve in witout visit | Cancelled | Sudhir Awasthi
11 | NORTH | 211794059 | 2025-06-03 16:27 | 15 | GP3.8501.../2420645 | INSTANCE ID :-100776818 SITE ID :- 14650 CALL BY CUSTOMER// DG ISSUE :-DG BATTER PROBLEM NAME :-Sandeep Panchal NUMBER :-9149000643 | Task Start | BHARTI AIRTEL LIMITED | Vidyut Engineers - Noida | 176.53 | SR opened for battery replacement | Closed | Kapil Solanki
30 | NORTH | 211794036 | 2025-06-03 16:23 | 58.5 | T4.8941.../2421991 | Starting issue Called by customer Name ; Shaizi Number : 9026430390 | Open | Ananya Power Solutions | S. R Engines Sales And Service - LUCKNOW |  | Cancelled- SR creation by mistake | Cancelled | Sudhir Awasthi
18 | North | 211794026 | 2025-06-03 16:22 | 40 | 3H.8951.../2420068 | FUEL LEAKAGE ISSUE | Closed | Ashoka Engg. Works | SAAN Royal Power Solutions Private Limited - Rohtak | 56 | Fuel leakage found from Water separator so open the sensor & replace the O-Ring & re-fitted the same,issue resolved | Closed | Ved Prakash Gupta
31 | NORTH | 211793981 | 2025-06-03 16:08 | 125.4 | 4H.8041.../2420690 | ALARM ISSUE | Closed | Jaishree Infra | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 176 | Found 3031/14 High adblue tem. Reset the alarm | Closed | Kapil Solanki
30 | South | 211793948 | 2025-06-03 16:04 | 25 | GP3.8702.../2421634 | VOC - Automation Issue Customer Name -Senthil Customer Number -7025086344 Mode- SR Generated through CDI calling. | Open | Senthil | Electro Controls - Kattappana | NA | Visit pending | Open | Mr. Sanjaimon S
31 | South zone | 211793870 | 2025-06-03 15:55 | 250 | F6.8842.C4../2420083 | Starting/Stopping Issue | Task Start | Vittal Plaza | Surya Power Services - Billekahalli | 1.3 | auto eb connection done for auto start | closed | Mr. Anil Kumar H G
32 | South zone | 211793870 | 2025-06-03 15:55 | 250 | F6.8842.C4../2420083 | Starting/Stopping Issue | Task Start | Vittal Plaza | Surya Power Services - Billekahalli | 1.3 | auto eb connection done for auto start | closed | Mr. Anil Kumar H G
12 | East | 211793846 | 2025-06-03 15:54 | 250 | F6.8841.../2420134 | Starting/Stopping Issue | Closed | TNZ CENEMA HALL | Green Powerline - Tezpur | 105 | There found no issue in DG in mannual Customer side auto pannel issue due to which DG was not starting in auto mode | CLOSED | Ujjwal Das
1 | East | 211793838 | 2025-06-03 15:51 | 25 | GP3.8702.../2520123 | Dg nut Start | Task Start | ATC Telecom Infrastructure Private Limited | Gangpur Sales and Services - BHUBANESWAR |  | Visit Pending | OPEN | Ujjwal Das
32 | NORTH | 211793807 | 2025-06-03 15:47 | 250 | DV8.9840.../2420003 | Voltage Issue | Task Start | Kundan Refinery P. Ltd. | Paluck Technologies Ltd. - Gurgaon | 8 | Gas Engine- Voltage flactuation | Closed | Kapil Solanki
13 | East | 211793757 | 2025-06-03 15:37 | 20 | GP3.8604.../2420121 | INSTANCE:- 100741934 SITE ID :- I-BR-PTNA-ENB-G002 CALL BY CUSTOMER :- DG ISSUE :-OIL LEAKAGE ISSUE , MOBIL LEAKAGE ISSUE NAME :-.ARYAN RAJ KUMAR MOB NUMBER :-9334787903 | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Patna | 133 | Found fuel and leakage in suction line at the Electric feed pump so tighten the clamp and lube oil leakage at the lube oil drain pipe due to clamp loose after tigten issue resolved | CLOSED | Prabhakar Kumar
59 | NORTH | 211793701 | 2025-06-03 15:30 | 58.5 | T4.8941.../2423102 | Starting/Stopping Issue | Completed | Das Nursing Home | Espiem Engines & Machines (P) Limited - Farukhabad | 9 | found and alarm found 157/14__2802/4__5838/1 alarm reset the alarm and panal 2A wire loose found and battery terminals _+ wire loose found cable connector neutral wire broken after tightness the all & found DG running ok | Closed | Sudhir Awasthi
26 | South zone | 211793688 | 2025-06-03 15:27 | 20 | GP3.8601.../2421946 | Starting/Stopping Issue | Completed | M. AMBEDKAR | Bharath Diesel Sales and Service - Dindigul | 23 | started the engine SPN 2802 AND FMI 3 and SPN 158 AND FMI 0 problem codes found. Check the controller battery voltage high. So check the charging alternetor fuse. After refitted with fuse,removed and check the charging alternetor wire connection (2B/4 &L2) after refitted recommend tight. After started the engine properly started. After check the charging alternetor Voltage 14.5 maintained. After take given load one hour ,no issues found ok. Check the all necessary parameters all are found ok. | Closed | Mr. NandhaGopal
60 | NORTH | 211793647 | 2025-06-03 15:15 | 125.4 | 4H.8042.C4../2420057 | Starting/Stopping Issue | Closed | SHUBHAM RMC SERVICES PRIVATE LIMITED | S.S. Enterprises - Allahabad | 1070 | Update pending | open | Sudhir Awasthi
61 | NORTH | 211793638 | 2025-06-03 15:11 | 30 | 3H.8902.../2420917 | Starting/Stopping Issue | Closed | DESAI | Vidyut Engineers - New Delhi | 6 | Customer side panel issue | Closed | Kapil Solanki
101 | North | 211793631 | 2025-06-03 15:07 | 58.5 | T4.8941.../2421361 | Door lock Issue Call By Customer Name :- Sanjiv kumar Mobile No :- 9023473623 | Task Start | Shivani Bakshi. | Megatron Engineers - Pathankot | 56 | Canopy door lock alignment issue due to bolt found loose so tightened the same to adjust the lock & resolve the Issue | Closed | Ved Prakash Gupta
14 | East | 211793606 | 2025-06-03 15:02 | 15 | GP3.8501.../2421477 | Red lamp alarm issue and stopping issue Called by customer Name : ROUSHAN Number 9509743365: | Cancelled | LALL CONSTRUCTION INDIA LTD | Globalline India Services Private Limited - Madhepura |  | SR cancelled on telephonic communication resolved | CANCELLED | Prabhakar Kumar
62 | NORTH | 211793553 | 2025-06-03 15:00 | 125 | F6.9840.../2420003 | Automations | Closed | Venu Eye Institute & Research Centre. | Vidyut Engineers - New Delhi | 59 | show spn number spn3607 fmi 5 this reason was d.g set alarm show I have cleared the fault for laptop and file to save after the start | Closed | Kapil Solanki
63 | NORTH | 211793550 | 2025-06-03 14:59 | 57 | T4.8941.../2420035 | Starting/Stopping Issue | Task Start | janta diagnostic center pvt.ltd | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki
64 | NORTH | 211793523 | 2025-06-03 14:55 | 125.4 | 4H.8041.../2420206 | Starting/Stopping Issue | Task Start | SHAMAN VIHAR APARTMENT | OVN Industries Private Limited - New Delhi | 15 | SPN/FMI 3509/3 sensor supply 1 Error check & found T4 sensor connection loose | Closed | Kapil Solanki
65 | NORTH | 211793516 | 2025-06-03 14:52 | 160 | 6H.8475.../2420086 | Sound/Vibration Issue | Closed | Sacred Heart Convent School. . | Pratap Diesels Pvt. Ltd. - Sri Ganganagar | 58 | Found V- belt loose tightness the same & topup the urea then issue resolve | Closed | Gourav Sharma
57 | South Zone | 211793498 | 2025-06-03 14:51 | 125.4 | 4H.8041.../2420668 | oil leakage problem and tripping problem Call by : Customer Name :Veeresh Contact :9535524666 | Task Start | Sudarshan Family Store | Surya Power Services - Kalyan Nagar | 169 | found oil leakage from oil sump crack at drain welding place so replaced new oil sump | Closed | Mr. Anil Kumar H G
102 | North | 211793475 | 2025-06-03 14:42 | 20 | GP3.8601.../2421221 | Starting/Stopping Issue | Task Start | REAL BUILDING CONSTRUCTIONS | SAAN Royal Power Solutions Private Limited - Zirakpur | 17 | Starting Issue with under speed alarm,checked fuel line found ok, reset the controller & resolve the Issue | Closed | Ved Prakash Gupta
27 | South zone | 211793409 | 2025-06-03 14:29 | 82.5 | 5H.8901.../2420476 | Automatically Switching off Call by : Customer Name :Jayaprakash Contact :8428953898 | Task Start | KALYAN JEWELLERS.. | Madhu Engineering Sales & Service -Poonamallee,Chennai | 574 | Visited the site and attend the checked the battery distilled water and cable connections found ok, checked the radiator coolent and v belt tension is ok, Then checked the oil level is low, customer is not maintain the ad blue is empty then after customer will top-up the DEF oil and fuel so engine is Automatically switch off,then checked the leaks sump joint and racer cover oring side is oil leakage. | Closed | Mr. NandhaGopal | Update Required
66 | NORTH | 211793407 | 2025-06-03 14:26 | 125.4 | 4H.8041.../2420256 | Starting issue and Automation issue Call By Customer Name :- Sunil Mobile No :- 9759936934 | Task Start | Sri Venkateswara University | Vidyut Engineers - New Delhi | 8 | Emergency switch pressed condition | Closed | Kapil Solanki
67 | NORTH | 211793368 | 2025-06-03 14:14 | 125.4 | 4H.8042.C4../2420472 | Starting and Voltage Issue Call By Customer Name :-Narendar Singh Mobile No :-7669931331 | Closed | M P Singh | Vidyut Engineers - Noida | 10 | Customer side panel issue | Closed | Kapil Solanki
15 | East | 211793338 | 2025-06-03 14:02 | 160 | 6H.8475.../2420152 | Engine Over Hitting Issue. Call By KGD Name:-Kumkum Mobile No.:-9234456624 | Closed | Siddartha Construction | HACS Engineering and Tech Private Limited - Hazaribagh | 41 | Found coolant leakage at radiator due to the charging alternator eye bolt loosen and hit the radiator due to which it got damage and will replace under warranty. | OPEN | Prabhakar Kumar
68 | NORTH | 211793330 | 2025-06-03 14:00 | 320 | F6.8802.../2320051 | Starting Issue Email By Customer Name:-Jeet Singh | Open | Sri Dwarkadheesh Polymers Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 116 | Over load issue | Closed | Gourav Sharma
69 | NORTH | 211793306 | 2025-06-03 13:57 | 40 | 3H.8951.../2421284 | Abnormal Sound Issue Call By Customer Name :- AMIT VARMA Mobile No :-9960909019 | Task Start | SADHU BRICKS | S.S. Enterprises - Sonbhadra | 112 | No any abnormal sound | Closed | Sudhir Awasthi
16 | East | 211793161 | 2025-06-03 13:18 | 82.5 | 5H.8901.../2420635 | Under Lamp On Alarm Issue Call By Customer Name :-VIVEK KUMAR Mobile No :- 9708034091 | Closed | SHRI GRISHNESWAR COLD STORAGE PVT LTD | Globalline India Services Private Limited - Begusarai | 101 | Low def level laram 6595,FMI: 0 - SPN: 1761,FMI: 16 | CLOSED | Prabhakar Kumar
103 | North | 211793115 | 2025-06-03 13:08 | 82.5 | 5H.8901.../2320017 | STARTING ISSUE Called by customer Name : Sikka Precision Technologies Number : 9810046365 | Open | Sikka Precision Technologies | SAAN Royal Power Solutions Private Limited - Bahadurgarh |  | Visit pending | open | Ved Prakash Gupta
19 | North | 211792733 | 2025-06-03 11:58 | 30 | 3H.8902.../2420043 | starting issue | Task Start | S. K. Trading Company | SAAN Royal Power Solutions Private Limited - Rohtak | 125 | Battery Voltage found low due to mains supply not given to Charger so installed the same & resolve the Issue | Closed | Ved Prakash Gupta
52 | South | 211792685 | 2025-06-03 11:55 | 125.4 | 4H.8041.../2420321 | Battery Problem Call by : Customer Name :Biju Contact :9447544718 | Closed | PRIMEMERIDIAN INFRASTRUCTURE PRIVATE LIMITED | G-Care Diesels Private Limited - Ernakulam | 60 | Loose connection from battery side, so tighten the connection | Task Start | Mr. Sanjaimon S
10 | South zone | 211792685 | 2025-06-03 11:55 | 125.4 | 4H.8041.../2420321 | Battery Problem Call by : Customer Name :Biju Contact :9447544718 | Task Start | PRIMEMERIDIAN INFRASTRUCTURE PRIVATE LIMITED | G-Care Diesels Private Limited - Ernakulam | 60 | checked the battery voltage low and informed customer to provide battery charger connection | Closed | Mr. Sanjaimon S
104 | North | 211792690 | 2025-06-03 11:52 | 125.4 | 4H.8041.../2420151 | Code problem | Closed | SHRI SHAKTI ENTERPRISES | SAAN Royal Power Solutions Private Limited - Sonipat | 560.3 | Oil leakage from rocker cover & AdBlue level low(1761/16) top-up the same,Rocker cover Ring need to replace | open | Ved Prakash Gupta
24 | South Zone | 211792631 | 2025-06-03 11:41 | 15 | GP3.8501.../2520091 | Loading issue Ca1led by customer Name : Patel Number : 9739401035 | Open | SHYAM TILES & GRANITE | KALA Care Global LLP - Belagavi | 15 | Customer using over load so educate customer | Closed | Mr. Anil Kumar H G
70 | NORTH | 211792612 | 2025-06-03 11:36 | 30 | 3H.8902.../2420522 | Low Speed Alarm Call By Customer. Name:- Shekhar Mobile No.:- 8527075873 | Task Start | Handicapped Women Welfare Association | OVN Industries Private Limited - New Delhi | 27 | found load unbalanced educate the customer for balancing the load | Closed | Kapil Solanki
105 | North | 211792533 | 2025-06-03 11:27 | 62.5 | T4.8941.../2320150 | AUTOMATION | Closed | AGRAWAL METALS | SAAN Royal Power Solutions Private Limited - Hisar | 80 | Voltage set of phases (From 215 V to 230 V on each Phase) through AVR as per customer demand & now Phase to Phase Voltage is 415 V.DG runs mostly at 55 amp but some time it requires more than 80 % & DG used to trip with Overload alarm | Closed | Ved Prakash Gupta
71 | NORTH | 211792445 | 2025-06-03 11:15 | 30 | 3H.8902.../2421456 | Leakage Issue | Closed | National Engineering Industries | Paluck Technologies Ltd. - Gurgaon | 299 | found that oil lekage from Blow by pipe required need to replace | Closed | Kapil Solanki
72 | NORTH | 211792452 | 2025-06-03 11:07 | 58.5 | 6H.9840.../2420007 | Starting Issue Call By Customer Name :- M. D Afroj Mobile No:-8700479015 | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 40 | Gas Engine- Gas pressure low & over load issue | Closed | Kapil Solanki
73 | NORTH | 211792398 | 2025-06-03 10:59 | 40 | 3H.8951.../2520037 | R Phase Issue Call By Customer Name :- Neeraj Agarwal Mobile No :-7838099619 | Open | Immigration Security Services Pvt . Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | Visit pending | open | Sudhir Awasthi
74 | NORTH | 211792393 | 2025-06-03 10:58 | 250 | F6.8841.../2320050 | Battery charging issue | Closed | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 269 | Battery charger faulty replace the charger | Closed | Kapil Solanki
75 | NORTH | 211792323 | 2025-06-03 10:48 | 15 | GP3.8501.../2421857 | Trip_Genset_Low_Voltage | Task Start | R. K. Traders | S. R Engines Sales And Service - Gorakhpur | 219 | Found R phase under voltage then check the AVR found Fuse was blown then change new fuse found agan same issue then change the AVR after tha issue resolve | Closed | Sudhir Awasthi | KRM Check
17 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | SE is on Site | OPEN | Ujjwal Das
9 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | update pending | OPEN | Ujjwal Das
15 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | Update pending at dealer end | OPEN | Ujjwal Das
7 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | Engine not starting due to carburetor issue | OPEN | Ujjwal Das
22 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | Engine not starting due to caburetor issue,Carburetor under EDO | OPEN | Ujjwal Das
14 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | Engine not starting due to caburetor issue,Carburetor under EDO | OPEN | Ujjwal Das
15 | East | 211792289 | 2025-06-03 10:45 | 5 | CP1.1003.../2400163 | Load Issue Call By Customer Name :- Surbha Mobile No :7543017545 | Open | M/s Riniam Enterprise | Almas Engineers - Dibrugarh |  | Engine not starting due to caburetor issue,Carburetor under EDO | OPEN | Ujjwal Das
23 | WEST | 211792294 | 2025-06-03 10:36 | 45 | 3H.8951.../2520075 | Genset Trip | Task Start | Perennial Technologies Pvt. Ltd | Shree Engineering Service - Jabalpur | 27 | The emergency stop button was pressed, so it was released and the customer was educated about the issue. | Closed | Vijay patil
29 | South | 211792189 | 2025-06-03 10:26 | 160 | 6H.8475.../2420418 | Starting/Stopping Issue | Task Start | KVR AUTO CARS PVT LTD | G-Care Diesels Private Limited - Kannur | 294 | Refitted the calibrated FIP and replace feed pump and connect fuel line then start the engine after starting the engine | Task Start | Mr. Sanjaimon S
18 | East | 211792161 | 2025-06-03 10:16 | 45 | 3H.8951.../2520086 | Voltage flickering | Task Start | MUNDHRA HOSPITAL PRIVATE LIMITED | HACS Engineering and Tech Private Limited - Jamshedpur | 16 | Customer Complaint was light flicker issue and on visiting found the LED blub which was flicker more that found defective and also observed customer load is unbalance and also neutral earthing not provided properly(1nos only) So we analysis load found current harmonic above normal and the volatage fluctuation was about 10-20 V but after the replacing the DSRL AVR by R150 the voltage fluctuation drops to 2-3V due to which the flickering also found to be normal, but current harmonics was not normal need to balance the load and neead proper neutral earthing. | CLOSED | Prabhakar Kumar
28 | South | 211792051 | 2025-06-03 09:50 | 125 | 4H.8052.C4../2520066 | Engine Replacement | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Abnormal sound from engine but not able to identify so engine is sending back to kagal plant | Task Start | Mr. NandhaGopal
106 | North | 211792037 | 2025-06-03 09:44 | 82.5 | 5H.8901.../2420804 | Under Speed Alarm Issue Call By Customer Name :-Naveen Mobile No :- 8222894142 | Closed | FAIRMOUNT HOTELS PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Sonipat | 1073 | SPN/FMI-520527/18,3364/27,4225/1,522122/1 related to CAN & DEF Tank diagnosis,checked the quality sensor & quality on I-Konnect,found ok,DEF found over Top-up so same communicated to customer(Keep 90%) & remove the code,Issue reolved | Closed | Ved Prakash Gupta | Under Observation
27 | South | 211792007 | 2025-06-03 09:36 | 30 | 3H.8902.../2420982 | Hunting problem Call by : Dealer Name : S.VENKATACHALAM . Contact : 8124647906 Dealer no:8870478403 | Task Start | S.Vengatachalam | Bharath Diesel Sales and Service - Pattanur | 31 | Underspeed alarm sometime occurs | Task Start | Mr. NandhaGopal
76 | NORTH | 211791996 | 2025-06-03 09:25 | 30 | 3H.8902.../2420478 | Automation Issue Call By Customer Name :- Ajit Kumar Mobile No :- 9810005959 | Closed | Zanskar Securities. | Vidyut Engineers - New Delhi | 15 | Wrong reporting SR | Closed | Kapil Solanki
77 | NORTH | 211791992 | 2025-06-03 09:15 | 15 | GP3.8501.../2420028 | INSTANCE ID:-100740393 SITE ID:- 17876 CALL BY CUSTOMER// DG ISSUE:- DG STARTING PROBLEM NAME:- PRAMOD KUMAR NUMBER:- 9871953792 | Closed | Bharti Airtel MO-Delhi | Vidyut Engineers - New Delhi | 2748 | Found that fuel line chocked so, clean the fuel line & Suction line in Tank filter defective, | Closed | Kapil Solanki
78 | NORTH | 211791969 | 2025-06-03 09:00 | 125.4 | 4H.8041.../2420010 | Automation Issue Call By Customer Name:-Abhijit . No:-9810392138 | Closed | Gopa Chanda | Vidyut Engineers - New Delhi | 21 | Selector switch on manual mode, so dg not start in auto | Closed | Kapil Solanki
107 | North | 211791936 | 2025-06-03 08:18 | 125.4 | 4H.8042.C4../2420449 | Voltage Fluctuation | Closed | ASHA MAHAJAN | SAAN Royal Power Solutions Private Limited - Zirakpur | 13 | Load unbalance(3,93,2)amp at R,Y & B phase respectively due to which voltage variation found on Load side , same communicated to customer & rectified by their technician(Load deviation corrected) | Closed | Ved Prakash Gupta
108 | North | 211791921 | 2025-06-03 07:13 | 62.5 | T4.8941.../2420290 | Electrical Problems | Closed | Green Energy Diesel Engines Private Limited. | SAAN Royal Power Solutions Private Limited - Sonipat | 331.1 | Battery Voltage found low due to Mains supply to battery charger was found disconnected on site(Previously installed) same communicated to customer & install the same | Closed | Ved Prakash Gupta
109 | North | 211791920 | 2025-06-03 07:06 | 125.4 | 4H.8041.../2420353 | Electrical Problems | Closed | PSG ELECTRICALS | SAAN Royal Power Solutions Private Limited - Sonipat | 23.22 | AC Voltage fluctuation due to Neutral wire found loose in pannel so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta
110 | North | 211791911 | 2025-06-03 06:57 | 15 | GP3.8501.../2420451 | Starting/Stopping Issue | Closed | Mr. Ravinder Rana | SAAN Royal Power Solutions Private Limited - Sonipat | 42 | Update pending | Open | Ved Prakash Gupta
26 | South | 211791844 | 2025-06-03 05:34 | 15 | GP3.8501.../2422183 | Trip_Genset_Low_Voltage | Open | SM Partners | G-Care Diesels Private Limited - Ernakulam | NA | Visit pending | Open | Mr. Sanjaimon S
40 | NORTH | 211791229 | 2025-05-03 19:22 | 250 | F6.8841.../2320050 | Starting Issue Call By Customer. Name:-Pradeep Yadav Mobile No.:-8368321282 | Closed | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 263 | Battery charger faulty replace the charger | Closed | Kapil Solanki
43 | South Zone | 211791182 | 2025-05-03 18:38 | 20 | GP3.8601.../2420901 | StoppingProblem Call by : Customer Name : Venkata narayana Contact : 8639592818 | Open | M/s. Sunrise Petrol Filling Station. | Sri Manjunath Technical Services - Bhimavaram |  | Cancelled | Cancelled | Mr. MD Saleem
22 | WEST | 211791022 | 45780.7486 | 200 | 6H.8435.../2420127 | TRIPPING ISSUE. Email By - Service Dealer Name -Vishal Raut | Cancelled | M. H. C. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | cancelled | Closed | Jagdeep Saini
14 | West | 211790937 | 2025-05-03 17:41 | 320 | F6.8802.../2420149 | Unbalance load alarm issue Call by customer Name - Rajendra Gaikwad No - 9975390626 | Task Start | Symbiosis Open Education Society | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | unbalance load | Closed | Jagdeep Saini
41 | NORTH | 211790936 | 2025-05-03 17:41 | 20 | GP3.8601.../2320006 | Power Supply Issue Call By Customer Name :- Mobile No :- | Task Start | Somti Power Solutions | Vidyut Engineers - Noida | 434 | No any issue found in DG | Closed | Kapil Solanki
94 | North | 211790905 | 2025-05-03 17:34 | 30 | 3H.8902.../2320163 | DG not starting,Not working-516626 | Open | ICICI Bank Limited | Gen Powers - PATIALA | 23 | Battery voltage low(10 V) , Battery charger fuse blown so replace the fuse ; charger working normal | Closed | Ved Prakash Gupta
25 | South | 211790832 | 2025-05-03 17:17 | 0 | GP3.8702.../2520276 | Observed Alarm in controller (SPN: 3510 FMI: 3 ,Sen Sply 2 err). | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | SPN: 3510 FMI: 3, remove the connector, then fitted, Clear the DTC. | Task Start | Mr. NandhaGopal
42 | NORTH | 211790824 | 2025-05-03 17:16 | 30 | 3H.8902.../2320076 | Starting Issue Call By Customer Name :- Bajrang .. Mobile No :- 8290690400 | Task Start | JMCC INFRA PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 4718 | Found starting relay connection was loose so, tightness the same after train on load then found no any iss in DG | Closed | Kapil Solanki
43 | NORTH | 211790691 | 2025-05-03 17:11 | 125.4 | 4H.8041.../2420233 | Maintenance Due Alarm And Shut Down Alarm Clear Call By Customer Name :-Anil Kumar Mobile No :- 9990907408 | Closed | Annu Auto Components | Paluck Technologies Ltd. - Gurgaon | 250 | found error code 3031 and 520528 and maintenance alarm then reset alarm | Closed | Kapil Solanki
44 | NORTH | 211790409 | 2025-05-03 17:01 | 125 | F6.9840.../2420003 | Starting/Stopping Issue | Open | Venu Eye Institute & Research Centre. | Vidyut Engineers - New Delhi |  | Visit pending | open | Kapil Solanki
95 | North | 211790352 | 2025-05-03 17:01 | 250 | F6.8841.../2420220 | Battery Charger Issue Call By customer Name :Tarachand . No : 9728993286 | Open | Powercam Electricals Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 80 | Found battery charger faulty, not given the output voltage so,need to replace | open | Ved Prakash Gupta
5 | East | 211790328 | 2025-05-03 16:59 | 125.4 | 4H.8041.../2420658 | ECU fail Alarm Issue Call By Customer Name :- Medoaj Mobile No :-7808977001 | Task Start | Divine Savior Church | HACS Engineering and Tech Private Limited - Ranchi | 59 | SPN: 1761,FMI: 16 , SPN: 3031 and SPN 516166 ,FMI: 0 low DEF level alarm and high adblue temp and Ecu flt so topup def and cleared code by ikonnect issue resolved. checked for 3-4 time found no issue. | OPEN | Prabhakar Kumar
2 | East | 211790333 | 2025-05-03 16:51 | 7.5 | D3.8305.../2400098 | Starting/Stopping Issue | Closed | FOREST RANGE OFFICER - BHUBANESWAR | Gangpur Sales and Services - BHUBANESWAR | 336 | Update Pending | CLOSED | Ujjwal Das
45 | NORTH | 211790289 | 2025-05-03 16:49 | 57 | T4.8941.../2420102 | Alarm Raise Issue & Starting Issue. Call By customer. Name:- Mohit Jahavar Mobile No.:-9999946975 | Task Start | B. M. Industries. | Paluck Technologies Ltd. - Faridabad | 103 | battery low charger connection removed | Closed | Kapil Solanki
46 | NORTH | 211790246 | 2025-05-03 16:32 | 20 | GP3.1021.../2420369 | INSTANCE ID :-100779503 SITE ID :- I-UE-SANS-ENB-G001 CALL BY CUSTOMER// DG ISSUE :-DG CHARGGING PROBLEM\ STARTTING PROBLEM \UNDER VOLTAGE ALARM PROBLEM NAME :- Adrash Pande NUMBER :-9580509091 | Task Start | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Raebareli |  | Visit pending | open | Sudhir Awasthi
3 | East | 211790058 | 2025-05-03 16:12 | 40 | 3H.8951.../2421461 | Starting/Stopping Issue | Closed | M/s. SR ENTERPRISE. | Revenus Industries Pvt. Ltd. - Barasat | 46 | SE found EGR Valve alarm Then flash the ECU and clear the code Then start the engine and found engine run good onload condition ok. | CLOSED | Prosanjit saha | Under Observation
47 | NORTH | 211789997 | 2025-05-03 16:00 | 250 | DV8.9840.../2420003 | Voltage issue | Closed | Kundan Refinery P. Ltd. | Paluck Technologies Ltd. - Gurgaon | 7 | GAS ENGINE- Today we visited the site with Jackson and KOEL team check the parameters and Started the Genset on load and found Load is varition is 25-30 kw frequently. As per Data logging of Load analyser 239kw load found at logging time. | Closed | Kapil Solanki
48 | NORTH | 211789960 | 2025-05-03 15:56 | 125.4 | 4H.8041.../2420683 | Amber Lamp Alarm Issue Call By Customer Name :- VIPIN KATHURIA Mobile No :-9891500846 | Task Close | S. FASTNERS | Paluck Technologies Ltd. - Faridabad | 105 | Low adblue level alarm reset the alarm then issue resolve | Closed | Kapil Solanki
96 | North | 211789953 | 2025-05-03 15:53 | 30 | 3H.8902.../2421995 | Genset Trip | Open | THE CLASSIC ESTATE | Suraj Motor Store - Srinagar | 50 | SPN/FMI-51/0 ; Open EGR & found valve is jammed due to low Load (4 KW) clean the valve & remove the codeafter that start the dg set working normally on load (CC done on 24/02/2025) | Closed | Ved Prakash Gupta
42 | South Zone | 211789909 | 2025-05-03 15:49 | 45 | 3H.8951.../2421473 | NCP Alarm Issue Email By - KGD Name -Sivagami S | Open | GOVINDAM | Madhu Engineering Sales & Service - Teynampet,Chennai |  | Cancelled | Cancelled | Mr. NandhaGopal
24 | South | 211789699 | 2025-05-03 15:32 | 15 | GP3.8501.../2420274 | Emergency Switch Issue Call By Customer Name :- Lakshminarayana Sir Mobile No :- 7899781013 | Open | M/s. Sree Vijaya Durga Petro Mart | KALA Care Global LLP - Ballari | NA | Visit pending | Open | Mr. Anil Kumar H G
29 | South zone | 211789658 | 2025-05-03 15:25 | 125.4 | 4H.8042.C4../2420533 | Load and Tripping issue Call By Customer Name :- Shishir Kumar Mobile No:-8884517180 | Task Start | Srinivasa enterprises | Surya Power Services - Peenya, Bangalore | 14 | Customer load side issue, customer using concrete mixer and pump, At that time engine RPM is dropping. | closed | Mr. Anil Kumar H G
49 | NORTH | 211789653 | 2025-05-03 15:23 | 40 | 3H.8951.../2421371 | dg frequent given alarm and dg stop LLOP | Open | ATC Telecom Infrastructure Private Limited | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi
34 | South zone | 211789625 | 2025-05-03 15:20 | 30 | 3H.8902.../2422076 | Battery issue | Open | Axis Bank Ltd | G-Care Diesels Private Limited - Ernakulam | 7 | Found battery voltage low. Battery given to changing. Battery charger not given input connection. Advice customer to give input eb connection for charger. | Closed | Mr. Sanjaimon S
6 | East | 211789617 | 2025-05-03 15:19 | 30 | 3H.8902.../2420512 | Door lock Issue Call By Customer Name :- Nitish kumar Mobile No :- 8709729151 | Task Start | Birju Chola. | HACS Engineering and Tech Private Limited - Dhanbad | 36 | Door lock issue- not closing properly so adjusted its locking hinge after that issue resolved. | CLOSED | Prabhakar Kumar
97 | North | 211789538 | 2025-05-03 15:10 | 320 | F6.8802.../2420096 | Starting/Stopping Issue | Closed | Gurdev Hospital | SAAN Royal Power Solutions Private Limited - Zirakpur | 75 | Update pending | Open | Ved Prakash Gupta
5 | South zone | 211789454 | 2025-05-03 14:57 | 500 | DV8.8501.C4../2420256 | Starting Issue Call By Customer Name :- Chndur Mobile No :-9176278928 | Task Start | Admach Auto Inustries India Pvt. Ltd. | Bharath Diesel Sales and Service - Chennai | 29 | Multiple fault showing on Ikonnect tool, clear the code, again pop-up then flash the DCU 2, fault code gone. When running on idle found no issue. But When running on load 657/5 pop-up. | task start | Mr. NandhaGopal
50 | NORTH | 211789387 | 2025-05-03 14:52 | 250 | F6.8841.../2420418 | Starting/Stopping Issue | Task Start | ACME ELECTRICAL & INDUSTRIAL CO | S. R Engines Sales And Service - LUCKNOW | 36 | check the engine then found that fuse of battery charger got blown then change the fuse then start the engine engine normally working | Closed | Sudhir Awasthi
4 | South zone | 211789358 | 2025-05-03 14:36 | 82.5 | 5H.8901.../2420044 | Starting issue Call By Service Dealer Name :- Pratap Mobile No :- 07722070544 | Task Start | P. M. C. Precast Products | Bharath Diesel Sales and Service - Chennai | 86 | 1761/18 top up the DEF and Clear the DTC | closed | Mr. NandhaGopal
4 | East | 211789327 | 2025-05-03 14:31 | 58.5 | T4.8941.../2423099 | Starting/Stopping Issue | Closed | Sri Balaji Enterprises | K.C. Diesel Services - East Sikkim | 6 | Customer Pressed the emergency switch after that released the switch ,Issue resolved | CLOSED | Prosanjit saha
24 | South zone | 211789287 | 2025-05-03 14:25 | 58.5 | T4.8941.../2421754 | Power Supply issue Called by Customer Name :Madhumohan Number:9986507632 | Task Start | LG ELECTRONICS INDIA LIMITED | Surya Power Services - Peenya, Bangalore | 172 | check and found battery distill water low | closed | Mr. Anil Kumar H G
51 | NORTH | 211789175 | 2025-05-03 14:03 | 40 | 3H.8951.../2421356 | Door Look Issue Call By Customer Name :- SHIV KUMAR CHAUDHARY Mobile No 7727870400 | Task Start | KOUSHALA RAM S/O PADMA RAM | Rajdhani Diesels and Electricals - Barmer |  | Cancelled | Cancelled | Gourav sharma
15 | West | 211789108 | 2025-05-03 13:59 | 160 | 6H.8475.../2420299 | Balck Smoke Issue Call By Customer Name :-Aanand .. Mobile No :- 9016720930 | Task Start | SUDHAN POWER TECH | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 507 | Adblue level low so top up . | Closed | Jagdeep Saini
16 | West | 211788895 | 2025-05-03 13:20 | 15 | GP3.8501.../2421127 | Red Lamp On Alarm Call By Customer Name :- 9324052368 Mobile No :-Santosh Sir | Open | Patel Retail Pvt. Ltd. | Transcreek Engineers Pvt. Ltd. - Bhiwandi |  | cancelled | Closed | Jagdeep Saini
52 | NORTH | 211788849 | 2025-05-03 13:17 | 15 | GP3.8501.../2420834 | Trip_Genset_High_Voltage | Task Start | Amar Jyoti Petrol Pump. | Rajdhani Diesels and Electricals - Jodhpur |  | Cancelled-Problem solve in Telephonic discussion | Cancelled | Gourav sharma
19 | West | 211788723 | 2025-05-03 12:57 | 125.4 | 4H.8042.C4../2421052 | Error code | Closed | Hotel Sanket Cafe | Mahalaxmi Diesels - Chiplun | 134 | Error code 516166 connect ikonnect and clear error code. | Closed | Jagdeep Saini
30 | South zone | 211788642 | 2025-05-03 12:47 | 160 | 6H.8475.../2420074 | Oil Leakage Issue Call By Customer Name :- Gopla Krishna Mobile No :-9480608324 | Task Start | SVG CONTROL SYSTEMS PVT LTD | Surya Power Services - Peenya, Bangalore | 142 | leakage water pump to radiator bottom house pipe, leakage | closed | Mr. Anil Kumar H G
53 | NORTH | 211788565 | 2025-05-03 12:39 | 40 | 3H.8951.../2320107 | Low Battery Alarm Issue Display issue Call By Customer Name :-Vikram .. Mobile No :-9810052795 | Closed | SRB EXPORTS PVT LTD | Vidyut Engineers - Noida | 136 | Update pending | open | Kapil Solanki
7 | South zone | 211788585 | 2025-05-03 12:39 | 0 | DV8.8542.C4../2420139 | Feed Pump not Working | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Feed pump not working, replace the same | task start | Mr. NandhaGopal
98 | North | 211788395 | 2025-05-03 12:20 | 125.4 | 4H.8041.../2320055 | Starting/Stopping Issue | Closed | Pri Oil And Gas Private Limited | SAAN Royal Power Solutions Private Limited - Sonipat | 150 | Found battery voltage low(9.1 V) because Mains supply to battery charger was not installed so install the same & resolve the Issue | Closed | Ved Prakash Gupta
23 | South | 211788354 | 2025-05-03 12:14 | 15 | GP3.8501.../2420804 | Electrical Problems | Open | BRUNDAVANA CONSTRUCTIONS PRIVATE LIMITED. | KALA Care Global LLP - Hospet | NA | Visit pending | Open | Mr. Anil Kumar H G
7 | East | 211788339 | 2025-05-03 12:06 | 15 | GP3.8501.../2420548 | Under Speed Alarm Problem Call by : Customer Name :Mohammed Jaffer Contact :9791064557 | Closed | Shiv Sankar Diesels | Hibreed Engineering Pvt. Ltd. - Guwahati | 107 | voltage was fluctuation 240-250V on load set the stability in the AVR by rotating clockwise issue resolved also have an trail for an hour found no issue | CLOSED | Ujjwal Das
8 | East | 211788248 | 2025-05-03 11:56 | 30 | 3H.8902.../2420087 | Starting issue Call By Customer Name :- Bimsingh Mobile No:-9588254146 | Task Start | Indian Army | Green Powerline - Tezpur | 83 | SPN: 2802,FMI: 4, battery discharged so need to charge the battery | CLOSED | Ujjwal Das
54 | NORTH | 211788182 | 2025-05-03 11:44 | 7.5 | D3.8305.../2400181 | Leakage Issue | Under Monitoring | Delhi Metro Rail Corporation D. M. R. C. | OVN Industries Private Limited - New Delhi | 25 | Oil through from exhaust side load-2.4KW, PF-1.11, RPM-1554 | open | Kapil Solanki
55 | NORTH | 211788170 | 2025-05-03 11:40 | 20 | GP3.8601.../2421270 | Starting/Stopping Issue | Task Start | MANOJ PHARMA | Paluck Technologies Ltd. - Faridabad | 3.51 | Found fuel sensor was faulty High fuel level alarm | open | Kapil Solanki
56 | NORTH | 211788136 | 2025-05-03 11:30 | 25 | GP3.8702.../2420048 | loading/ flecture issue Call by Customer Name :-Keshav NO :-9654019499 | Closed | Jitender Kumar | Paluck Technologies Ltd. - Gurgaon | 408 | Flactute the light then check & found earthing wire was loose so, tightness the same then isuue resolve | Closed | Kapil Solanki
57 | NORTH | 211788054 | 2025-05-03 11:15 | 82.5 | 5H.8901.../2420644 | Starting Issue Call By Customer Name :- Tarun Sethi Mobile No :- 9899714253 | Closed | TARUN SETHI | Vidyut Engineers - New Delhi | 2.1 | Found in panel 11 number wire was loose so this reason was d.g set not be start retight the wire after the start the dg set was proper working in manual mode and automatic | Closed | Kapil Solanki
99 | North | 211788001 | 2025-05-03 11:06 | 35 | 3H.8902.../2422400 | Starting/Stopping Issue | Task Start | Axis Bank Ltd | Suraj Motor Store - Srinagar | 26 | Update pending | Open | Ved Prakash Gupta
58 | NORTH | 211787994 | 2025-05-03 11:04 | 500 | DV8.8501.C4../2320042 | error code problem | Task Start | KEDAR DRUGS AND PHARMACEUTICALS PRIVATE LIMITED | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 69 | found ECU malfunc warning then top-up DFE Laval and clear alarm and start engine running normally | Closed | Sudhir Awasthi
25 | South zone | 211787973 | 2025-05-03 10:58 | 500 | DV8.8501.C4../2320070 | Low battry voltage issue Called by Customer Name :Kartik Number:9841896405 | Open | Unitherm Engineers Limited | Bharath Diesel Sales and Service - Chennai | 163 | Visited the above site checked the engine oil level and coolant level found ok. Checked the battery not charging compliant checked the battery charger working conditions found ok. Checked the battery distilled water level found ok. Checked the charging alternator working condition found ok. Checked the loose connection due to control panel back dide recorrect wire then started the engine checked the dg running condition found ok. | Closed | Mr. NandhaGopal
100 | North | 211787945 | 2025-05-03 10:56 | 58.5 | T4.8941.../2423280 | Electrical Problems | Task Start | SGJ CONSULTANCY PVT LTD | Gen Powers - PATIALA | 14 | Battery Voltage found low ; Mains supply was not given to Charger so installed the same & resolve the Issue | Closed | Ved Prakash Gupta
89 | North | 211787943 | 2025-05-03 10:55 | 82.5 | 5H.8901.../2320076 | Tripping issue Call by customer Name - Vinay Kumar Shaha No - 7734061228 | Closed | Sandhu Construction | SAAN Royal Power Solutions Private Limited - Karnal | 2400 | SPN/FMI- 633/3 check fuel line and fuel filter ; fuel filter found choked so change the sameand check Dosing module in urea leakage then module open and found gasket cracking clean the Dosing pipes ; Gasket need to replace | Open | Ved Prakash Gupta
90 | North | 211787908 | 2025-05-03 10:50 |  | GP3.8702.../2520437 | Lube oil leakage | Task Start | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - kathua | LR- | Oil Cooler O ring defective replace with new one resolve the issue | Closed | Ved Prakash Gupta
91 | North | 211787865 | 2025-05-03 10:41 |  | 3H.8951.../2520441 | Charging alternator | Task Start | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - kathua | LR- | Charging altenator not giving output so sent same for testing to vendor | Open | Ved Prakash Gupta
25 | South zone | 211787857 | 2025-05-03 10:40 | 25 | GP3.8702.../2421241 | MIL Lamp alarm Call by : Customer Name :Deepu Contact : 9731113315 | Closed | Obul Consultancy & Contract Pvt.Ltd | Surya Power Services - Peenya, Bangalore | 1.27 | 2791/4 , clear the DTC | closed | Mr. Anil Kumar H G
31 | South Zone | 211787784 | 2025-05-03 10:33 | 125.4 | 4H.8042.C4../2421040 | Error code issue | Task Start | R & C Infra Engineers Private Limited | KALA Care Global LLP - Hubli | 44 | Observed the error code is SPN 6595/0 AND SPN 1761/16 then connect the tool and check the error code realated issue is low addblue level then top-up the addblue and clear the error code and start the DG with load and trail 30 minutes DG running was Good | Closed | Mr. Anil Kumar H G
9 | East | 211787790 | 2025-05-03 10:31 | 30 | 3H.8902.../2421791 | AMF Panel Fitting Issue Call By Customer Name :-Arvind Mobile No :- 9973466779 | Open | LOHA CONSTRUCTION PRIVATE LIMITED | Globalline India Services Private Limited - Begusarai | 0.76 | No issue in DG only customer want to know about the controller working SR will cancel | OPEN | Prabhakar Kumar
23 | South zone | 211787708 | 2025-05-03 10:22 | 125.4 | 4H.8042.C4../2420511 | Commisoning | Open | KGD NEXGEN GLOBAL ENTERPRISES | Surya Power Services - Bangalore | NA | Cancelled | Cancelled | Mr. Anil Kumar H G
28 | NORTH | 211787669 | 2025-05-03 10:12 | 125.4 | 4H.8041.../2420016 | Red Lamp Alarm issue Call By Customer Name :- Pankaj Juneja Mobile No:-9897599426 | Task Start | Juneja Construction (P) Ltd. | R K Engineers - Meerut | 1897 | Found Dosing module chocked, & Supply module not build up the pressure | open | Sudhir Awasthi
51 | South | 211787641 | 2025-05-03 10:01 | 15 | GP3.8501.../2422183 | Leakage Issue | Closed | SM Partners | G-Care Diesels Private Limited - Ernakulam | 3 | found diesel leak from diesel filter banjo side and tighter the banjo corrected the problem | Closed | Mr. Sanjaimon S
26 | South zone | 211787637 | 2025-05-03 09:58 | 20 | GP3.8601.../2421607 | Starting Issue Call by Customer. Name:- Manikyam Mobile No.:-9064481684 | Task Start | PRECISION POWER SERVICES | Surya Power Services - Mysuru | 6 | Emergency wire loose, tighten the wire | closed | Mr. Anil Kumar H G
24 | WEST | 211787586 | 2025-05-03 09:45 | 160 | 6H.8475.../2420159 | Electrical Problems | Closed | Riyanshi Construction | Unique Techno Services Pvt Ltd. - Gandhidham | 184 | SPN/FMI- 516166/0,1761/16 Low DEF level. | Closed | Vijay patil
16 | South zone | 211787574 | 2025-05-03 09:36 | 40 | 3H.8951.../2420114 | Starting Problem Call by :Customer Name : Manohar Contact : 7569172525 | Closed | Dr. Reddys Foundation | Laxmi Diesels - Srikakulam | 617 | checked the dg found that dg not started due to battery not working so replaced the new one then started the dg running found ok | Closed | Mr. MD Saleem
92 | North | 211787570 | 2025-05-03 09:33 | 82.5 | 5H.8901.../2420804 | Sensor Aalarm Issue Call By Customer Name :- Naveen Mobile No :- 8222894142 | Closed | FAIRMOUNT HOTELS PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Sonipat | 1056 | SPN-4225/1 SPN-3224/2 SPN-1761/15 SPN-3364/27 SPN-3364/10 SPN-522122/19 SPN-522120/19 SPN-3364/29 then Checked DEF line found chocked, then check DM found Choked & gaskit was defective, then cleaned all the Urea DEF line pipes with hot water then reset the code with Ikonnect tool and cleared all the codes, after that started the DG load trial of DG for 1 hour, now DG is running fine on load and now no code is showing in the display but the customer is using local DEF | Closed | Ved Prakash Gupta
25 | WEST | 211787542 | 2025-05-03 09:26 | 25 | GP3.8702.../2420580 | Starting/Stopping Issue | Closed | Riyanshi Construction | Unique Techno Services Pvt Ltd. - Gandhidham | 624 | SPN/FMI- 2802/4,157/14 Low battery voltage - 9.5V so checked and found charging alternator fuse burnt so replaced it. | Closed | Vijay patil
29 | NORTH | 211787528 | 2025-05-03 08:32 | 625 | DV0.8501.C4../2320022 | Genset Trip | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 58 | Found fuel level sensor connection was loose so, tightness the same | Closed | Kapil Solanki
30 | NORTH | 211786826 | 2025-04-03 20:44 | 250 | F6.8842.C4../2420024 | Red lamp Alarm issue call by customer Name:VIJAY SINGH Number:9557347100 | Closed | RAGHUNATH SINGH VERMA PATEL MP COLD STORAGE | Espiem Engines & Machines (P) Limited - Agra | 39 | Low def level topup the def then issue resolve & reset the alarm | Closed | Sudhir Awasthi
30 | South zone | 211786817 | 2025-04-03 20:05 | 25 | GP3.8702.../2421446 | Starting Problem (oil leakage problem) Call by : Customer Name : K Dileep Kumar Contact : 919885379887 | Task Start | Srikalahasti filling station | Ultimate Power Source - Tirupati | 1 | checked the battery voltage is low after that putting battery in out side shop battery charging next day will taken battery fitted the connected the battery charger also, | Closed | Mr. NandhaGopal | Update Rquired
2 | South zone | 211786790 | 2025-04-03 19:21 | 15 | GP3.8501.../2320007 | Error Code Issue Call By Customer Name :- Prabhakar Mobile No :-9176669465 | Closed | S. K. Agency. | Bharath Diesel Sales and Service - Arni | 125 | 2A ferule number wiring loose connection then properly tightness connecte | closed | Mr. NandhaGopal
20 | South zone | 211786686 | 2025-04-03 18:48 | 125.4 | 4H.8042.C4../2420828 | Starting Problem Call by : Customer Name : Naidu Vijay Contact : 9963944802 | Closed | SVC Cinemas | Powerlinks Infra Tech Pvt Ltd - L B Nagar | 21 | engine panal board in battery Wiring loose connections, So arrest the Compliant is OK normal. | Closed | Mr. Sanjaimon S
22 | WEST | 211786680 | 2025-04-03 18:45 | 320 | F6.8802.../2420283 | Voltage Issue Call By Customer Name:-Sachin . No:-8889908014 | Closed | Cipla. | Natraj Power Tech - Indore | 11 | Customer side issue(AC & Cold storage issue) | Closed | Vijay patil
31 | NORTH | 211786709 | 2025-04-03 18:40 | 58.5 | T4.8941.../2520013 | Diesel leakage issue Email By - KGD Name - Gautam | Closed | CLASSIC BITUMEN PRIVATE LIMITED | Rajdhani Diesels and Electricals - Barmer | 4 | Found fuel level sensor connector was loose so connected the same | Closed | Gourav Sharma
32 | NORTH | 211786021 | 2025-04-03 17:16 | 58.5 | T4.8941.../2422616 | Starting Issue Call By Customer Name :- SUNIL GUPTA Mobile No 9910995020 | Closed | RATAN INDUSTRIES | Paluck Technologies Ltd. - Ghaziabad | 3 | find panel fuse blown which was replaced with available one in panel. | Closed | Kapil Solanki
33 | NORTH | 211786018 | 2025-04-03 17:15 | 5.5 | CC1.1013.../2400266 | Under Voltage Alarm Issue. Call By Customer. Name:-Sparsh Mobile No.:6386425820 | Task Start | IDBI Bank | S. R Engines Sales And Service - LUCKNOW |  | Update pending | open | Sudhir Awasthi
34 | NORTH | 211785848 | 2025-04-03 16:31 | 82.5 | 5H.8901.../2420898 | Starting/Stopping Issue | Closed | GOPAL TRADERS | Espiem Engines & Machines (P) Limited - Aligarh | 3 | SPN/FMI 3031/14 High Adblue alarm so, flash the latest file | Closed | Sudhir Awasthi
35 | NORTH | 211785815 | 2025-04-03 16:26 | 82.5 | 5H.8901.../2320023 | Emergency alarm issue Call by customer Name - Arun Kumar No - 9999311334 | Closed | AGNISYS TECHNOLOGY PRIVATE LIMITED | Vidyut Engineers - Noida | 104 | Update pending | open | Kapil Solanki
36 | NORTH | 211785772 | 2025-04-03 16:13 | 30 | 3H.8902.../2420576 | Starting Issue Email By KGD Name:-Neeraj Saini | Closed | Dudani Hospital & Rehabilitation Centre | Pratap Diesels Pvt. Ltd. - Alwar | 77 | high coolent temp.checked coolent level found recovery bottle empty bring coolent and add in recovery bottle and radiator and checked for leakage found coolent drain hose clamps loose | Closed | Gourav Sharma
12 | South zone | 211785678 | 2025-04-03 15:58 | 15 | GP3.8501.../2420407 | Starting/Stopping Issue | Closed | ALUMINA CARBIDES INC | Surya Power Services - Billekahalli | 26 | DG not stating in auto mode, check and found that auto sensoning wire was loose in amf panel | closed | Mr. Anil Kumar H G
37 | NORTH | 211785632 | 2025-04-03 15:46 | 40 | 3H.8951.../2320076 | Maintenance Due Alarm And Emergency Alarm Call By Customer Name :- Gurdeep Singh Mobile No :- 7503779670 | Closed | PANDA INTERNATIONAL PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 524 | Reset the maintenance due alarm | Closed | Kapil Solanki
3 | South zone | 211785605 | 2025-04-03 15:44 | 625 | DV0.8501.C4../2320014 | Errore Problem Call by : Customer Name :Rajekumar Contact :9043632187 | Closed | VIM ALLOY PRIVATE LIMITED | Bharath Diesel Sales and Service - Chennai | 43 | ECU amber alarm showing on controller, just remove the alarm, no other issue found | closed | Mr. NandhaGopal | KRM Check
27 | South zone | 211785559 | 2025-04-03 15:37 | 82.5 | 5H.8901.../2420755 | Starting Problem Call by : Customer Name :Mahesh Contact : 8971523128 | Closed | PRESTIGE ESTATES PROJECTS LIMITED | Surya Power Services - Bommasandra, Bangalore | 7 | engine not starting due to the 2 c waring really leg cut replace the new 2 c warring | closed | Mr. Anil Kumar H G
10 | East | 211785592 | 2025-04-03 15:35 | 10 | GP3.8301.../2420445 | starting problem | Closed | SHIVAM HOUSE OF ENTERPRISE | Hibreed Engineering Pvt. Ltd. - Guwahati | 3 | LR- Replaced EGR valve issue, SE visited and Checked EGR connector and its continuity and voltage found ok then removed the EGR found the it was stuck so replaced by new one then issue resolved | CLOSED | Ujjwal Das
1 | East | 211785442 | 2025-04-03 15:29 | 125.4 | 4H.8041.../2420688 | Leakage Issue | Open | ABINASH DASH | Gangpur Sales and Services - Berhampur | 57 | SE found no leakage in DG,DG running condition was normal | CLOSED | Ujjwal Das
24 | WEST | 211785440 | 45750.6438 | 30 | 3H.8902.../2520075 | Engine Trip by low oil | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | error code 100/3 ,.low oil pressure sensor alarm, check connection found ok so replace lop sensor | Closed | Jagdeep Saini
6 | South zone | 211785431 | 2025-04-03 15:24 | 0 | DV2.8501.C4../2520015 | FLYWHEEL REPLACMENT | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | update pending | task start | Mr. NandhaGopal
22 | South | 211785396 | 2025-04-03 15:20 | 0 | GP3.8601.../2520109 | ENGINE HUNTING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Engine hunting issue yet not resolved, need to replace Feed pump | Task Start | Mr. NandhaGopal
21 | South | 211785383 | 2025-04-03 15:17 | 0 | GP3.8501.../2520262 | FUEL RETURN HOSE FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | inspectied the dg noticed the fuel leak for fuel leakoff hose , need to be changed hose | Task Start | Mr. NandhaGopal
38 | NORTH | 211785377 | 2025-04-03 15:16 | 82.5 | 5H.8901.../2420373 | Leakage Issue | Closed | SHAKTI PACKERS INDIA PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | 46 | coolant leakege then all hose pipe cleam tight and coolant leakege problem done low coolant top up | Closed | Kapil Solanki
20 | South | 211785329 | 2025-04-03 15:08 | 25 | GP3.8702.../2421061 | Red lamp alarm issue Call by : Customer Name : Shivayya Swamy Contact : 9008528421 | Open | GUTTI SHANTHI | KALA Care Global LLP - Ballari | NA | Visit pending | Open | Mr. Anil Kumar H G
39 | NORTH | 211785325 | 2025-04-03 15:07 | 15 | GP3.8501.../2320032 | Red lamp on alarm issue Called by customer Name :Robin Number : 9319721286 | Closed | MEDANTA LABS | OVN Industries Private Limited - New Delhi | 30 | found the dg battery charger not working then new battery charger to be change | Closed | Kapil Solanki
50 | South Zone | 211784974 | 2025-04-03 13:44 | 125.4 | 4H.8042.C4../2420097 | Starting Issue Call By Customer Name :- Venket Mobile No :- 8884418908 | Closed | N. V. Hospital. | Prasad Power Engineers - Davangere | 9 | emergency button pushed, release the button | Closed | Mr. Anil Kumar H G
34 | NORTH | 211784921 | 2025-04-03 13:39 | 15 | GP3.8501.../2421084 | Control issue | Closed | HARJEET SINGH S/O GURBACHAN SINGH | Megatron Engineers - Hoshiarpur | 63 | Controller not on check & found ON, OFF switch lock was removed so, connect the same after issue resolve | Closed | Ved Prakash Gupta
17 | West | 211784937 | 2025-04-03 13:38 | 500 | DV8.9313.../2420039 | Fuel filter damage | Closed | SENIOR SECTION ENGINEERS | Transcreek Engineers Pvt. Ltd. - Mumbai | 2.46 | Fuel fliter damage from outside so replace the fuel filter. | Closed | Jagdeep Saini
11 | East | 211784803 | 2025-04-03 13:19 | 30 | 3H.8902.../2420140 | Automation issue Call By Customer Name :- Pratik Mobile No :- 8340504876 | Closed | Balram Children Hospital. | HACS Engineering and Tech Private Limited - Ranchi | 193 | customer side issue mains voltage is unhealthy it some time drop below 180V due to which DG start in auto mode no issue found in DG all sensing wire also found tighten and voltage drop also seen in multimeter | CLOSED | Prabhakar Kumar
23 | South Zone | 211784550 | 2025-04-03 12:39 | 250 | F6.8842.C4../2420101 | Starting/Stopping Issue | Task Start | Appidi Usha Kiran | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | visit pending | Task Start | Mr. MD Saleem
39 | South Zone | 211784552 | 2025-04-03 12:39 | 58.5 | T4.8941.../2421405 | Canopy door lock problem Call by : Customer Name : Sashi kumar Contact : 9513313113 | Open | Rangatorana | KALA Care Global LLP - Ballari |  | visit pending | Open | Mr. Anil Kumar H G
35 | NORTH | 211784467 | 2025-04-03 12:31 | 125.4 | 4H.8041.../2420184 | Tripping Issue Call By Customer Name - Omkar Number - 9779958732 | Task Start | Makkar Motors Pvt. Ltd. | Dynamic Engineering Services - Jalandhar |  | Visit pending | Open | Ved Prakash Gupta
93 | North | 211784467 | 2025-04-03 12:31 | 125.4 | 4H.8041.../2420184 | Tripping Issue Call By Customer Name - Omkar Number - 9779958732 | Closed | Makkar Motors Pvt. Ltd. | Dynamic Engineering Services - Jalandhar | 161 | SPN/FMI-1761/16 ; AdBlue Level LOW,Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta
12 | East | 211784456 | 2025-04-03 12:24 | 125 | 4H.8042.C4../2520142 | FAILED TO START FUSE GOT BURNT | Task Start | POWERLINE GREEN | Hibreed Engineering Pvt. Ltd. - Nagaon | LR | charging alternator defective- found not output voltage as well as controller D+ sensing wire connection and voltage found OK so replaced by new one issue resolved | OPEN | Ujjwal Das
7 | South zone | 211784427 | 2025-04-03 12:23 | 58.5 | T4.8941.../2421280 | Door lock problem Call by : Customer Name :Rajesh Contact :7994160916 | Closed | THYOHAR DIAMONDS LLP | G-Care Diesels Private Limited - Thrissur | 32 | dg door locks problem rectified. Door lock clamp loose condition. Tight the clamp. Problem clear. D | Closed | Mr. Sanjaimon S
36 | NORTH | 211784434 | 2025-04-03 12:19 | 7.5 | D3.8305.../2400015 | Starting issue Call By Customer Name :- BRIJRAJ CHATURVEDI Mobile No :-9897059070 | Closed | BRIJRAJ CHATURVEDI | Espiem Engines & Machines (P) Limited - Agra | 11 | Airlock in fuel line so, remove the air after that issue resolve | Closed | Sudhir Awasthi
6 | NORTH | 211784417 | 2025-04-03 12:18 | 320 | F6.8802.../2320051 | Starting Issue Email By Customer Name:-Jeet Singh | Closed | Sri Dwarkadheesh Polymers Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 115 | Over load issue | Closed | Gourav Sharma
7 | NORTH | 211784415 | 2025-04-03 12:18 | 500 | DV8.8501.C4../2420131 | Starting/Stopping Issue | Closed | TECHNO THERMAL TRETARS PVT LTD | Pratap Diesels Pvt. Ltd. - Bhiwadi | 93 | Customer always stop by the Emergency , So same Educate the customer | Closed | Gourav Sharma
8 | NORTH | 211784303 | 2025-04-03 11:51 | 58.5 | T4.8941.../2421674 | Starting/Stopping Issue | Task Start | SHIV SHAKTI ENGINEERING | S. R Engines Sales And Service - Gorakhpur | 221 | R 66 Y82 B 84 load ampere overload issue so, same Educate the customer | Closed | Sudhir Awasthi
41 | South Zone | 211784225 | 2025-04-03 11:34 | 30 | 3H.8902.../2420352 | Starting Issue Email By - KGD Name -A.K.Engineers Gulbarga | Open | M/S RAINBOW MEDICALS | KALA Care Global LLP - Kalaburagi |  | visit pending | Open | Mr. Anil Kumar H G
28 | South zone | 211784219 | 2025-04-03 11:34 | 15 | GP3.8501.../2421835 | Starting issue called by customer Name : RAJESH Number : 6383825495 | Closed | KARUR VYSYA BANK-KOLATHUR BRANCH | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 2 | Emergency Disconnect switch is activated condition ignition commend cut so engine is not running Condition, Emergency disconnect switch released, now engine is running Condition. | Closed | Mr. NandhaGopal
13 | East | 211784201 | 2025-04-03 11:28 | 15 | GP3.8501.../2421153 | Starting issue Call by customer Name - Aparna Sutradhar No - 9774548608 | Cancelled | Nepack Associates | Johnson Techno Sales & Services - Agartala |  | Cancelled on telephonic communication issue resolved | CANCELLED | Ujjwal Das
6 | West | 211784197 | 2025-04-03 11:27 | 20 | GP3.8601.../2420560 | Starting/Stopping Issue | Task Start | Om Prakash Verma. | Shree Engineering Service - Raipur | 150.26 | Controller R phase sensing 5Ams fuse was burnt. | Closed | Vijay Patil
9 | NORTH | 211784198 | 2025-04-03 11:27 | 160 | 6H.8475.../2420233 | coolant consumption issue Call By Customer Name :-Gordhan Mobile No :-9602270032 | Closed | Dr .Heera Diagnostic Centre Pvt ltd | Rajdhani Diesels and Electricals - Jodhpur | 20 | Found any Coolant leakage but Recovery bottle is Empty so, top up the Coolant | Closed | Gourav Sharma
30 | South Zone | 211784123 | 2025-04-03 11:15 | 125.4 | 4H.8042.C4../2420797 | Alarm problem Call by : Customer Name :Jay Krishan Contact :9562046840 | Task Start | MGL LIFE SCIENCE | EMKAY MOTORS - Kollam | 24 | found an alarm ECU fault and adblue High temperature fault | Task Start | Mr. Sanjaimon S
4 | West | 211784133 | 2025-04-03 11:13 | 160 | 6H.8475.../2420190 | Tripping Issue Email By KGD Name:-Harshad patel | Task Start | Ronak Construction | Unique Techno Services Pvt Ltd. - Ankleshwar | 419 | V belt loose & high DEF temperature alarm so calibrated the ECU with Dummy file. | Closed | Amit Sandlya
10 | NORTH | 211784061 | 2025-04-03 11:05 | 250 | F6.8842.C4../2420067 | LINE REJECTION | Task Start | SHREE KRISHNA COLD STORAGE | Espiem Engines & Machines (P) Limited - Agra | 21 | wiring harness replacement DG is running ok but as observed , DTC 1761/16 appearing also in iKonnect data log saw DEF Level percentage increasing gradually (Taking 2-3 mins to reflect actual DEF level in Data Log) while at GCU it is 74% (actual DEF level). | open | Sudhir Awasthi
14 | East | 211784007 | 2025-04-03 10:54 | 40 | 3H.8951.../2420095 | Starting/Stopping Issue | Closed | M/s. Singh Industries | Green Powerline - Tezpur | 197 | update pending | CLOSED | Ujjwal Das
11 | NORTH | 211783881 | 2025-04-03 10:39 | 30 | 3H.8902.../2320159 | Starting/Stopping Issue | Closed | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 240 | Update pending | open | Kapil Solanki
2 | East | 211783876 | 2025-04-03 10:34 | 40 | 3H.8951.../2420649 | Starting/Stopping Issue | Task Start | FOREVER FORTUNE VENTURE | Gangpur Sales and Services - Dhenkanal | 425 | SE start the engine then found there was a loose connection somewhere all the connections are tightening the same,Issue resolved | CLOSED | Ujjwal Das
10 | South Zone | 211783875 | 2025-04-03 10:33 | 15 | GP3.8501.../2520246 | ENGINE HUNTING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | DG hunting issue, need to change FIP. | Task Start | Mr. NandhaGopal
11 | South Zone | 211783813 | 2025-04-03 10:23 | 0 | GP3.8501.../2520262 | ERROR CODE | Cancelled | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur |  | cancelled | Cancelled | Mr. NandhaGopal
19 | South Zone | 211783785 | 2025-04-03 10:18 | 30 | 3H.8902.../2422402 | starting issue | Task Start | HOTEL GOPI | Madurai Electro Controls - Ramanathapuram |  | visit pending | Task Start | Mr. NandhaGopal
37 | South Zone | 211783802 | 2025-04-03 10:18 | 15 | GP3.8501.../2421414 | Starting/Stopping Issue | Task Start | The Karur Vysya Bank Limited | Electro Controls - Nagercoil |  | update pending | Task Start | Mr. Sanjaimon S
37 | South zone | 211783770 | 2025-04-03 10:08 | 45 | 3H.8951.../2421473 | NCP Alarm Issue Email By - KGD Name -Sivagami S | Closed | GOVINDAM | Madhu Engineering Sales & Service - Teynampet,Chennai | 4 | SPN 2791 and fmi 18, clear the DTC and flash the ECU | Closed | Mr. NandhaGopal
15 | East | 211783750 | 2025-04-03 10:00 | 45 | 3H.8951.../2520086 | Voltage Fluctuation | Closed | MUNDHRA HOSPITAL PRIVATE LIMITED | HACS Engineering and Tech Private Limited - Jamshedpur | 11 | light flickering issue - SE found on load alternator output voltage increases by 10-20V also found load unbalancing this DG is in hospital there is no balance load, but if load is balance then also same problem, replaced the AVR by TAVR but same problem( light flickering increase) today SE will visit site for same | OPEN | Prabhakar Kumar
12 | NORTH | 211783676 | 2025-04-03 09:53 | 500 | DV8.8501.C4../2420013 | Starting/Stopping Issue | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 42 | Update pending | open | Kapil Solanki
13 | NORTH | 211783639 | 2025-04-03 09:44 | 30 | 3H.8902.../2320082 | Starting Issue Call By Customer Name :-Rakb Mobile No :-7017855044 | Task Start | EDS Construction Private Limited | OVN Industries Private Limited - New Delhi | 1243 | started the dg but dg not started due to 2A wire loose from the battery terminals so tight all connections then started the dg and found running is ok | Closed | Kapil Solanki
16 | East | 211783635 | 2025-04-03 09:40 | 58.5 | T4.8941.../2420624 | Silencer broken issue Email By - KGD Name -SUNRISE POWER | Closed | Yadav Tent House | Globalline India Services Private Limited - Darbhanga | 250 | Found expansion bellow damage - DG is on trolley and found no misalignment of the exhaust pipe it's suspected this issue raised due to extra jerk/vibration on DG due to trolley | CLOSED | Prabhakar Kumar | Part and alignment to be check
14 | NORTH | 211783476 | 2025-04-03 09:01 | 125.4 | 4H.8041.../2420112 | Genset Trip | Closed | Accurex Industris | Paluck Technologies Ltd. - Faridabad | 255 | SPN/FMI 3031/14 High Adblue alarm so, flash the Dummy file | Closed | Kapil Solanki
84 | North | 211783444 | 2025-04-03 08:45 | 250 | F6.8841.../2420348 | Electrical Problems | Closed | Xaverian Healthcare & Clinincal Lab. | Gen Powers - Bathinda | 40 | SPN/FMI- 655/5 & 3031/14. As per 655/5 injector wire found broken wire in cylinder head ;repaired and Engine ECU reflashed as per koel instructions due to 3031/14 code. | Closed | Ved Prakash Gupta
15 | NORTH | 211783427 | 2025-04-03 08:25 | 57 | T4.8941.../2320147 | Electrical Problems | Closed | Arihant Machinery Store | OVN Industries Private Limited - New Delhi | 226 | Battery terminal dusty, Air lock in fuel line because filter & Benjo was loose so, tightness the same then issue resolve | Closed | Kapil Solanki
16 | NORTH | 211783422 | 2025-04-03 08:13 | 82.5 | 5H.8901.../2420347 | Auto Stopping issue Call By Customer Name :- Asad Bhatti Mobile No.:- 9968663656 | Closed | Annat C.G.H.S. Ltd. | OVN Industries Private Limited - New Delhi | 18 | During night DG was start in auto after set the voltage VMR Relay Voltage set 265 | Closed | Kapil Solanki
17 | NORTH | 211783419 | 2025-04-03 08:07 | 250 | F6.8841.../2420127 | Starting/Stopping Issue | Closed | KIDS CLINIC INDIA LTD | OVN Industries Private Limited - New Delhi | 1995 | Serevice required, No issue in DG | Closed | Kapil Solanki
1 | West | 211783417 | 2025-04-03 07:28 | 35 | 3H.8902.../2422242 | Automation Issue Call By Customer Name - Shubham Patel Number - 7869774708 | Closed | ST. JUDEâ€™S HIGHER SECONDARY SCHOOL | Natraj Power Tech - Barwani | 7 | SPN/FMI-2791/18, Calibtrated the ECU. | Closed | Vijay Patil
1 | East | 211782889 | 2025-03-03 20:58 | 15 | GP3.8501.../2520097 | Staring Issue Call By KGD Name:-Alisha No:-9647904206 | Open | Alisha Gurung | K.C. Diesel Services - SILIGURI |  | Visit Pending | OPEN | Prosanjit saha
21 | East | 211782889 | 2025-03-03 20:58 | 15 | GP3.8501.../2520097 | Staring Issue Call By KGD Name:-Alisha No:-9647904206 | Open | Alisha Gurung | K.C. Diesel Services - SILIGURI | 56 | Today SE will visit site | OPEN | Prosanjit saha
85 | North | 211782833 | 2025-03-03 19:07 | 200 | 6H.8435.../2420253 | Controller issue Email By - GOEM Name - Anil Wagh | Task Start | HDFC BANK LIMITED | Suraj Motor Store - Jammu | 36 | Automation Issue , wire found loose in pannel for Auto command so corrected the same & resolve the Issue | Closed | Ved Prakash Gupta
13 | East | 211782800 | 2025-03-03 18:47 | 25 | GP3.8702.../2421606 | Starting Issue Call By Customer Name :-Father Jini Mobile No :-7478006368 | Open | St. Claret Hostel | HACS Engineering and Tech Private Limited - Deoghar | 59 | unbalanced load, y phase is under load. We have chcek the complaint over call and ask customer to call electrician for equal load divide. | CLOSED | Prabhakar Kumar
59 | South Zone | 211782736 | 2025-03-03 18:16 | 20 | GP3.8601.../2421510 | Starting issue Call By KGD Name :- Babita Mobile No :-9448570905 | Closed | SLN Coffee Pvt. Ltd. | Prasad Power Engineers - Tumkur | 2 | Airlock issue, remove the air lock | Closed | Mr. Anil Kumar H G
18 | NORTH | 211782734 | 2025-03-03 18:15 | 82.5 | 5H.8901.../2320088 | Starting/Stopping Issue | Closed | Jain Multispeciality Hospitals Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 252 | auto panel connection loose and tight | Closed | Kapil Solanki
2 | East | 211782405 | 2025-03-03 17:53 | 625 | DV0.8501.C4../2420160 | Starting Issue Email By - GOEM Name - Saktimay Satpathy | Task Start | RUNGTA SONS PVT LTD. | Gangpur Sales and Services - Keonjhar |  | Today SE will visit site | OPEN | Ujjwal Das
6 | East | 211782405 | 2025-03-03 17:53 | 625 | DV0.8501.C4../2420160 | Starting Issue Email By - GOEM Name - Saktimay Satpathy | Task Start | RUNGTA SONS PVT LTD. | Gangpur Sales and Services - Keonjhar | 13 | Not starting issue. SE is visiting today | OPEN | Ujjwal Das | Pig tail part number
19 | NORTH | 211782350 | 2025-03-03 17:40 | 500 | DV8.8501.C4../2420056 | ECU Lamp On Alarm. Call By Customer Name :- Krishan Kumar Sharma Mobile No :-7830295735 | Closed | Infratech Solution | Vidyut Engineers - Noida | 32 | DEF level low topup the def & reset the alarm with i-konnect tool then issue is resolve | Closed | Kapil Solanki
20 | NORTH | 211782334 | 2025-03-03 17:37 | 750 | DV2.8501.C4../2420149 | ECU Lamp On Alarm. Call By Customer Name :- Krishan Kumar Sharma Mobile No :-7830295735 | Closed | Infratech Solutions | Vidyut Engineers - Noida | 23 | DEF level low topup the def & reset the alarm with i-konnect tool then issue is resolve | Closed | Kapil Solanki
86 | North | 211782098 | 2025-03-03 17:10 | 125.4 | 4H.8042.C4../2420237 | Error Cod Issue OIl Consumtion Issue Call By Customer Name :- Goutam Sharma Mobile No :- 9002919389 | Closed | DHUNSERI POLY FILMS PVT LTD | Suraj Motor Store - kathua | 275 | found error code 3031/14 showing on display so connect the tool-tab & clear the code after complete the work ;will flash the ECU by today | Open | Ved Prakash Gupta
16 | East | 211781944 | 2025-03-03 16:47 | 20 | GP3.8601.../2421241 | Starting issue Call by Service Dealer Name - Parsuram Singh No - 9151061241 | Task Start | Raunaq T. V. S. | HACS Engineering and Tech Private Limited - Jamshedpur | 66 | No issue found at site. SR to be cancelled | OPEN | Prabhakar Kumar
11 | South zone | 211781928 | 2025-03-03 16:47 | 125.4 | 4H.8042.C4../2520076 | Starting Problem Call by : Customer Name :Shaera Contact :9037344188 | Closed | ANSAR MASJID | G-Care Diesels Private Limited - Malappuram | 41 | Attented site checked engine oil leakage oil filter assembly to fip pipe broken condition.as per customer urgency and site issue pipe crimbed in local hydraulic team .crimbed pipe refitted | Closed | Mr. Sanjaimon S
2 | West | 211781901 | 2025-03-03 16:37 | 25 | GP3.8702.../2421526 | Low Oil Level Call By Customer Name:-Nitin . No:-8669092138 | Task Start | RHC. Constructions Unit-II UP. | Natraj Power Tech - Khandwa | 947 | Oil was coming from breather pipe and exhaust side, first service has been done. Customer is not agreeing to open the rocker cover. | OPEN | Vijay Patil | Details required
21 | NORTH | 211781848 | 2025-03-03 16:32 | 30 | 3H.8902.../2420948 | Starting Issue Call By Customer Name :- DEVENDER JANGRA Mobile No:-9868487598 | Closed | MANMOHAN FURNITURE | OVN Industries Private Limited - New Delhi | 245 | Low fuel level, topup the fuel remove the air then start the dg after that issue resolve | Closed | Kapil Solanki
18 | West | 211781884 | 2025-03-03 16:31 | 250 | F6.8841.../2320029 | Yesterday we noticed a beep sound from digi set also fuel indicator shows same level since last 10 days | Open | HDFC Bank Limited | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | cancelled | Closed | Jagdeep Saini
18 | East | 211781792 | 2025-03-03 16:19 | 20 | GP3.8601.../2421367 | Power supply issue Call by customer Name - Ajay Shaha No - 8486037521 | Open | Shine Enterprise | Hibreed Engineering Pvt. Ltd. - Guwahati | 20 | No output voltage. Output voltage found coming to the load panel and it is not going outside from panel. Panel issue. | CLOSED | Ujjwal Das
14 | East | 211781752 | 2025-03-03 16:08 | 5.5 | CC1.1013.../2400171 | Electrical Problems | Task Start | Mahadev Advertiser | HACS Engineering and Tech Private Limited - Deoghar | 9.1 | Inverter module is changed due to no output voltage. SR not close due to EFSR issue. | OPEN | Prabhakar Kumar
22 | NORTH | 211781727 | 2025-03-03 16:06 | 160 | 6H.8475.../2420031 | Belt broken and I-bolt damage Email By - GOEM Name -Product Support | Closed | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 3221 | No issue in DG | Closed | Kapil Solanki
21 | South Zone | 211781668 | 2025-03-03 15:59 | 30 | 3H.8902.../2420394 | Exhaust Fan problem Call by : Customer Name :Nazeer Contact :9633602477 | Task Start | Veluthamanal Muslim Jamayath | EMKAY MOTORS - Kollam |  | visit pending | Task Start | Mr. Sanjaimon S
36 | South zone | 211781475 | 2025-03-03 15:17 | 82.5 | 5H.8901.../2420145 | Starting/Stopping Issue | Closed | Cameo Bakery. | Electro Controls - Palakkad | 13 | Visited the site, as per customer request , customer need to reduce the cooling time below 30 sec as per koel decision cooling time reduced to 180 seconds . Started the engine found performance ok | Closed | Mr. Sanjaimon S
87 | North | 211781442 | 2025-03-03 15:11 | 125.4 | 4H.8042.C4../2420265 | Call By: Customer Name : Kamal Goswami No 6239810814 | Open | Fair International Jalandhar | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Visit pending | Open | Ved Prakash Gupta
12 | West | 211781458 | 2025-03-03 15:10 | 5 | CP1.1003.../2400024 | Overheating Issue Email By - KGD Name - Vishal Raut | Closed | Jhulelal Ice-creams | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | unbalance load | Closed | Jagdeep Saini
23 | NORTH | 211781408 | 2025-03-03 15:01 | 250 | F6.8842.C4../2420059 | Electrical Problems | Closed | New S.L & Sons Refrigeration | Deep Jyoti Electricals and Services - Moradabad | 49 | Low def level topup the def then issue resolve | Closed | Sudhir Awasthi
13 | West | 211781361 | 2025-03-03 14:44 | 125.4 | 4H.8042.C4../2420083 | Starting/Stopping Issue | Closed | Kings Marque Group. . | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 962 | Adblue leakage , so open the dosing module and refittted , under observation. | Closed | Jagdeep Saini
13 | South zone | 211781328 | 2025-03-03 14:37 | 250 | F6.8841.../2420103 | Fuel sensor & display problem Call by : Customer Name : Manjunath Contact : 9663202854 | Closed | Asha Sweet Center | Surya Power Services - Peenya, Bangalore | 45 | check the engine fuel gauge is strucked So removed the fuel gauge and correct the fuel gauge | closed | Mr. Anil Kumar H G
88 | North | 211781335 | 2025-03-03 14:35 | 400 | DV8.8542.C4../2420085 | Low coolant and Low oil level Issue Email By - GOEM Name - Poonam Shedage | Task Start | Accurate Powertech India Private Limited | Industrial Power Solutions - LUDHIANA | 19 | Coolant leakage found from reserve Tank due to over Top-up so reduce from same & resolve the Issue | Closed | Ved Prakash Gupta
11 | West | 211781325 | 2025-03-03 14:33 | 125.4 | 4H.8042.C4../2421027 | Electrical Problems | Closed | MD INFRA INDIA PRIVATE LIMITED | Mahalaxmi Diesels - Satara | 105 | Error code 516166 connect ikonnect and clear error code. | Closed | Jagdeep Saini
45 | South Zone | 211781306 | 2025-03-03 14:29 | 45 | 3H.8951.../2421504 | Stoping problem Call by : Customer Name : Shivakumar Contact : 9989449441 | Cancelled | SANJEEVANI HOSPITAL | Powerlinks Infra Tech Pvt Ltd - Khammam |  | cancelled | Cancelled | Mr. MD Saleem
35 | South zone | 211781311 | 2025-03-03 14:29 | 160 | 6H.8475.../2420186 | Starting/Stopping Issue | Closed | Sri Technology Solutions India Pvt. Ltd. | Laxmi Diesels - Visakhapatnam | 20 | During our site visit, it was observed that the engine was tripping due to overload. This was caused by an unequal load distribution. | Closed | Mr. MD Saleem
24 | NORTH | 211781296 | 2025-03-03 14:24 | 20 | GP3.8601.../2420104 | Starting Issue Call By Customer Name :- Shubm . Mobile No :- 9871774661 | Closed | SUSTAIN INFRA | Vidyut Engineers - Noida | 54 | Found maintenance due alarm reset the alarm & battery charger Maine supply connection not available, educate the customer for connection required | Closed | Kapil Solanki
25 | NORTH | 211781227 | 2025-03-03 14:07 | 625 | DV0.8501.C4../2420006 | Ecu malfunc warning | Task Start | Dabas Construction Co. | Vidyut Engineers - New Delhi | 7 | DM not proper working so, replace the same after that issue resolve | Closed | Kapil Solanki | SOP Required
26 | NORTH | 211781236 | 2025-03-03 14:04 | 20 | GP3.1021.../2420275 | INSTANCE ID :-100777774 SITE ID :- I-UE-FZAD-ENB-0186 CALL BY CUSTOMER// DG ISSUE :-DG STARTING PROBLEM NAME :- RAJVENDR YADAV NUMBER :-9621704752 | Closed | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Faizabad | 1323 | Air filter chowk and cranking device faulty arange device fitting starting on running but maintenance due alarm & service due | Closed | Sudhir Awasthi
27 | NORTH | 211781213 | 2025-03-03 14:01 | 125 | F6.9840.../2420031 | Under Speed Alarm issue Call By Customer Name :- Durgesh Awasthi Mobile No :- 9602907049 | Closed | UNIQUE POWER SOLUTION. | Vidyut Engineers - Noida | 33 | Gas Engine - 3217/15 , 3607/5 reset the alarm with laptop | Closed | Kapil Solanki | Training Required
1 | North | 211781182 | 2025-03-03 13:55 | 58.5 | T4.8941.../2423102 | Starting Issue Call By Customer Name :- Ankit Das Mobile No:-9919299993 | Open | Das Nursing Home | Espiem Engines & Machines (P) Limited - Farukhabad | 7 | Found Battery terminal loose after tightness DG run ok (CC on 29/01/2025) | Closed | Sudhir Awasthi
2 | North | 211781109 | 2025-03-03 13:35 | 40 | 3H.8951.../2420947 | Inspection/Maintenance | Open | General Electric & Machinery Corporation | Industrial Power Solutions - LUDHIANA |  | Cancelled- Problem solve in PM visit | Cancelled | Ved Prakash Gupta
3 | North | 211781107 | 2025-03-03 13:33 | 58.5 | T4.8941.../2422810 | Low fuel level issue alarm an automation issue call by customer Name:Anup Number:9509797217 | Open | E2P MAART PRIVATE LIMITED | Rajdhani Diesels and Electricals - Jodhpur | 59 | Customer side panel issue Our controller no show the alarm service due ( CC done on 20/11/2024) | Closed | Gourav Sharma
4 | North | 211781077 | 2025-03-03 13:28 | 250 | F6.8841.../2420343 | Tripping Issue Call By Customer Name :- Ayush Sir. Mobile No :-7903029346 | Task Start | DIVYA JYOTI JAGRATI SANSTHAN | OVN Industries Private Limited - New Delhi | 76 | SPN/FMI 100/1, 516166/0, 6595/0 Clear the DTC | Closed | Kapil Solanki
3 | East | 211781094 | 2025-03-03 13:27 | 30 | 3H.8902.../2421670 | Starting/Stopping Issue | Open | PACHAMI BASALT MINING PVT LTD. | Revenus Industries Pvt. Ltd. - Md. Bazar | 205 | 2791/31 (EGR Inducement Shutdown Fault) 100/1 (Engine oil pressure low) ,today SE will visit the site | OPEN | Prosanjit saha
3 | East | 211781094 | 2025-03-03 13:27 | 30 | 3H.8902.../2421670 | Starting/Stopping Issue | Open | PACHAMI BASALT MINING PVT LTD. | Revenus Industries Pvt. Ltd. - Md. Bazar | 205 | 2791/31 (EGR Inducement Shutdown Fault) 100/1 (Engine oil pressure low) ,today SE will visit the site | OPEN | Prosanjit saha
11 | East | 211781063 | 2025-03-03 13:23 | 20 | GP3.8601.../2420651 | Starting/Stopping Issue | Task Start | Hill Billy | Green Powerline - Tezpur | 167 | Wire in NC block of emergency switch was loose. Tighten it and issue has been resolved | CLOSED | Ujjwal Das
5 | North | 211781058 | 2025-03-03 13:22 | 125.4 | 4H.8041.../2420094 | Starting/Stopping Issue | Task Start | Ayushman Multispecialty Hospital | SAAN Royal Power Solutions Private Limited - Hisar | 158 | Low def level topup the def & clear the DTC | Closed | Ved Prakash Gupta
49 | South Zone | 211781052 | 2025-03-03 13:19 | 40 | 3H.8951.../2421174 | Coolant Leakage Problem Call by : Customer Name :Madu Contact : 9663743227 | Closed | THOTA UTHPANNAGALA MARATA SAHAKARA SANGH | Prasad Power Engineers - Davangere | 95 | coolant leakage from radiator hose, tighten th clamp | Closed | Mr. Anil Kumar H G
20 | South zone | 211780906 | 2025-03-03 12:59 | 200 | 6H.8435.../2420223 | Leakage Issue | Task Start | JOYALUKKAS INDIA LIMITED | Surya Power Services - Bangalore | 267 | coolant leakage from radiator hose, tighten the clamp | closed | Mr. Anil Kumar H G
8 | East | 211780905 | 2025-03-03 12:58 | 125.4 | 4H.8042.C4../2420505 | Tripping Issue Call By Customer Name :- Janmeet Chadha Mobile No :-7717411685 | Task Start | ArrisOne BuildTech Pvt. Ltd. | Globalline India Services Private Limited - Muzaffarpur | 7 | Update pending | OPEN | Prabhakar Kumar
10 | West | 211780816 | 2025-03-03 12:33 | 25 | GP3.8702.../2422065 | Tripping Issue Email By - KGD Name - Vishal Raut | Task Start | St.George Balikagram | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 5 | No issue with dg | Closed | Jagdeep Saini
19 | South | 211780763 | 2025-03-03 12:26 | 320 | F6.8802.../2420105 | Aaram sound problem Call by : Customer Name : Dilip Contact : 9603780177 | Task Start | BVRIT HYDERABAD College of Engineering for Women | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 70 | checked the spn 3364 FMI 8 so flash file available so flash the new file | Task Start | Mr. NandhaGopal
1 | South zone | 211780726 | 2025-03-03 12:20 | 125.4 | 4H.8042.C4../2420897 | Abnormal sound Problem Call by : Customer Name :DINESH Contact :8248676890 | Open | ADHINARAYANAN | Bharath Diesel Sales and Service - Arni |  | Cancelled | Cancelled | Mr. NandhaGopal
10 | East | 211780677 | 2025-03-03 12:13 | 10 | GP3.8301.../2420178 | RED LAMP ON | Open | M/s. Skywiew Enterprise & Ganapati Builders | Green Powerline - Dhemaji |  | Idle Gear damaged. PIR will be shared | OPEN | Ujjwal Das
9 | West | 211780676 | 2025-03-03 12:12 | 15 | GP3.8501.../2420649 | Starting/Stopping Issue | Task Start | New Tanishka Cake Cafe | Mahalaxmi Diesels - Pandharpur | 136 | Dg trip due to unbalanced load. | Closed | Jagdeep Saini
8 | WEST | 211780592 | 2025-03-03 11:51 | 125.4 | 4H.8042.C4../2420716 | Inspection/Maintenance | Open | AARADHANA MATCHING CENTER | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 20 | Adblue tank sensor connection found loose so tight the connection issue solved. | Closed | Jagdeep Saini
6 | North | 211780596 | 2025-03-03 11:51 | 250 | F6.8842.C4../2520007 | Automation issue Call by customer Name - Balram Gupta No - 9654086525 | Task Start | MAA LAXMI NAMKEEN | Paluck Technologies Ltd. - Ghaziabad | 4 | Customer want to Connection for Auto , done the connection after DG check run with both mode DG running well | Closed | Kapil Solanki
7 | North | 211780581 | 2025-03-03 11:48 | 58.5 | T4.8941.../2520194 | Fuel leakage | Task Start | HITARTH ORTHOPEDIC AND DETAL HOSPITAL | Rajdhani Diesels and Electricals - Barmer | LR-3 | Found Diesel tank leakage, repaired the tank after done the CC | Closed | Gourav Sharma
8 | North | 211780537 | 2025-03-03 11:38 | 160 | 6H.8475.../2420444 | Power supply issue Call by customer Name - Jagpal Singh No - 7527000675 | Task Start | Taranjot Ceramics Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Zirakpur | 3 | Customer panel change over fuse was burn so, replace the Fuse after that issue resolve | Closed | Ved Prakash Gupta
9 | North | 211780528 | 2025-03-03 11:35 | 320 | F6.8802.../2420175 | Starting/Stopping Issue | Task Start | Anjali Cold Storage | S. R Engines Sales And Service - LUCKNOW | 3.6 | Low def level & Coolant low in recovey bottle topup the def | Closed | Sudhir Awasthi
10 | North | 211780527 | 2025-03-03 11:35 | 82.5 | 5H.8901.../2320021 | Oil pump to be Change | Task Start | CRMK Select | Vidyut Engineers - Noida |  | Oil pump change | open | Kapil Solanki | Detail required
18 | South zone | 211780526 | 2025-03-03 11:35 | 15 | GP3.8501.../2420275 | Genset Trip | Closed | KRISHH PACKAGING | Madurai Electro Controls - Sivakasi | 79 | Genset trip due to overload. Heater is over load in this company. I will explain to the customer. When Genset is on. Off the 3 heater. oil level checked, coolant level checked | Closed | Mr. NandhaGopal
4 | East | 211780494 | 2025-03-03 11:32 | 58.5 | T4.8941.../2422211 | Leakage Issue | Task Start | M/S OM POULTRY FARM | Gangpur Sales and Services - Bargarh |  | Visit Pending | OPEN | Ujjwal Das
5 | East | 211780494 | 2025-03-03 11:32 | 58.5 | T4.8941.../2422211 | Leakage Issue | Task Start | M/S OM POULTRY FARM | Gangpur Sales and Services - Bargarh | 180 | Update pending | OPEN | Ujjwal Das
11 | North | 211780476 | 2025-03-03 11:27 | 25 | GP3.8702.../2520255 | Starting/Stopping Issue | Task Start | OSS. Construction Pvt. Ltd. | Excel Diesel Private Limited - Faizabad | 26 | Found charging alternator wire was broken so, battery low, after connect the wire then issue resolve | Closed | Sudhir Awasthi
14 | South zone | 211780477 | 2025-03-03 11:27 | 160 | 6H.8475.../2420408 | Starting issue Call by customer Name - Basudev . No - 7894778579 | Closed | AVNM Hotels and Resorts Pvt Ltd | Surya Power Services - Chikkaballapur | 41 | 1761/16 and top up the adblue and clear the error code | closed | Mr. Anil Kumar H G
12 | North | 211780379 | 2025-03-03 11:10 | 15 | GP3.8501.../2420709 | Automation On / Off Issue. call By Customer. Name:-Ravindra Varma. Mobile No.:-8708399844 | Task Start | Raj & Company | SAAN Royal Power Solutions Private Limited - Ambala | 164 | Mains voltage high (260v) and some wire connection in main panel are loose ,so due to genset goes off and on , so now we guide the customer about this and after tight main wire connection now genset working ok | Closed | Ved Prakash Gupta
13 | North | 211780376 | 2025-03-03 11:08 | 125.4 | 4H.8041.../2420112 | Genset Trip | Task Start | Accurex Industris | Paluck Technologies Ltd. - Faridabad | 254 | Low def level so, DG was trip SPN/FMI 1761/14 then after top up the def issue resolve | Closed | Kapil Solanki
14 | North | 211780320 | 2025-03-03 10:57 | 58.5 | T4.8941.../2422070 | Genset Trip | Task Start | S N ENTERPRISES | S.S. Enterprises - Allahabad | 9 | Fuel sensor change (Update pending) | open | Sudhir Awasthi
15 | North | 211780313 | 2025-03-03 10:54 | 82.5 | 5H.8901.../2420644 | Starting Issue And Controller Panel Issue Call By Customer Name :- Tarun Shetty Mobile No:-9899714253 | Task Start | TARUN SETHI | Vidyut Engineers - New Delhi | 2 | Battery low due to battery charger connection removed from customer end | Closed | Kapil Solanki
16 | North | 211780312 | 2025-03-03 10:54 | 58.5 | 6H.9840.../2420007 | Call By Customer Name :- M. D Afroj Mobile No:-8700479015 | Task Start | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 38 | Gas pressure low 300 milli bar, required pressure 1 bar so, educate the customer same | Closed | Kapil Solanki
17 | North | 211780311 | 2025-03-03 10:54 | 125.4 | 4H.8041.../2420222 | Amberlamp alarm issue Call by customer Name:Avinash . Number:9540023080 | Task Start | SHIVALIK ENGG.WORKS | Paluck Technologies Ltd. - Faridabad | 431 | Oil leakage from sump oil drain side | open | Kapil Solanki
18 | North | 211780295 | 2025-03-03 10:51 | 160 | 6H.8475.../2420030 | Coolant Issue Call By Customer Name :- Rajiv Sir Mobile No :-9968080005 | Task Start | Sri Vijayrama Impex Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 6 | Engine check and coolant leakege then hops pipe cleam tight coolant leakege problem (before Cuttoff) | Closed | Kapil Solanki
1 | WEST | 211780226 | 2025-03-03 10:43 | 625 | DV0.8501.C4../2420005 | Error code issue | Open | ENTREMONDE POLYCOATERS LIMITED | Dhanashree Technocrats Pvt. Ltd. - Nasik | 1954 | 523576 /0 (inducment alarm ) , 4358/1, 516166/0, dosing module did not spray ,found loose connection in adblue tank sensor connector ,tight the connection ,issue solved ,supply module ok . | Closed | Jagdeep Saini
83 | North | 211780222 | 2025-03-03 10:41 | 58.5 | T4.8941.../2422284 | Leakage Issue | Task Start | SIDHARTHA OVERSEAS | SAAN Royal Power Solutions Private Limited - Panipat | 34 | Update pending | Open | Ved Prakash Gupta
20 | WEST | 211780218 | 2025-03-03 10:39 | 30 | 3H.8902.../2421255 | Starting/Stopping Issue | Task Start | Ganesh Vastra Bhandar | Mahalaxmi Diesels - Solapur | 7 | Battery changer connection was not done by the customer so suggest the customer to do the battery charger connection. | Closed | Jagdeep Saini
8 | South Zone | 211780212 | 2025-03-03 10:37 | 125.4 | 4H.8042.C4../2520041 | ABNORMAL NOISE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the dg noticed the noise come to after throttle valve bolt loosed, correct the bolt tightness issue solved | Task Start | Mr. NandhaGopal
19 | North | 211780106 | 2025-03-03 10:36 | 125 | F6.9840.../2420045 | Genset Trip | Closed | IGS APPARELS | Paluck Technologies Ltd. - Ghaziabad | 7 | Gas Engine check spn3607 fmi 5 alarm clear and file flash | Closed | Kapil Solanki
18 | South | 211780102 | 2025-03-03 10:34 | 0 | GP3.8601.../2520133 | OIL COLOR CHANGE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected engine and noticed water entered into the oil sump noticed oil and water seperately may be due to after engine tested water wasing time possibilities to enter water into the engine | Closed | Mr. NandhaGopal
1 | North | 211780085 | 2025-03-03 10:29 | 58.5 | T4.8941.../2422519 | Fuel censer issue Call by customer Name - Tej Bahadur Yadav No - 8353985299 | Open | Krishi Auzar Bhandar | SAM Engineering corporation - Varanasi Cantt. | 107 | fuel level not proper showing sometimes low & sometimes high after that give the supply ground then show right then issue resolve | Closed | Sudhir Awasthi
79 | North | 211780062 | 2025-03-03 10:27 | 500 | DV8.8501.C4../2420090 | Coolant leakage issue | Open | Ping Engineers India Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh |  | Under Cancellation-Asset running Fine | Cancelled | Ved Prakash Gupta
24 | WEST | 211780049 | 2025-03-03 10:19 | 58.5 | T4.8941.../2421301 | Inspection/Maintenance | Open | ATLAS CASTALLOY LIMITED | Transcreek Engineers Pvt. Ltd. - Wadkhal |  | Cancelled | Closed | Jagdeep Saini
20 | North | 211780007 | 2025-03-03 10:10 | 125.4 | 4H.8042.C4../2420345 | Error code issue | Completed | TS. Jaina Construction | Espiem Engines & Machines (P) Limited - Etawah | 37 | Low def level top up the def & clear the dtc then issue resolve | Closed | Sudhir Awasthi
21 | North | 211780012 | 2025-03-03 10:10 | 160 | 6H.8475.../2420100 | Urea Leakage issue Call By Customer Name :- Anubhav Sharma Mobile No:-8076804414 | Task Start | SURYA ROSHNI LIMITED | OVN Industries Private Limited - New Delhi | 8.35 | Def level 50% so, topup the def 100% no leakage of def, A check done on 22/09/2024 | Closed | Kapil Solanki
2 | WEST | 211780001 | 2025-03-03 10:07 | 58.5 | T4.8941.../2422077 | air locking problem | Open | Shree Marketing Devkar Poultry Farm | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati | 242 | dg not start due to air lock , remove thr air lock from the fuel system , issue resolved. | Closed | Jagdeep Saini
26 | WEST | 211779964 | 2025-03-03 10:00 | 15 | GP3.8501.../2421273 | Electrical Problems | Closed | Maa Shakti Petroleum. | Unique Techno Services Pvt Ltd. - Baroda | 20 | KRM SIM was not working properly, hence Vodafone SIM was provided to the customer in place of Airtel SIM. | Closed | Amit Sandlya
17 | South | 211779907 | 2025-03-03 09:49 | 15 | GP3.8501.../2420483 | Starting Problem Call by : Customer Name : Santosh Kumar Contact : 9398879707 | Closed | Larsen & Toubro Ltd. | KALA Care Global LLP - Belagavi | 99 | The DG was not starting due to a high fuel level indication on the control panel (showing 100% fuel level, with the fuel float not moving from 100%).Checked the fuel float ohm value, which was found fluctuating only between 0 to 1 ohm, indicating a faulty fuel float. Replace the fuel level sensor. | Closed | Mr. Anil Kumar H G
16 | South | 211779886 | 2025-03-03 09:42 | 58.5 | T4.8941.../2520005 | Starting/Stopping Issue | Closed | SPEC 3 DETAILING | G-Care Diesels Private Limited - Ernakulam | 1.7 | Emergency switch not working so replaced emergency stop switch with NC contactor | Closed | Mr. Sanjaimon S
80 | North | 211779884 | 2025-03-03 09:41 | 30 | 3H.8902.../2420081 | Electrical Problems | Open | Nav Nirman Contruction Company | SAAN Royal Power Solutions Private Limited - Panipat | 48 | Under Frequency & Under Voltage alarm used to occur sometime when stop command given as per customer saying but Trial taken on site but no such issue occured | Closed | Ved Prakash Gupta
15 | South | 211779882 | 2025-03-03 09:41 | 160 | 6H.8475.../2420418 | Belt tension checking | Closed | KVR AUTO CARS PVT LTD | G-Care Diesels Private Limited - Kannur | 269 | , check belt with belt tensioner meter with help of ASE Godson, check belt tension found 114 Hz | Closed | Mr. Sanjaimon S
81 | North | 211779895 | 2025-03-03 09:40 | 15 | GP3.8501.../2421747 | Voltage Issue | Completed | JAI MATA FILLING STATION | SAAN Royal Power Solutions Private Limited - Baddi | LR-2 | found AVR card(R-120) not working properly ; showing B-phase over voltage alarm as soon as load given so replace the same & resolve the Issue | Closed | Ved Prakash Gupta | KRM Check
18 | South zone | 211779871 | 2025-03-03 09:37 | 15 | GP3.8501.../2420928 | Inspection/Maintenance | Closed | GEETHANJALI HARISH | Surya Power Services - Kalyan Nagar | 23.15 | visited the site found oil diesel mix in sump, so remove the oil, and fill the new oil, engine under observation | closed | Mr. Anil Kumar H G
3 | South Zone | 211779851 | 2025-03-03 09:10 | 15 | GP3.8501.../2421986 | Krm is not working. Unable to see the status of genset from mobile. Previously it was working now stopped working | Cancelled | G.SRINIVASAN | Bharath Diesel Sales and Service - Kumbakonam |  | cancelled | Cancelled | Mr. NandhaGopal
27 | WEST | 211779823 | 2025-03-03 08:47 | 250 | F6.8842.C4../2420115 | Canopy Emergency Switch | Task Start | SANSKAR ENGINEERS | Unique Techno Services Pvt Ltd. - Bhavnagar | 6 | Emergency Alarm was showing in the controller. So checked the wiring and found controller 54 pin wire 54(1H) wire was loose. | Closed | Amit Sandlya
3 | West | 211779823 | 2025-03-03 08:47 | 250 | F6.8842.C4../2420115 | Canopy Emergency Switch | Task Start | SANSKAR ENGINEERS | Unique Techno Services Pvt Ltd. - Bhavnagar | 6 | Emergency alarm was showing in controller. So checked the 4 pin connector and found that the 54(1H) wire had come out of its place, so the 54(1H) and 1H wires were connected through an extra wire. | Closed | Amit Sandlya
37 | North | 211779804 | 2025-03-03 08:29 | 30 | 3H.8902.../2320159 | Starting/Stopping Issue | Task Start | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 239 | Found Under speed alarm show in the controller so, check battery connection found positive terminal loose | Closed | Kapil Solanki
2 | North | 211779815 | 2025-03-03 07:56 | 15 | GP3.8501.../2421179 | Starting/Stopping Issue | Task Start | Jaiswal Kirana Store | S. R Engines Sales And Service - Gorakhpur | 31 | Abnormal sound from the turbo during cranking (update pending ASE) | open | Sudhir Awasthi
43 | South Zone | 211779795 | 2025-03-03 07:11 | 125.4 | 4H.8042.C4../2420351 | Tripping Issue Call By Customer Name - Bhaskar Number - 9003180817 | Cancelled | THE JOINT COMMISSIONER | Madhu Engineering Sales & Service - Teynampet,Chennai |  | cancelled | Cancelled | Mr. NandhaGopal
5 | West | 211780443 | 2025-03-03 | 160 | 6H.8424.../2420002 | CC SR | Open | Dr. Abhishek Tiwari | Natraj Power Tech - Mandsaur | CC | DG starting issue due to leakage from fuel pipe. | OPEN | Vijay Patil
3 | North | 211779152 | 2025-02-03 18:11 | 125 | F6.9840.../2420045 | Low Water Level Alam Call By Customer Name :- Manoj Kumar Mobile No :-9350058139 | Closed | IGS APPARELS | Paluck Technologies Ltd. - Ghaziabad | 7 | Gas Engine -major hardware alarm | Closed | Kapil Solanki
35 | South Zone | 211779133 | 2025-02-03 17:36 | 82.5 | 5H.8901.../2420588 | Starting Problem Call by : Customer Name : Mahesh Contact : 7997991289 | Cancelled | Sneha Farms Pvt. Ltd. | Powerlinks Infra Tech Pvt Ltd - L B Nagar |  | cancelled | Cancelled | Mr. Sanjaimon S
22 | North | 211779108 | 2025-02-03 16:33 | 125.4 | 4H.8041.../2320163 | Starting/Stopping Issue | Closed | Panchachuli Sehkari Aavak Samiti | Vidyut Engineers - Noida | 158 | Wrong report SR | Closed | Kapil Solanki
23 | North | 211779068 | 2025-02-03 15:34 | 125.4 | 4H.8041.../2420368 | Starting/Stopping Issue | Closed | Charms Collection | Gen Powers - PATIALA | 47 | Low def level topup the def & clear the DTC | Closed | Ved Prakash Gupta
53 | South Zone | 211779049 | 2025-02-03 14:46 | 15 | GP3.8501.../2421305 | AMF panel problem Call by : Customer Name : Giridhar Contact : 9791144436 | Open | P S GIRIDHAR | Prasad Power Engineers - Hassan |  | visit pending | Open | Mr. Anil Kumar H G
14 | South | 211779048 | 2025-02-03 14:38 | 58.5 | T4.8941.../2423276 | Red light Alaram | Closed | St. Pauls Lutheran Church. | Sri Manjunath Technical Services - Bhimavaram | 1 | SPN: 5838 P106A EGR valve malfunction Error showing in unit, connected the service tool(ikonnect tool) and cleared the errors through ECU flashing and after start the dg running is ok, | Closed | Mr. MD Saleem
24 | North | 211779045 | 2025-02-03 14:16 | 82.5 | 5H.8901.../2420012 | Urea issue Call By Coustomer Name = Sanram No =9891002854 | Open | SHAKTI PACKERS INDIA PRIVATE LIMITED | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki
16 | South zone | 211779035 | 2025-02-03 13:46 | 58.5 | T4.8941.../2420603 | Starting issue Call By Coustomer Name = Shrikant . No =9066421299 | Closed | Chalukya Technologies Private Limited | Surya Power Services - Kalyan Nagar | 49.5 | check the ECU TO relay board supply fault then looping extra wire 2B3 to 2A wire loop then start the engine check the engine running condition normal | closed | Mr. Anil Kumar H G
25 | North | 211779028 | 2025-02-03 13:30 | 15 | GP3.8501.../2420328 | diesel leakage Call By Coustomer Name = Saksham No =8700988806 | Closed | Hra Rice Mills | Dynamic Engineering Services - Jalandhar | 82 | Found no any leakage of fuel customer fuel fill over so, fuel dropping in above tank | Closed | Ved Prakash Gupta
26 | North | 211779021 | 2025-02-03 13:16 | 20 | GP3.8601.../2320039 | Red Alaram Issue Called by Customer Name: Mohmmad Wali No: 9128000020 | Cancelled | Mohammad Wali | Vidyut Engineers - Noida |  | Cancelled- Problem solve in Telephonic discussion | Cancelled | Kapil Solanki
9 | East | 211778998 | 2025-02-03 12:29 | 82.5 | 5H.8901.../2420562 | Starting and tripping Issue Called by Customer Name: Aniket No: 7462011929 | Task Start | KALYAN JEWELLERS INDIA LTD | Globalline India Services Private Limited - Patna | 95 | Update pending | OPEN | Prabhakar Kumar
17 | East | 211778998 | 2025-02-03 12:29 | 82.5 | 5H.8901.../2420562 | Starting and tripping Issue Called by Customer Name: Aniket No: 7462011929 | Task Start | KALYAN JEWELLERS INDIA LTD | Globalline India Services Private Limited - Patna | 98 | DG trip after 5 - 10 min on increasing load and RPM also fluctuate that time also found urea was not dosing and supply module not generating pressure of 5 bar,so change supply module found same problem then checked the fuel line found loose and also found airlock after removing the air lock DG operated on load without trip found no issue and supply module also started to generate the pressure so again refitted the previous SM and it also started working found no issue | OPEN | Prabhakar Kumar
82 | North | 211778979 | 2025-02-03 12:17 | 500 | DV8.8501.C4../2420273 | Starting/Stopping Issue | Closed | MUBARAKPUR FARMING COMPANY | SAAN Royal Power Solutions Private Limited - Zirakpur | 61 | Attend the site check dg found found starting issue due to error code problem related to DEF(520528/31,1761/0,1761/16,523583/16,1761/15)so connected diagnostic tool and remove error code then start dg working ok | Closed | Ved Prakash Gupta | KRM Check
4 | North | 211778992 | 2025-02-03 12:09 | 125.4 | 4H.8042.C4../2420667 | Black smoke Issue Called by Customer Name: Sumit Nandiya No: 9999707382 | Closed | BHARAT ELECTRICAL | Paluck Technologies Ltd. - Gurgaon | 90 | Update pending | open | Kapil Solanki
34 | South Zone | 211778947 | 2025-02-03 11:52 | 15 | GP3.8501.../2422183 | Diesel Leakage Issue Email By KGD Name:- Vishal Raut | Cancelled | SM Partners | G-Care Diesels Private Limited - Ernakulam |  | cancelled | Cancelled | Mr. Sanjaimon S
27 | North | 211778933 | 2025-02-03 10:52 | 500 | DV8.8501.C4../2420339 | Starting/Stopping Issue | Closed | MUBARAKPUR FARMING COMPANY | SAAN Royal Power Solutions Private Limited - Zirakpur | 127 | SPN/FMI 520528/31,1761/0,1761/16523583/16,1761/15,523584/15 clear the DTC | Closed | Ved Prakash Gupta
38 | North | 211778909 | 2025-02-03 10:00 | 750 | DV2.8501.C4../2320030 | Starting/Stopping Issue | Closed | Shree Cement Ltd. | SAAN Royal Power Solutions Private Limited - Panipat | 153 | found that display error code showing 656/3 due to found 6 no. cylinder connector was loose so clean the injector connector after found no issue | Closed | Ved Prakash Gupta
5 | North | 211778924 | 2025-02-03 09:24 | 20 | GP3.8601.../2421270 | Starting/Stopping Issue | Closed | MANOJ PHARMA | Paluck Technologies Ltd. - Faridabad | 3.5 | Fuel sensor change required | Closed | Kapil Solanki
11 | South zone | 211777489 | 2025-01-03 18:42 | 25 | GP3.8702.../2421085 | Starting issue Called by customer Name : Wasim Majid Number : 9844959529 | Closed | A H SILKS | 9 | 9 | Emergency wire loose, tighten the wire | closed | Mr. Anil Kumar H G
55 | South Zone | 211777267 | 2025-01-03 18:12 | 20 | GP3.8601.../2520271 | Commissoning | Open | Alans Heritage | Prasad Power Engineers - Mangalore |  | visit pending | Open | Mr. Anil Kumar H G
22 | East | 211777247 | 2025-01-03 17:59 | 20 | GP3.8601.../2421560 | starting issue | Task Start | Dipak Prasad | K.C. Diesel Services - SILIGURI | LR | Low oil pressure. 100/1. Replaced the Oil switch and resolved the issue | CLOSED | Prosanjit saha
13 | South | 211776920 | 2025-01-03 16:51 | 45 | 3H.8951.../2421271 | Sensore problem Call by : Customer Name :Rapert Contact :9489690370 | Closed | Good Shepherd Education Trust | Electro Controls - Coimbatore | 11.24 | Visit the site,call in kirloskar krm support number activate the krm unit | Closed | Mr. Sanjaimon S
30 | NORTH | 211776644 | 2025-01-03 15:45 | 750 | DV2.8501.C4../2420077 | Leakage Issue | Closed | Indian Oil Corpotation Ltd. | Paluck Technologies Ltd. - Gurgaon | 17 | Engine found This Engine 6no head to coolant leakage after that head Bolts Retaight and check start Engine Running 10 min. Found coolant drop is continuos | Open | Kapil Solanki
12 | East | 211776646 | 2025-01-03 15:45 | 40 | 3H.8951.../2421469 | Maintanance due alarm issue Called by dealer Name : Kumkum Number : 9234456624 | Open | M/s. Riya Tent Light & Sound | HACS Engineering and Tech Private Limited - Daltonganj | 63 | PM required. Need to cancel | CANCELLED | Prabhakar Kumar
12 | South | 211776432 | 2025-01-03 14:53 | 250 | F6.8842.C4../2420110 | Starting/Stopping Issue | Closed | P M S A Memorial Malappuram District Co Operative Hospital Limited | G-Care Diesels Private Limited - Malappuram | 47 | coolend leakage from hose clip replace hose clip, 516166/0, flash the ECU | Closed | Mr. Sanjaimon S
31 | NORTH | 211776423 | 2025-01-03 14:51 | 57 | T4.8941.../2320279 | Current Supply Issue Call By Customer Name :- Anil Varma Mobile No :- 9899996167 | Closed | Diesel Engine & Electrical Services | Paluck Technologies Ltd. - Ghaziabad | 124 | Earting wire cut in panel | Closed | Kapil Solanki
28 | South zone | 211776285 | 2025-01-03 14:23 | 40 | 3H.8951.../2420868 | Leakage Issue | Closed | S G INTERIORS | Surya Power Services - Kalyan Nagar | 41 | diesel over flow | closed | Mr. Anil Kumar H G
11 | South | 211776180 | 2025-01-03 13:43 | 125.4 | 4H.8042.C4../2421102 | CC CHECK UP | Closed | POORVIKA MOBILES PRIVATE LIMITED | Madhu Engineering Sales & Service -Poonamallee,Chennai | LR | Starting issue due to wiring ferule no (k88), loose connection, also found DTC 3031/14, so flash the ne file | Closed | Mr. NandhaGopal
56 | South Zone | 211776106 | 2025-01-03 13:29 | 160 | 6H.8475.../2520011 | ENGINE NOT START | Closed | Gorakshanatha Jnana Mandira | Prasad Power Engineers - Mangalore | 10 | Adblue level low, top-up the adblue | Closed | Mr. Anil Kumar H G
16 | South Zone | 211775881 | 2025-01-03 12:46 | 15 | GP3.8501.../2421319 | Red clamp alarm Call by :Customer Name : Chandra sekar Contact : 6381784453 | Closed | Rasikas Restaurant | Bharath Diesel Sales and Service - Salem | 10.38 | FOUND IN 3 PIN CONNECTOR FROM CONTROL PANEL TO EMERGENCY STOP SWITCH NEGATIVE (1)SUPPLY PROBLEM. BYPASSED THE CONNECTOR.NEGATIVE DIRECTLY GIVEN TO EMERGENCY STOP SWITCH. NOW D.G WORKING FINE. AND NO ALARM. | Closed | Mr. NandhaGopal
6 | South Zone | 211775687 | 2025-01-03 11:59 | 100 | 4H.8052.C4../2520031 | CAC HOSE FAILURE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Check the found CAC hose damage, replace the same. | Closed | Mr. NandhaGopal
57 | South Zone | 211775685 | 2025-01-03 11:58 | 20 | GP3.8601.../2421017 | Starting/Stopping Issue | Closed | Martins Hyper Market. | Prasad Power Engineers - Mangalore | 66 | Emergency alarm, found wire loose, tighten the wire | Closed | Mr. Anil Kumar H G
7 | South Zone | 211775678 | 2025-01-03 11:54 | 0 | GP3.8501.../2520215 | ANNORMAL NOISE | Completed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | ENGINE HUNTING AND RPM VARIATION AS PER SOP PROGRAM RESETTITE AND ISSUE NOT RESOVED AFTER REPLACMENT OF FIP ISSUE RESOLVED | completed | Mr. NandhaGopal
32 | NORTH | 211775505 | 2025-01-03 11:21 | 125.4 | 4H.8041.../2420171 | Starting Issue Call By Customer Name :- Udit Tiwari Mobile No :- 9711169025 | Closed | Malrik Seam Export | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 220 | Battery low due to battery charger connection removed from customer end | Closed | Kapil Solanki
48 | South Zone | 211775425 | 2025-01-03 11:03 | 25 | GP3.8702.../2520042 | No ventilation to generator | Closed | M/S HALLIKERE SALES CORPORATION | Prasad Power Engineers - Davangere | LR | Check the DG set not proper space and earthing issue | Closed | Mr. Anil Kumar H G
8 | West | 211775421 | 2025-01-03 11:02 | 30 | 3H.8902.../2421732 | DG automation | Open | ATC Telecom Infrastructure Private Limited | Transcreek Engineers Pvt. Ltd. - Ambernath | NA | Cancelled | Closed | Jagdeep Saini
1 | South Zone | 211775387 | 2025-01-03 10:57 | 25 | GP3.8702.../2420744 | DG has alternator output issue | Task Start | ATC Telecom Infrastructure Private Limited | Bharath Diesel Sales and Service - Chengalpattu | 35 | Inspect the engine main alternator coupling disc failure | Task Start | Mr. NandhaGopal | Details required
9 | South Zone | 211775219 | 2025-01-03 10:16 | 30 | 3H.8902.../2420003 | Starting Issue And Battery Issue Call By Customer Name :- Narayan ... Mobile No:-9840413243 | Task Start | Dr. Santha Narayanan | Madhu Engineering Sales & Service - Teynampet,Chennai | 26 | Check the complaint engine not staring. Check the battery voltage voltage 12.2v during cranking 8.5 V, Check the battery charger voltage is 13.7 v in the battery showing only 12.5 v . After started the dg running for 15 min checked the battery voltage is 13.1v now started the dg running normal. Suspected for DG pannel wiring issue removed the battery charger line and directly fixed in battery terminal. Started the dg running normal. Dg under observation | Task Start | Mr. NandhaGopal
24 | South zone | 211775142 | 2025-01-03 09:55 | 30 | 3H.8902.../2420380 | Low Oil pressure Call by : Customer Name :Philip Rajan Contact :9841039970 | Closed | James Rajan | Madhu Engineering Sales & Service - Teynampet,Chennai | 84 | Visit the site to meet the customer to check the engine low fuel level so engine not alarm comes low oil pressure then top up fuel and start the engine running few minutes Also done A-check. | Closed | Mr. NandhaGopal
15 | South zone | 211775067 | 2025-01-03 09:25 | 125.4 | 4H.8042.C4../2420278 | Starting/Stopping Issue | Closed | BRUNDAVAN BAR & RESTURANT | Surya Power Services - Billekahalli | 31 | visited the site and Checked the dg battery was theft so new battery fitting in Dg, after started the engine running condition found ok. | closed | Mr. Anil Kumar H G
23 | East | 211775061 | 2025-01-03 09:17 | 15 | GP3.8501.../2420641 | Over Current Alarm issue Call By Customer Name :- Deezong Mobile No :- 8116367591 | Open | Adarsha Nursing Home | K.C. Diesel Services - SILIGURI | 45 | Maintenance due alarm. Visited the engineer and rectified the site. Claim will be rejected | CLOSED | Prosanjit saha
33 | NORTH | 211775053 | 2025-01-03 09:04 | 125.4 | 4H.8041.../2420070 | Electrical Problems | Open | Rivah Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Cancelled-Problem solve in tele discussion | Cancelled | Gourav Sharma
28 | South Zone | 211775033 | 2025-01-03 08:24 | 25 | GP3.8702.../2421807 | Tripping Issue Email By - KGD Name -Shibu Mon .V | Closed | HOTEL SREE SARAVANA BHAWAN | Electro Controls - Thiruvananthapuram | 3.5 | Genset R phase showing under voltage. R phase fuse was in removed condition from customer side. connected the fuse and started the dg. advised customer to balance the load in three phases.informed to sales dealer Abou the same. | Closed | Mr. Sanjaimon S