## SPN
SL NO | Zone | Incident no | Creation Date | KVA | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Run hours | Observation | Incident Status | ASM Name | HO remark | Observation -2 | Elapsed Days | Component | Severity (S) | Occurrence (O) | Detection (D) | RPN | Priority
31 | North | 211898850 | 02/04/2025 | 750 | DV2.8501.C4../2420044 | Alarm issue problem | Task Start | Rajhans Infratech Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Agra | 51 | SPN/FMI 1761/15, 4358/1 Def level Low after topup the def then issue resolve | Closed | Sudhir Awasthi |  |  | 4 | DEF | 8 | 7 | 5 | 280 | High
94 | North | 211905166 | 04/04/2025 | 40 | 3H.8951.../2421714 | Starting/Stopping Issue | Task Start | SAMZAN | Suraj Motor Store - Srinagar | 19 | SPN/FMI-637/2 Related to Crank sensor,voltage supply to sensor found ok,TIR found 0.68 mm so increase it to add a washer to 1.03 mm & remove the code,issue resolved | Closed | Ved Prakash Gupta |  |  | 2 | Crank Sensor | 8 | 7 | 6 | 336 | High
91 | North | 211906099 | 04/04/2025 | 58.5 | T4.8941.../2420915 | Alaram issue Call by customer Name : Prittam Singh Number :7507680940 | Task Start | Prittam Singh | SAAN Royal Power Solutions Private Limited - Mandi | 91.54 | SPN/FMI-7026/3 metering unit shorted to battery ; re-connected connections of charging alternator & remove the code ; issue resolved | Closed | Ved Prakash Gupta | Ckt check |  | 2 | Alternator | 7 | 5 | 6 | 210 | High
48 | North | 211894664 | 01/04/2025 | 160 | 6H.8475.../2420394 | alarm issue | Closed | Tulsi Dham | Espiem Engines & Machines (P) Limited - Agra | 95 | SPN/FMI 1761/17 , 4365/2 , 1761/16 Low def level alarm topup the def after that issue resolve | Closed | Sudhir Awasthi |  |  | 5 | DEF | 8 | 7 | 5 | 280 | High
43 | North | 211897685 | 02/04/2025 | 82.5 | 5H.8901.../2320056 | Alarm Issue Call By Customer Name : Kuldeep Number : 7828773011 | Closed | Arise Ventures LLP. | Vidyut Engineers - Noida | 145 | Controller show the alarm, SPN/FMI 3364/27,6595/0,522130/19 Reset the alarm after that issue resolve | Closed | Kapil Solanki |  |  | 5 | Controller | 7 | 6 | 5 | 210 | High
4 | West | 211908757 | 05/04/2025 | 15 | GP3.8501.../2421888 | Genset Trip | Closed | DWARKESH ENERGY STATION. | Unique Techno Services Pvt Ltd. - Jamnagar | 11.6 | SPN/FMI-970 & 31 (Emergency Stop Alarm),Cable tie was not on connector. Tightened emergency stop button wire and connector. Used cable tie. | Closed | Amit Shandilya |  |  | 1 | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
29 | North | 211898903 | 02/04/2025 | 20 | GP3.8604.../2420198 | INSTANCE ID:-100742275 SITE ID:-I-UE-GKPR-ENB-9091 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-SHAILESH YADAV NUMBER:-8299698446 | Task Start | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur | 266 | Alarm show J1939 coolant level low, SPN/FMI 110/0 show loose connection tightness the same after that issue resolve | Closed | Sudhir Awasthi |  |  | 4 | Coolant | 8 | 7 | 6 | 336 | High
26 | North | 211898974 | 02/04/2025 | 58.5 | T4.8941.../2520194 | Genset Trip | Task Start | HITARTH ORTHOPEDIC AND DETAL HOSPITAL | Rajdhani Diesels and Electricals - Barmer | 19 | SPN/FMI 637/5 remove the crank sensor clean after refitted again then issue resolve | Closed | Gourav sharma |  |  | 4 | Crank Sensor | 8 | 7 | 6 | 336 | High
4 | North | 211877335 | 29/04/2025 | 500 | DV8.8501.C4../2320079 | ECU alarm issue Call By Customer Name :- Ishwar Saini Mobile No :- 7631866031 | Closed | Leighton India Contractors Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 387 | SPN/FMI 516166/0 after check and found under speed alarm after that check in main alternator found R phase wire was not connected so, connected the same then issue resolve | Closed | Kapil Solanki |  |  | 9 | Alternator | 7 | 5 | 6 | 210 | High
43 | East | 211902784 | 03/04/2025 | 125.4 | 4H.8042.C4../2420886 | Error code Issue Call By Customer Name : Abdul Number : 8134963146 | Open | Mech Technik India Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 179 | SPN- 6595 FMI- P1561 . Check dozing module and supply module voltage and continuity from ECU found ok then flashed ECU issue resolved | OPEN | Ujjwal Das |  |  | 3 | ECU | 10 | 9 | 7 | 630 | High
38 | North | 211884350 | 31/04/2025 | 40 | 3H.8951.../2421593 | Starting/Stopping Issue | Closed | MOON LIGHT GUEST HOUSE | SAAN Royal Power Solutions Private Limited - Mandi | 80.4 | SPN/FMI-637/2 ; Related to crank sensor ;Crank sensor found not fitted properly so fitted the same & remove the code ,isue resolved Update Pending | Open | Ved Prakash Gupta |  |  | 6 | Crank Sensor | 8 | 7 | 6 | 336 | High
113 | North | 211893906 | 01/04/2025 | 15 | GP3.8501.../2421802 | Starting Issue Call by customer Name :Riyaz Ahmad Number :9149503769 | Task Start | SEW ENGINEERING WORKS PRIVATE LIMITED | Suraj Motor Store - Srinagar | 12 | SPN/FMI-2802/4 : Battery Voltage found low ; mains supply not available on site so install the same & resolve the issue | Closed | Ved Prakash Gupta |  |  | 5 | Battery | 8 | 6 | 4 | 192 | Moderate
14 | North | 211894070 | 01/04/2025 | 125.4 | 4H.8041.../2320125 | Hai | Task Start | YUG ENTERPRISES | Paluck Technologies Ltd. - Faridabad | 1085 | SPN/FMI 4095/2, 4339/2 Replace the DEF filters and Supply module after that issue resolve | Closed | Kapil Solanki |  |  | 5 | Supply Module | 7 | 5 | 4 | 140 | Moderate
99 | North | 211902213 | 03/04/2025 | 30 | 3H.8902.../2421080 | Electrical Problems | Closed | HERBON CHEMICALS LLP | SAAN Royal Power Solutions Private Limited - Sonipat | 1.55 | SPN/FMI-97/2 Water self test with protect lamp on ; clean the fuel filter & engine - Pannel connector but alarm persisted , Battery +ve terminal found in loose condition so corrected the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 3 | Battery | 8 | 6 | 4 | 192 | Moderate
36 | North | 211898570 | 02/04/2025 | 125.4 | 4H.8041.../2320132 | Alarm | Task Start | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 338 | SPN/FMI 516166/0 , 7598/7 Check the supply module pressure found ok after reset the alarm | Closed | Kapil Solanki |  |  | 4 | Supply Module | 7 | 5 | 4 | 140 | Moderate
33 | North | 211879696 | 29/04/2025 | 40 | 3H.8951.../2421648 | Alarm Issue Call By Customer Name : Kuldeep Number : 9760746097 | Closed | Jayco Engineering Company | Vidyut Engineers - Noida | 14 | SPN/FMI 2791/18 clear the DTC after that issue resolve (Revisit on site and Flash the file if again repeated) | Closed | Kapil Solanki |  |  | 8 | DTC | 6 | 5 | 4 | 120 | Moderate
75 | North | 211904239 | 04/04/2025 | 160 | 6H.8475.../2420024 | Error code Issue Call by customer Name :Karun Number:7206727293 | Task Start | Tool Room Engineers LLP | Paluck Technologies Ltd. - Faridabad | 265 | SPN/FMI 110/0 High coolant tem. Alarm due to belt was broken so, change the same after that issue resolve and Radiator cleaning required | Closed | Kapil Solanki |  |  | 3 | Radiator | 7 | 5 | 4 | 140 | Moderate
72 | North | 211904578 | 04/04/2025 | 250 | F6.8841.../2320006 | Starting/Stopping Issue | Task Start | Katyayani Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi | 180 | SPN/FMI 168/3, 516166/0, 3031/14, so clear the DTC after that issue resolve | Closed | Gourav sharma |  |  | 3 | DTC | 6 | 5 | 4 | 120 | Moderate
52 | North | 211894237 | 01/04/2025 | 500 | F6.8843.C4../2420002 & 2420002 | Error code | Task Start | Brij Healthcare & Research Centre. | Espiem Engines & Machines (P) Limited - Agra | 1352 | SPN/FMI 3031/14, 3364/8, 1761/16, 520527/16, 4365/2, 4095/1, 520527/18, 4365/16 low def alarm clear the DTC after that issue resolve | Closed | Sudhir Awasthi |  |  | 5 | DTC | 6 | 5 | 4 | 120 | Moderate
26 | South | 211893577 | 01/04/2025 | 320 | F6.8802.../2420306 | Starting/Stopping Issue | Task Start | SHOBHIKA WEDDINGS EDAPPAL LLP | G-Care Diesels Private Limited - Malappuram | 362 | Founded SPN 1761/16, 4095/2, 4095/1 Error codes.Connected I connect Tool and Cleared All Error codes and Rectifyed Engine starting and Alarm issue.Engine 1 Hours trial Run Done. Not Found Any Repeated Error codes issue.Engine Running performance ok. | Closed | Mr. Sanjaimon S |  |  | 5 | Error Codes | 5 | 4 | 3 | 60 | Low
111 | North | 211897799 | 02/04/2025 | 200 | 6H.8435.../2420229 | Urea consumption Issue Call By Customer Name :Bhupendra .. Number :7860629092 | Closed | Vishwasamudra Engg Pvt, Jammu | Suraj Motor Store - Jammu | 664 | SPN/FMI-516166/0 ; clear the code & educated to customer to avaoid hot shutdown | Closed | Ved Prakash Gupta |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211871214 | 27/04/2025 | 82.5 | 5H.8901.../2420649 | Starting Issue Call By Customer Name :-Mukesh Kumar Mobile No :-7990851596 | Closed | KALYAN JEWELLERS INDIA LTD | S. R Engines Sales And Service - LUCKNOW | 54 | SPN/FMI 3031/14 reset the alarm after that issue resolve | Closed | Sudhir Awasthi |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211883510 | 31/04/2025 | 125.4 | 4H.8042.C4../2420462 | AMF Panel fittng Issue Call By Customer Name - Kachan mishra Number 8130780192 | Task Start | IMPACTQA SERVICES [P] LTD | Vidyut Engineers - Noida | 14 | SPN/FMI 3031/14, 2802/4 reset the alarm after that issue resolve | Closed | Kapil Solanki |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211881861 | 30/04/2025 | 57 | T4.8941.../2420149 | Starting Problem Call By Customer Name : Sanjay Arora Mobile : 9873022666 | Completed | USHA ARORA | OVN Industries Private Limited - New Delhi | 17 | SPN/FMI 100/4 Change the oil sensor after that isuue resolve | Closed | Kapil Solanki | MAJOR |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
27 | South | 211893571 | 01/04/2025 | 58.5 | T4.8941.../2421704 | Electrical Problems | Task Start | Sri Vasista Educational Trust | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 88.25 | As per Koel Area office instructions attend the site with warranty BD SR and found active fault code is SPN 2791/FMI 0 then reset fault code with Ikonnect tool and start the dg tested on available load for 30 mins found no fault codes active and checked customer load below 10℅ only present load not available at customer site. | Closed | Mr. MD Saleem |  |  | 5 | Warranty | 4 | 3 | 2 | 24 | Low
47 | North | 211895068 | 01/04/2025 | 125.4 | 4H.8041.../2320121 | Power Fluctuation problem Email By Customer Name:-Vinod Rana | Closed | XPERT POWERGEN PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1963 | SPN/FMI 516166/0 , Cool down time 30 sec. so, change the time 180 sec. | Closed | Kapil Solanki |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
42 | North | 211897773 | 02/04/2025 | 125.4 | 4H.8041.../2320134 | Error Code Issue Call By Customer Name : Kashif Ahmad Number : 8445820675 | Task Start | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar | 1386 | SPN/FMI 51/0 Clean the Air filter body and Check itv connection found ok clear the DTC after that issue resolve | Closed | Sudhir Awasthi |  |  | 5 | Air Filter | 4 | 4 | 3 | 48 | Low
23 | West | 211894149 | 01/04/2025 | 625 | DV0.8501.C4../2420103 | Tripping Issue Call by Customer Name : Jivendra Bhavsar Number : 9799392341 | Task Start | Ravi Infrabuild Projects Pvt. Ltd. | Natraj Power Tech - Indore | 145 | SPN/FMI- 110/0 & 110/16. DG tripped due to overheating and found belt loose, tightened it. | OPEN | Vijay Patil |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
27 | North | 211898969 | 02/04/2025 | 750 | DV2.8501.C4../2420001 | Error code issue Call by Customer Name - Shubham Number - 8076641759 | Task Start | Homekraft Infra Pvt. Ltd. | Vidyut Engineers - Noida | 49 | Checked Error code SPN/FMI 523576/0, checked Dozing Conectors clean and refitted , reset the alarm after that issue resolve | Closed | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211884740 | 31/04/2025 | 15 | GP3.8501.../2421760 | Starting Problem Call by : Customer Name : Madhu Contact : 8217223689 | Closed | MELODY WORLD | Surya Power Services - Mysuru | 226 | Engine not start due to spn 244/8 and 190/8 engine speed sensor error and llop open fault. So tighten the respective wire for both the sensor issue resolve | Closed | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211885036 | 31/04/2025 | 125.4 | 4H.8041.../2420176 | Alarm issue | Closed | XPERT POWERGEN PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1807 | SPN/FMI 7598/7 & 516166/0 after that reset the alarm then issue resolve | Closed | Kapil Solanki |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
55 | North | 211901462 | 03/04/2025 | 58.5 | T4.8941.../2420649 | Tripping Issue Call By Customer Name- Ravindra Kumar Number-9910112643 | Open | House Warming Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 98 | check and found SPN/FMI 97/5 after tightness the panel connection then issue resolve | Closed | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211871353 | 27/04/2025 | 200 | 6H.8435.../2420007 | Tripping Issue & MIL Lamp On alarm Issue. Call By customer. Name:-Ashish .. Mobile No.:-9891239461 | Closed | SUPER COMPUTECH PRIVATE LIMITED | Vidyut Engineers - Noida | 245 | SPN/FMI 5461/8, 3031/14 reset the alarm after that issue resolve | Closed | Kapil Solanki |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low

## Non-SPN
SL NO | Zone | Incident no | Creation Date | KVA | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Run hours | Observation | Incident Status | ASM Name | HO remark | Observation -2 | Elapsed Days | Component | Severity (S) | Occurrence (O) | Detection (D) | RPN | Priority
69 | East | 211893004 | 01/04/2025 | 30 | 3H.8902.../2421716 | Voltage Fluctuation | Closed | Vibrant Induction Private Limited | Hibreed Engineering Pvt. Ltd. - Guwahati | 547 | Egr replaced - found it was choked customer load is not stable this time replaced on good will basis and email communication provided to customer regarding this | CLOSED | Ujjwal Das |  |  | 6 | EGR | 9 | 7 | 5 | 315 | High
2 | West | 211904399 | 04/04/2025 | 25 | GP3.8702.../2422113 | Automation / emergency Alarm issue call by customer name : Fazal number : 9998622871 | Task Start | JUMMA MASJID | Unique Techno Services Pvt Ltd. - Ankleshwar | 3.53 | Engine not starting due to emergency stop alarm. Loose wire on distribution Block XDBK3(-Ve). | Open | Amit Shandilya |  |  | 3 | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
20 | WEST | 211883122 | 31/04/2025 | 5.5 | CC1.1013.../2400201 | Voltage Fluctuation | Closed | Wipro enterprises (p) limited | Shree Engineering Service - Raipur | 11 | The controller was not on. So checked and found that the controller power supply connections were loose, so tightened them. | Closed | Amit Sandlya |  |  | 7 | Controller | 7 | 6 | 5 | 210 | High
28 | North | 211898938 | 02/04/2025 | 250 | F6.8842.C4../2520121 | Electrical Problems | Open | AATAMDEEP VIDYALAYA | S. R Engines Sales And Service - Gorakhpur | 41 | Def level low after the topup def then issue was resolve | Closed | Sudhir Awasthi |  |  | 4 | DEF | 8 | 7 | 5 | 280 | High
18 | WEST | 211884562 | 31/04/2025 | 82.5 | 5H.8901.../2420354 | Error code isue | Closed | KALYAN JEWELLERS | Natraj Power Tech - Chhindwara | 48.29 | Low DEF level | Closed | Amit Sandlya |  |  | 6 | DEF | 8 | 7 | 5 | 280 | High
32 | North | 211898774 | 02/04/2025 | 58.5 | T4.8941.../2420142 | emergency stop alarm showing at DG | Task Start | Bharti Airtel ANG | Vidyut Engineers - Noida | 459 | Controller show the Emergency alarm, then check and found Emergency switch was pressed & Connection found also Loose & Fuel circuit open alarm then check and found Fuel level only 2% | Closed | Kapil Solanki |  |  | 4 | Controller | 7 | 6 | 5 | 210 | High
28 | East | 211905146 | 04/04/2025 | 125.4 | 4H.8041.../2320003 | White smoke | Closed | N.K. CONSTRUCTION & SUPPLIERS | Hibreed Engineering Pvt. Ltd. - Nagaon | 172 | Customer complaint was related smoke as load was just only 10-15 KW so on increasing load smoke disappears so need to increase the load. also educated customer. | CLOSED | Ujjwal Das |  |  | 2 | Load | 8 | 6 | 5 | 240 | High
13 | WEST | 211869797 | 27/04/2025 | 750 | DV2.8501.C4../2420103 | Coolant leakage issue | Closed | B. G. SHIRKE CONSTRUCTION TECHNOLOGY PRIVATE LIMITED | Transcreek Engineers Pvt. Ltd. - Mumbai | 2.3 | coolant leakage from dosing module return pipe , tight the same and issue solved. | Closed | Jagdeep Saini |  |  | 10 | Dosing Module | 8 | 6 | 5 | 240 | High
35 | North | 211898584 | 02/04/2025 | 82.5 | 5H.8901.../2420328 | Starting Problem | Task Start | Axis Bank Ltd | Vidyut Engineers - Noida | LR-9 | DG show the alarm Fail to stop, so flash the controller, after that found Wrong connection in panel | open | Kapil Solanki |  |  | 4 | Controller | 7 | 6 | 5 | 210 | High
31 | East | 211904257 | 04/04/2025 | 125.4 | 4H.8042.C4../2421079 | VOC - AD BLUE TANK BANK B -REPROGRAM Customer Name - Pulinbhuyan Customer Number -9365967617 Mode- SR Generated through CDI calling. | Open | Shree Shyam Tea Company | Almas Engineers - Sivsagar |  | low DEF level alarm as per KRM its in inducement | OPEN | Ujjwal Das |  |  | 3 | Inducement | 8 | 6 | 5 | 240 | High
6 | WEST | 211877987 | 29/04/2025 | 82.5 | 5H.8901.../2520058 | Mil Lamp Alarm issue Email By - KGD Name - Surekha Auti | Closed | Grand Realty | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 2 | error code p1079(Inducement ) , p0070( Ambient air temp ) , check connection between ambient temp sensor and ecu found ok need ikonnect to clear error code. | Closed | Jagdeep Saini |  |  | 8 | ECU | 10 | 9 | 7 | 630 | High
41 | North | 211897784 | 02/04/2025 | 57 | T4.8941.../2420455 | Tripping Issue Call by customer Name :Sachin Number :9557755050 | Task Start | Meerut Ptfe Products Pvt. Ltd | R K Engineers - Meerut | 86 | DG was tripping due to unbalance load (R 32/ Y 97/ B 34) so educate the customer kindly maintain the load | Closed | Sudhir Awasthi |  |  | 5 | Load | 8 | 6 | 5 | 240 | High
41 | South | 211892923 | 01/04/2025 | 20 | GP3.8601.../2320016 | Starting/Stopping Issue | Closed | Avani Fuel Station | G-Care Diesels Private Limited - Kannur | 110 | Found fuel leakage from Fuel filter copper washer side. Replace New copper washer start the engine trail taken ok. | Closed | Mr. Sanjaimon S |  |  | 6 | Fuel Leakage | 10 | 8 | 7 | 560 | High
1 | WEST | 211881962 | 30/04/2025 | 15 | GP3.8501.../2520275 | Over current issue and Tripping issue Call By customer Name:Akash Bhang Number :9960050073 | Open | SAIRAJ BHAND AND COMPANY | Mahalaxmi Diesels - Pandharpur | 3 | customer site unbalanced load, balance the load and issue solved. | Closed | Jagdeep Saini |  |  | 7 | Load | 8 | 6 | 5 | 240 | High
35 | East | 211903411 | 03/04/2025 | 200 | 6H.8435.../2420214 | ECU Fault Email By KGD Name:-Pooja Sarma | Closed | Shine Enterprise | Almas Engineers - Dibrugarh | 12.13 | 516166,0- ECU Fault-High - most severe- so cleared the DTC issue resolved but also flashed the the ecu | CLOSED | Ujjwal Das |  |  | 3 | ECU | 10 | 9 | 7 | 630 | High
20 | East | 211877195 | 30/04/2025 | 40 | 3H.8951.../2421466 | Alarm Issue And Power Supply Issue And Abnormal Sound Issue Call By Customer Name :-Tamal . Mobile No:-9432883622 | Open | Associated Engineering Works | Revenus Industries Pvt. Ltd. - South Kolkata | 9 | 2791/17 (EGR Fault code) after that fashing the ECU ,issue resolved. | CLOSED | Prosanjit saha |  |  | 8 | EGR | 9 | 7 | 5 | 315 | High
36 | East | 211903398 | 03/04/2025 | 500 | DV8.8501.C4../2420098 | Display issue | Closed | Koderma Chemical Pvt. Ltd. | HACS Engineering and Tech Private Limited - Hazaribagh | 70 | 516166,0- ECU Fault-High - most severe so flashed ECU issue resolved | CLOSED | Prabhakar Kumar |  |  | 3 | ECU | 10 | 9 | 7 | 630 | High
16 | East | 211876197 | 28/04/2025 | 320 | F6.8802.../2420190 | red lamp alram call by customer name-MR AMAN SIR number-7992310977 | Closed | SHIV SHAKTI CHAWAL UDYOG PRIVATE LIMITED | Globalline India Services Private Limited - Purnia | 87 | Low def level alarm top the DEF also educated customer. | CLOSED | Prabhakar Kumar |  |  | 9 | DEF | 8 | 7 | 5 | 280 | High
15 | East | 211877225 | 29/04/2025 | 58.5 | T4.8941.../2422910 | Starting issue Call By Customer Name :- Subhash Mobile No :- 7488128689 | Closed | HARE RAM HARE KRISHNA ENTERPRISES | HACS Engineering and Tech Private Limited - Hazaribagh | 119 | DG fails to start due to controller start command from 3 no. pinwire found littile bit loose after tightening issue resolved | CLOSED | Prabhakar Kumar |  |  | 9 | Controller | 7 | 6 | 5 | 210 | High
14 | East | 211877390 | 29/04/2025 | 15 | GP3.8501.../2420666 | Red lamp on alarm issue Called by customer Name : ANAND KUMAR Number : 8084808585 | Closed | Jep Ranchi. | HACS Engineering and Tech Private Limited - Ranchi | 73 | Red lamp alarm was due to emergency stop switch SE visited and checked the wiring connection all found ok then removed ECU connector and reconnected it after issue resolved | CLOSED | Prabhakar Kumar |  |  | 9 | ECU | 10 | 9 | 7 | 630 | High
24 | North | 211893056 | 01/04/2025 | 250 | F6.8841.../2420110 | Voltage Fluctuation | Task Start | KIDS CLINIC INDIA LIMITED | OVN Industries Private Limited - New Delhi | 2291 | Def tank dusty, but erro code not show after clean the def tank then issue resolve (service due Quatation send to the customer) | Closed | Kapil Solanki |  |  | 6 | DEF | 8 | 7 | 5 | 280 | High
24 | West | 211894043 | 01/04/2025 | 160 | 6H.8475.../2520069 | Leakage Issue | Closed | Four Lakes | Natraj Power Tech - Bhopal | 3.6 | No coolant leakage found but reservoir tank was fully empty so maintained the coolant level between Max & Min. | Closed | Vijay Patil |  |  | 5 | Coolant | 8 | 7 | 6 | 336 | High
23 | East | 211906907 | 04/04/2025 | 15 | GP3.8501.../2420815 | Out Put issue Call By Customer Name :- Nityanand No :-9304415416 | Task Start | M/S RANJAN JEWELLERS | Globalline India Services Private Limited - Patna, Exhibition Road | 59 | customer complaint was ita output voltage showing low in R phase on no load so cheked and found R phase sensing found littlr bit loose aftertightening issue rsolved | CLOSED | Prabhakar Kumar |  |  | 2 | Load | 8 | 6 | 5 | 240 | High
1 | South | 211885498 | 31/04/2025 | 15 | GP3.8501.../2520033 | Diesel Leakage Problem Call by : Customer Name : MOHAN Contact : 9500945018 | Completed | MOHAN AGENCIES | Bharath Diesel Sales and Service - Kallakurichi | 15 | Fuel filter to fuel pump. Fuel hose Banjo Bolt losse . tight the 19 size Banjo Bolt done . Fuel leak complaint solved | Closed | Mr. NandhaGopal |  |  | 6 | Fuel Pump | 8 | 6 | 5 | 240 | High
4 | East | 211901561 | 03/04/2025 | 25 | GP3.8702.../2421439 | Tripping issue and Preventive Maintenance Call By Customer Name:-Mohd Riyan No:-7978115997 | Closed | ASTANA BANO | Gangpur Sales and Services - Sambalpur | 8 | Customer side overload issue,no issue in DG | CLOSED | Ujjwal Das |  |  | 3 | Load | 8 | 6 | 5 | 240 | High
1 | North | 211872851 | 28/04/2025 | 500 | DV8.8508.C4../2420007 | MCB Lamp Alarm And Indicator Issue Call By Customer Name :-Nihar Ranjan Mobile No:-8595668201 | Task Start | Anand Divine Developers Private Limited. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 13 | Def level low topup the def then issue resolve | Closed | Kapil Solanki |  |  | 10 | DEF | 8 | 7 | 5 | 280 | High
33 | South | 211893107 | 01/04/2025 | 15 | GP3.8501.../2422058 | main alternator issue | Task Start | Hitha Shyam | Ultimate Power Source - Hosur | LR | Found low out put voltage.dg trip with with R phase under voltage .and abnormal noise come from alternator, removed alternator exitor stator cover ,found exiter rotor shake condition due to exitor rotor seating area damaged .replaced new exitor rotor coupled alternator.started the dg given load trail found performance satisfactory | Closed | Mr. NandhaGopal | Alternator issue |  | 6 | Alternator | 7 | 5 | 6 | 210 | High
31 | South | 211893126 | 01/04/2025 | 40 | 3H.8951.../2520288 | Not starting | Task Start | Eversub India Private Limited | Surya Power Services - Kalyan Nagar | LR | checked the engine based on complaint reported power supply issue,found neutral connector LVM fault, replaced the connector, started the engine on load running condition is normal | Closed | Mr. Anil Kumar H G |  |  | 6 | Load | 8 | 6 | 5 | 240 | High
12 | West | 211907423 | 05/04/2025 | 20 | GP3.8601.../2420566 | Electrical Problems | Closed | Jay Ambe Petroleum | Unique Techno Services Pvt Ltd. - Morbi | 105.45 | Emergency Stop alarm so tightened the wire and issue resolved. | Closed | Amit Shandilya |  |  | 2 | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
6 | North | 211884619 | 31/04/2025 | 125.4 | 4H.8042.C4../2420151 | NOT TAKING LOAD | Closed | Gagan Generators. | Vidyut Engineers - New Delhi | 1056 | Engineer visit the site check with the load on 1 hour found no any issue | Closed | Kapil Solanki |  |  | 6 | Load | 8 | 6 | 5 | 240 | High
28 | South | 211893461 | 01/04/2025 | 125.4 | 4H.8041.../2320068 | AMF Panel problem Call by : Customer Name :Sreenish Contact : 8891540552 | Open | POWERMECH DIESELS | G-Care Diesels Private Limited - Ernakulam | 34 | DG start/stop working properly in manual mode. While in auto mode, DG starts without any command. EB voltage monitoring was enabled in controller, but no visual indication of line voltage in controller. flashing of controller(KG640C(E)) for def level indication was done few weeks before. Main monitoring disabled, then tested DG on auto-manual modes, working properly. Start/stop actions are performing properly. | Open | Mr. Sanjaimon S |  |  | 5 | Controller | 7 | 6 | 5 | 210 | High
24 | South | 211893621 | 01/04/2025 | 58.5 | T4.8941.../2423094 | Alternator Replacement issue Call by customer Name - Rajesh Number -7019731273 | Open | M/S VHF RESORTS | Prasad Power Engineers - Sirsi | 209 | As per customer requirement marine Alternator so replace the Alternator, This case already inform to Kadhirvel Sir | Closed | Mr. Anil Kumar H G |  |  | 5 | Alternator | 7 | 5 | 6 | 210 | High
23 | South | 211893641 | 01/04/2025 | 58.5 | T4.8941.../2423202 | Alternator Replacement issue Call by customer Name - Rajesh Number -7019731273 | Open | M/S VHF RESORTS | Prasad Power Engineers - Sirsi | 84 | As per customer requirement marine Alternator so replace the Alternator, This case already inform to Kadhirvel Sir | Closed | Mr. Anil Kumar H G |  |  | 5 | Alternator | 7 | 5 | 6 | 210 | High
53 | North | 211893885 | 01/04/2025 | 82.5 | 5H.8901.../2320095 | Voltage Fluctuation Issue Call By Customer Name :- shubham ... Mobile No :-8901042010 | Closed | Skycore Industries Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 327 | Voltage flactuation is continuous, load is Welding machine near about (60A) and Computer | open | Kapil Solanki |  |  | 5 | Load | 8 | 6 | 5 | 240 | High
9 | West | 211902088 | 03/04/2025 | 20 | GP3.8601.../2421515 | Electrical Problems | Task Start | DR. SAGAR PADMAWAR | Dicksons Engineering Co.Pvt.Ltd. - Yavatmal | 14 | Dg not giving volt after start the dg , dg tripped due to under voltage and abnormal sound from ac alternator , so removed the alternator and send to service center . | Open | Jagdeep Saini |  |  | 3 | Alternator | 7 | 5 | 6 | 210 | High
7 | West | 211788422 | 05/04/2025 | 0 | T4.8941.../2520586 | thermostat to radiator in pipe puncture observed. | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | coolant leakage from hose pipe so change the hose. | Closed | Jagdeep Saini |  |  | 32 | Coolant | 8 | 7 | 6 | 336 | High
14 | South | 211884008 | 31/04/2025 | 125.4 | 4H.8041.../2420328 | over heating | Closed | Map Hospitality | Laxmi Diesels - Visakhapatnam | 50 | Error code 6595-0,3031-14 so checked all wiring found ok checked dosing module for any crystallization not found and cleared the error code then start and found that engine running condition found ok. | Closed | Mr. MD Saleem |  |  | 6 | Dosing Module | 8 | 6 | 5 | 240 | High
17 | North | 211893383 | 01/04/2025 | 160 | 6H.8475.../2520001 | Coolant required | Task Start | Jaya Siddhartha Hospital | GLOBALVISION POWER SOLUTIONS PVT LTD - DEHRADUN | `40 | Low Def level and Coolant level So, topup the same after that issue resolve | Closed | Sudhir Awasthi |  |  | 5 | Coolant | 8 | 7 | 6 | 336 | High
16 | East | 211905271 | 04/04/2025 | 10 | GP3.8301.../2420030 | Starting/Stopping Issue | Closed | Odisha Mining Corporation Limited. OMC. Bhubaneswar | Gangpur Sales and Services - BHUBANESWAR | 4 | SE Found 516166 code alram showing in Controller after that flashing the ECU ,Issue resolved | CLOSED | Ujjwal Das |  |  | 2 | ECU | 10 | 9 | 7 | 630 | High
6 | West | 211873211 | 28/04/2025 | 30 | 3H.8902.../2422416 | return from site | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Coolant mixed in oil , replaced the cylinder head gasket , trail done. | Closed | Jagdeep Saini |  |  | 10 | Cylinder Head | 9 | 4 | 6 | 216 | High
6 | South | 211884658 | 31/04/2025 | 40 | 3H.8951.../2520288 | LOAD CABLE ISSUE-PRABIN | Closed | Eversub India Private Limited | Surya Power Services - Kalyan Nagar | LR | Checked the engine based on complaint reported found B phase no power supply from dg,checked the mccb,load cable all found normal,after removing load cable, power supply is coming,need to check the change over panel | Closed | Mr. Anil Kumar H G |  |  | 6 | Load | 8 | 6 | 5 | 240 | High
23 | North | 211893102 | 01/04/2025 | 250 | F6.8841.../2420127 | Genset Trip | Task Start | KIDS CLINIC INDIA LTD | OVN Industries Private Limited - New Delhi | 2295 | Dosing module not working, so clean the DEF line with hot water after that issue resolve (service due Quatation send to the customer) | Closed | Kapil Solanki |  |  | 6 | Dosing Module | 8 | 6 | 5 | 240 | High
22 | East | 211907442 | 05/04/2025 | 125.4 | 4H.8042.C4../2420872 | Red Lamp Alarm Issue Call By customer Name :RK Ranjeet No :7085739188 | Task Start | HOTEL MOMON | Hibreed Engineering Pvt. Ltd. - Guwahati | 14 | 516166- so cleared code and flashed the ECU issue resolved | CLOSED | Ujjwal Das |  |  | 2 | ECU | 10 | 9 | 7 | 630 | High
2 | South | 211884972 | 31/04/2025 | 30 | 3H.8902.../2420019 | DG not starting Email By - KGD Name -J Sathish Balaji | Task Start | N. Venkateswaran | Madhu Engineering Sales & Service - Teynampet,Chennai | 48 | Engine not start proplem. due to controller backside wiring connector (03) (04) (05) connector loose, re connect then start the DG running ok. | Closed | Mr. NandhaGopal |  |  | 6 | Controller | 7 | 6 | 5 | 210 | High
17 | South | 211883582 | 31/04/2025 | 25 | GP3.8702.../2420657 | Voltage Problem Call by : Customer Name :sathi Contact :8760183536 | Task Start | PS EXPORTS & CONSOLIDATES PVT. LTD | Bharath Diesel Sales and Service - Karaikal | 31 | Alternator burn due to Eb supply reverse. R- phase burn. Alternator send to nidec team for investigation. ECU,MPU, wiring harness burned so need to be a new wiring harness and ECU, MPU must so educated the customer | Task Start | Mr. NandhaGopal |  |  | 7 | Alternator | 7 | 5 | 6 | 210 | High
56 | North | 211901434 | 03/04/2025 | 125.4 | 4H.8041.../2420197 | Genset Trip | Task Start | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad | 2421 | UREA LEVEL (TOP UP) THEN CHECK TO START DG ON LOAD ITS TRIPPING AND INCREASE THE RPM FROM 1351 TO 1602 OR VOLTAGES ARE 415 VAC TO 395 SO,CHECK AND CLEAN FUEL LINE AND REPLACED THE FUEL FILTER OR REPROGRAMMING (FLASHING) THE ECU AND SET THE CONTROLLER AS PER SITE REQUIREMENTS THEN CHECK TO START AND TESTING ON LOAD FOR ONE HOURS DG SET OK, BUT ITS UNDER OBSERVATION FOR FEW DAYS. | Monitoring | Kapil Solanki |  |  | 4 | ECU | 10 | 9 | 7 | 630 | High
46 | North | 211895118 | 01/04/2025 | 500 | DV8.8501.C4../2420020 | Emergency stop alarm issue Call By Customer Name :- Ajay Number :- 9958214785 | Completed | ESQUIRE TECH.. | Vidyut Engineers - New Delhi | 94 | Topup the def and Emergency Switch 1C2 wire was loose tightness the same after that issue resolve | Closed | Kapil Solanki |  |  | 5 | DEF | 8 | 7 | 5 | 280 | High
10 | East | 211878228 | 29/04/2025 | 125.4 | 4H.8041.../2320003 | Display not show urea level | Closed | N.K. CONSTRUCTION & SUPPLIERS | Hibreed Engineering Pvt. Ltd. - Nagaon | 170 | Replaced controller - due to in previous DEF level indication was not available | CLOSED | Ujjwal Das |  |  | 8 | Controller | 7 | 6 | 5 | 210 | High
107 | North | 211899396 | 02/04/2025 | 40 | 3H.8951.../2420947 | Starting/Stopping Issue | Open | General Electric & Machinery Corporation | MegaGen Services Pvt. Ltd. - Ludhiana | 77 | Starting Issue due to -ve wire on controller found loose so corrected the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 4 | Controller | 7 | 6 | 5 | 210 | High
59 | East | 211898502 | 02/04/2025 | 125.4 | 4H.8042.C4../2420844 | Over Heating Issue Call By Customer Name :-Shobit Kumar Number :-7549039250 | Closed | Shantidoot Infra Services Pvt. LTd. | Globalline India Services Private Limited - Patna | 30 | customer complaint was overheating but actually engine temp was 78-85 dgr c after 20min on load, found improper cross ventilation required the exhaust piping | CLOSED | Prabhakar Kumar |  |  | 4 | Load | 8 | 6 | 5 | 240 | High
11 | East | 211878057 | 29/04/2025 | 20 | GP3.8601.../2420741 | Red Lamp On Alarm Issue Call By Customer Name :-Amit .. Mobile No :- 8929151618 | Closed | AAROHI HOSPITALITY | Globalline India Services Private Limited - Purnia | 102 | Red lamp alarm was due to over load - the DG trip due to over load as customer load was | CLOSED | Prabhakar Kumar |  |  | 8 | Load | 8 | 6 | 5 | 240 | High
26 | North | 211881109 | 30/04/2025 | 500 | DV8.8508.C4../2420007 | MCB Lamp Alarm And Emergency Stop Alarm Issue Call By Customer Name :-Nihar Ranjan Mobile No:-8595668201 | Closed | Anand Divine Developers Private Limited. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 14 | Low def level alarm check and found def is not available, Educate the customer kindly purchase the def | Closed | Kapil Solanki |  |  | 8 | DEF | 8 | 7 | 5 | 280 | High
76 | North | 211904159 | 04/04/2025 | 400 | DV8.8542.C4../2420010 | Power Supply Issue Call By Customer Name :-Yetendra Singh Mobile No:-7042248939 | Open | MCAM. Surion India Ltd. | Paluck Technologies Ltd. - Ghaziabad | 258 | Customer gives the over load, so educate the customer please maintain the load | Closed | Kapil Solanki |  |  | 3 | Load | 8 | 6 | 5 | 240 | High
73 | North | 211904467 | 04/04/2025 | 58.5 | T4.8941.../2421994 | LOADING ISSUE CALL BY CUSTOMER NAME-Omveer Singh NUMBER-9999786175 | Open | CHAUDHARY GENERATOR SERVICE | Paluck Technologies Ltd. - Ghaziabad | 499 | FOUND OIL PRESSURE FLT-VLT HIGH TRIPPING IN DG SET AFTER 30 MIN OR SOME TIME 15 MIN OF RUNNING, SO CHECK WIRING HARNESS, FOUND MCB 2A1 WIRE WAS LOOSE AND CHECK THE SENSOR FOUND OK AND FLASH THE FILE OR CLEAR THE DTC THEN CHECK TO START AND STOP DG FOR ONE HOUR TESTING DG SET OK. | Closed | Kapil Solanki |  |  | 3 | Wiring Harness | 7 | 6 | 5 | 210 | High
30 | North | 211881080 | 30/04/2025 | 25 | GP3.8702.../2421212 | Starting/Stopping Issue | Open | KOREA ENGINEERING AND CLEAN TECHNOLOGY CO INDIA [P] LTD | Vidyut Engineers - Noida | 181 | Found emergency stop alarm so reset the alarm then issue resolve | Closed | Kapil Solanki |  |  | 8 | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
60 | East | 211897914 | 02/04/2025 | 125.4 | 4H.8042.C4../2421079 | Electrical Problems | Closed | Shree Shyam Tea Company | Almas Engineers - Sivsagar | 38 | Engine RPM fluctuation on load and without load AS per SE found intake manifold is back pressure the | OPEN | Ujjwal Das |  |  | 5 | Load | 8 | 6 | 5 | 240 | High
70 | North | 211905111 | 04/04/2025 | 40 | 3H.8951.../2421045 | INSTANCES ID :-100788287 SITE ID :-UP/RA/TT/12498 CALL BY CUSTOMER// DG ISSUSE :- DG STARTING PROBLEM NAME:-DENASH NUMBER:-9621704752 | Open | ATC Telecom Infrastructure Private Limited | Excel Diesel Private Limited - Faizabad | 21 | Fuel is not available in the tank and Fuel sensor connector was removed so, fuel percentage not showing in the controller educate the customer kindly maintain the fuel | Closed | Sudhir Awasthi |  |  | 2 | Controller | 7 | 6 | 5 | 210 | High
112 | North | 211894890 | 01/04/2025 | 15 | GP3.8501.../2420293 | Starting/Stopping Issue | Closed | Dr. Sandeep Malik. | SAAN Royal Power Solutions Private Limited - Hisar | 38 | Airlock found in fuel line due to low fuel level so release the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 5 | Fuel Line | 9 | 7 | 6 | 378 | High
36 | North | 211878354 | 29/04/2025 | 125.4 | 4H.8041.../2420182 | Starting/Stopping Issue | Closed | Sunil Generators | OVN Industries Private Limited - New Delhi | 610 | Found battery was not charging due charging alternator fuse was faulty so, Need to replace | Closed | Kapil Solanki |  |  | 8 | Alternator | 7 | 5 | 6 | 210 | High
37 | North | 211878344 | 29/04/2025 | 125.4 | 4H.8041.../2320018 | Abnormal Sound Issue Call by customer Name - Pappu Number -9718863311 | Closed | COLORZ N STYLE PVT. LTD. | Vidyut Engineers - Noida | 71 | low def level topup the def and then issue resolve | Closed | Kapil Solanki |  |  | 8 | DEF | 8 | 7 | 5 | 280 | High
57 | East | 211898535 | 02/04/2025 | 10 | GP3.8301.../2420609 | Alaram failure issue Email By KGD Name :- Ashutosh Kumar Singh | Cancelled | AKSHAYPATRA EQUIPMENTS PVT LTD | HACS Engineering and Tech Private Limited - Jamshedpur |  | Postponed Visit - Work load | CANCELLED | Prabhakar Kumar |  |  | 4 | Load | 8 | 6 | 5 | 240 | High
67 | North | 211900152 | 02/04/2025 | 125.4 | 4H.8041.../2420215 | Electrical Problems | Task Start | SM Partners | Vidyut Engineers - Noida | 16 | Main alternator fitted and High adblue alarm so, flash the file | Closed | Kapil Solanki |  |  | 4 | Alternator | 7 | 5 | 6 | 210 | High
12 | North | 211883916 | 31/04/2025 | 30 | 3H.8902.../2421143 | Starting/Stopping Issue | Task Start | SR. Power Engineers | OVN Industries Private Limited - New Delhi | 1.81 | Air lock in fuel line after start the DG then issue resolve | Closed | Kapil Solanki |  |  | 7 | Fuel Line | 9 | 7 | 6 | 378 | High
61 | East | 211894989 | 01/04/2025 | 125.4 | 4H.8041.../2420314 | Power supply Issue Call By Customer Name :- Ajit Kumar Sharma Mobile No :- 9800804124 | Closed | Damco India Private Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 114 | customer load was unbalance due to which voltage was fluctuating no issue in DG on balance load it was stable | CLOSED | Ujjwal Das |  |  | 5 | Load | 8 | 6 | 5 | 240 | High
59 | North | 211901195 | 03/04/2025 | 200 | 6H.8435.../2420025 | Starting Issue Call By Customer Name :- Gaurav Mobile No :-7976790652 | Task Start | MORINGA HILL RESORT | BSES (I) Pvt. Ltd. - Udaipur | 672 | Low Def level so, topup the same and Emegency alarm check and found connection loose after that issue resolve | Closed | Gourav sharma |  |  | 4 | DEF | 8 | 7 | 5 | 280 | High
9 | East | 211879041 | 29/04/2025 | 82.5 | 5H.8901.../2420464 | Error code issue Called by customer Name : Yogesh Number : 7879661902 | Closed | KALYAN JEWELLERS.. | HACS Engineering and Tech Private Limited - Deoghar | 206 | air lock issue - found fuel line banjo loose at fuel filter so removed air and the retigthen the banjo after checked for 2 3 times found ok | CLOSED | Prabhakar Kumar |  |  | 8 | Fuel Line | 9 | 7 | 6 | 378 | High
41 | East | 211902880 | 03/04/2025 | 15 | GP3.8501.../2420781 | Red lamp on alarm issue Called by customer Name : Ratan Number : 6000379554 | Cancelled | Ratan Sen | Almas Engineers - Sivsagar |  | Postponed Visit - Work load | CANCELLED | Ujjwal Das |  |  | 3 | Load | 8 | 6 | 5 | 240 | High
5 | East | 211884111 | 31/04/2025 | 125.4 | 4H.8042.C4../2420883 | Red Lamp Alarm Issue Call by customer Name - Mukesh Kumar No - 9304928319 | Task Start | CIRCUIT HOUSE KATIHAR | Globalline India Services Private Limited - Purnia | 16 | ECU fault 516166 code so flashed the ECU issue resolved | CLOSED | Prabhakar Kumar |  |  | 6 | ECU | 10 | 9 | 7 | 630 | High
65 | East | 211893758 | 01/04/2025 | 20 | GP3.8601.../2421651 | Tripping issue Called by customer Name : Parsuram Singh Number : 9151061241 | Closed | Girish chanachur &snacks pvt. ltd | HACS Engineering and Tech Private Limited - Jamshedpur | 27 | MCB loose connection - alternator output voltage wire was loose after tightening issue resolved and customer doudt was related KRM that it shows correct after an delay | CLOSED | Prabhakar Kumar |  |  | 5 | Alternator | 7 | 5 | 6 | 210 | High
20 | North | 211883141 | 31/04/2025 | 45 | 3H.8951.../2421695 | MEN ALARM Call By Customer Name =Lalit . No=9818763872 | Task Start | Gaurannga Institute For Vedic Education | Espiem Engines & Machines (P) Limited - Agra | 630 | Low def level alarm topup the def then issue resolve | Closed | Sudhir Awasthi |  |  | 7 | DEF | 8 | 7 | 5 | 280 | High
8 | North | 211878141 | 29/04/2025 | 25 | GP3.8702.../2420006 | Alarm issue Call by customer Name - Gaurav Number -8650930961 | Task Start | ENOVATE LIFESTYLES PRIVATE LIMITED(Candere Lifestyles Jewellery) | R K Engineers - Meerut | 54 | Panel em-switch nc switch not give output so dg controller give em-switch alarm so dg not start change the Switch then issue resolve | Closed | Sudhir Awasthi |  |  | 8 | Controller | 7 | 6 | 5 | 210 | High
104 | North | 211900978 | 03/04/2025 | 15 | GP3.8501.../2421617 | Automation Issue Call By Customer Name - RAKESH BATRA No - | Task Start | MRS. ANITA | MegaGen Services Pvt. Ltd. - Jalandhar | 2 | Auto starting issue due to controller programming found wrong (mains enable for semi-auto from Input E) so corrected the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 4 | Controller | 7 | 6 | 5 | 210 | High
64 | East | 211893856 | 01/04/2025 | 25 | GP3.8702.../2421429 | Auto Panel Issue Call By KGD Name :- Sheetal Gupta Mobile No :- 6299024030 | Cancelled | KAJAL ENTERPRISES | Globalline India Services Private Limited - Biharsharif |  | Postponed Visit - Work load- | CANCELLED | Prabhakar Kumar |  |  | 5 | Load | 8 | 6 | 5 | 240 | High
83 | North | 211903225 | 03/04/2025 | 40 | 3H.8951.../2420625 | Starting/Stopping Issue | Closed | Ethens Hotel | S. R Engines Sales And Service - Gorakhpur | 289 | Battery discharge, because charger connection was removed, so done the connection after charge the battery then issue resolve | Closed | Sudhir Awasthi |  |  | 3 | Battery | 8 | 6 | 4 | 192 | Moderate
10 | West | 211904273 | 04/04/2025 | 750 | DV2.8501.C4../2420100 | Alarm issue call by customer name : Kamlesh Khopde number : 8007208547 | Completed | Acropolis purple developer | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 4 | Def pressure not generate in bank 2 interchange the supply module, found ok then remove the dosing module found burnt so need to replace. | Open | Jagdeep Saini |  |  | 3 | Supply Module | 7 | 5 | 4 | 140 | Moderate
84 | North | 211902295 | 03/04/2025 | 57 | T4.8941.../2320159 | Emergency stop Alarm Call by customer Name:-Vijay . No:-8743030807 | Closed | Shreeyansh Industries | Paluck Technologies Ltd. - Faridabad | 614 | Engine was over heat due to radiator was chocked, so radiator cleaning required | Closed | Kapil Solanki |  |  | 3 | Radiator | 7 | 5 | 4 | 140 | Moderate
42 | South | 211892862 | 01/04/2025 | 15 | GP3.8501.../2421824 | Leakage Issue | Task Start | Dodla Dairy Limited | Bharath Diesel Sales and Service - Dharmapuri | 40 | Dg oil leakage found in oil filter assembly Allen key dummy bolt side. so removed the dummy bolt & applied taplen tab then refitted the dummy bolt. started the engine found normal condition no leakage. | Closed | Mr. NandhaGopal |  |  | 6 | Oil Filter | 6 | 5 | 4 | 120 | Moderate
93 | North | 211905489 | 04/04/2025 | 40 | 3H.8951.../2420325 | starting issue call by costomer name RAJESH KUMAR contact 8219978813 | Task Start | Rajesh Air Conditioner & Refrigeration | SAAN Royal Power Solutions Private Limited - Baddi |  | Under Cancellation - Customer denied for service | Cancelled | Ved Prakash Gupta |  |  | 2 | CAN | 7 | 5 | 4 | 140 | Moderate
15 | North | 211894039 | 01/04/2025 | 200 | 6H.8435.../2320015 | Leakage Issue | Open | TCI Supply Chain Solutions - A division of Transport Corporation of India Limited | Paluck Technologies Ltd. - Ghaziabad | 286 | Attend to site check found oil leakage done DG manual start Stop ok oil check and v belt check and all leakage check and all hose pipe check and all fuel pipe check and and battery water check and coolant check and DG manual start Stop ok oil leakage issue done | open | Kapil Solanki |  |  | 5 | Battery | 8 | 6 | 4 | 192 | Moderate
43 | South | 211892814 | 01/04/2025 | 30 | 3H.8902.../2420391 | Over heat | Task Start | Sunithas. | G-Care Diesels Private Limited - Kannur | 405 | 100/0 Error code. Radiator find blocked condition, check external silencer cladding found cladding damaged, Radiator blocked with cladding particles,need to remove and clean Radiator | Closed | Mr. Sanjaimon S | GOEM issue |  | 6 | Radiator | 7 | 5 | 4 | 140 | Moderate
102 | North | 211901410 | 03/04/2025 | 500 | DV8.8501.C4../2420078 | Radiator Cap Damage | Open | MTI. Industries Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 367.1 | Radiator cap found damaged so replace the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 4 | Radiator | 7 | 5 | 4 | 140 | Moderate
85 | North | 211902206 | 03/04/2025 | 58.5 | T4.8941.../2420650 | Starting Issue Call By Customer Name Raju Ji NO:9001399660 | Closed | Mahadev Building Material | Rajdhani Diesels and Electricals - Barmer | 312 | Air lock in fuel remove the air after that issue resolve | Closed | Gourav sharma |  |  | 3 | Air Lock | 6 | 5 | 4 | 120 | Moderate
90 | North | 211906768 | 04/04/2025 | 500 | DV8.8501.C4../2420389 | Leakage Issue | Closed | Orchid Hospitality Services Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 471 | Coolant leakage found from Radiator tank(Bottom side) due to clamp found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 2 | Radiator | 7 | 5 | 4 | 140 | Moderate
13 | North | 211885326 | 31/04/2025 | 58.5 | T4.8941.../2422036 | Starting/Stopping Issue | Closed | MANSAROVAR EYE HOSPITAL | S. R Engines Sales And Service - LUCKNOW | 22 | Air lock in fuel remove the air after that issue resolve | Closed | Sudhir Awasthi |  |  | 6 | Air Lock | 6 | 5 | 4 | 120 | Moderate
12 | North | 211885513 | 31/04/2025 | 58.5 | T4.8941.../2422852 | Starting/Stopping Issue | Closed | VIJAY KUMAR VERMA | S. R Engines Sales And Service - LUCKNOW | 45 | Air lock in fuel remove the air after that issue resolve | Closed | Sudhir Awasthi |  |  | 6 | Air Lock | 6 | 5 | 4 | 120 | Moderate
1 | East | 211903346 | 03/04/2025 | 200 | 6H.8435.../2420108 | Leakage Issue | Completed | M/s. Innovative Construction | Gangpur Sales and Services - Cuttack | 213 | SE found engine not start due to water mixed in fuel. Then clean fuel tank, change fuel filter. Clear DTC. Then start the engine, Now DG is running ok on load. | CLOSED | Ujjwal Das |  |  | 3 | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
10 | North | 211886268 | 31/04/2025 | 125.4 | 4H.8041.../2420251 | MCB lamp Blink issue and Error code issue Call By Customer Name:AVINASH ... Number:9953106484 | Closed | Pratham Mri Centre LLP. | Paluck Technologies Ltd. - Gurgaon | 344 | Low def level alarm topup the def clear the DTC after that issue resolve | Closed | Kapil Solanki |  |  | 6 | DTC | 6 | 5 | 4 | 120 | Moderate
11 | West | 211893415 | 01/04/2025 | 20 | GP3.8601.../2420321 | Starting/Stopping Issue | Task Start | Realix Risk Care Hospital | Transcreek Engineers Pvt. Ltd. - Thane | 16 | Abnormal sound, Zero Oil Pressure when checked with LLOP gauge (Video attached),When Oil drained metal particles found, engine dismental and send to the workshop. | Open | Jagdeep Saini |  |  | 5 | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
78 | North | 211904119 | 04/04/2025 | 25 | GP3.8702.../2421723 | Oil Leakage Issue Email By - OEM Name -Piyush Sharma Jaipur | Open | Shri Jagdamba Udyog | Pratap Diesels Pvt. Ltd. - Sikar | 6 | Oil leakage from near oil filter allen key bolt so, change the washer after that issue resolve | Closed | Gourav sharma |  |  | 3 | Oil Filter | 6 | 5 | 4 | 120 | Moderate
20 | North | 211893193 | 01/04/2025 | 125.4 | 4H.8041.../2420825 | Over Heating Issue Call by Customer Name : Manoj Sir Number : 9911311755 | Closed | BANSAL ASSOCIATES | OVN Industries Private Limited - New Delhi | 2374 | Found radiator was chocked so, clean the Radiator after that issue resolve | Closed | Kapil Solanki |  |  | 6 | Radiator | 7 | 5 | 4 | 140 | Moderate
57 | North | 211901416 | 03/04/2025 | 750 | DV2.8501.C4../2320003 | Trip_Genset_Low_Voltage | Closed | MRS. Bectors Food Specialities Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 545 | Radiator chocked so, cleaning required | Closed | Gourav sharma |  |  | 4 | Radiator | 7 | 5 | 4 | 140 | Moderate
50 | North | 211894523 | 01/04/2025 | 58.5 | T4.8941.../2520332 | Starting Issue Email By KGD Name:-Lokesh Gautam | Open | JEET INTERNATIONAL | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Cancelled | Cancelled | Gourav sharma |  |  | 5 | CAN | 7 | 5 | 4 | 140 | Moderate
49 | North | 211894543 | 01/04/2025 | 320 | F6.8802.../2320047 | Starting issue Called by Customer Name:-Kuldeep Mobile No:-9929629080 | Closed | GREEN FIELD INDUSTRIES A UNIT OF S D CHEM PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar | 129 | Battery terminal dusty and clean the same after that start the DG then issue resolve | Closed | Gourav sharma |  |  | 5 | Battery | 8 | 6 | 4 | 192 | Moderate
58 | North | 211901230 | 03/04/2025 | 625 | DV0.8501.C4../2320001 | Coolent leakage issue Call By Customer Name :- Pradip Kumar Mobile No :- 8178306138 | Task Start | Tata Tele services | Vidyut Engineers - New Delhi | 58 | Found coolant leakage from radiator cap Engineer run the DG for 3 times but found leakage only 1 time now under observation | Monitoring | Kapil Solanki |  |  | 4 | Radiator | 7 | 5 | 4 | 140 | Moderate
61 | North | 211901099 | 03/04/2025 | 82.5 | 5H.8901.../2320078 | KRM Issue Call By Customer Name :-Shoukin Khan Mobile No:-7827824447 | Closed | Pragya Components Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 773 | KRM not working check and found KRM connector was removed so, connect the connector after KRM working ok | Closed | Kapil Solanki |  |  | 4 | KRM | 6 | 5 | 4 | 120 | Moderate
62 | North | 211901044 | 03/04/2025 | 30 | 3H.8902.../2421144 | starting issue Call By Customer Name - sandip No -9415216286 | Task Start | VIVANTA DEVELOPER | S.S. Enterprises - Allahabad | 11 | Air lock in fuel remove the air after that issue resolve | Closed | Sudhir Awasthi |  |  | 4 | Air Lock | 6 | 5 | 4 | 120 | Moderate
45 | North | 211895107 | 01/04/2025 | 320 | F6.8802.../2320039 | ECU Malfunction Alarm and Under Voltage Alarm issue Call By Customer Name:-Yashwant Singh Mobile No:-8979131986 | Task Start | EXPRESS TOWERS PVT LTD | Espiem Engines & Machines (P) Limited - Agra | 494 | Found Radiator was chocked, so cleaning required, and DG show the Under volatge alarm and trip the DG and check the voltage found 25V after that found Diode was damage so, need to replace the RRA plate | open | Sudhir Awasthi | Alternator issue |  | 5 | Radiator | 7 | 5 | 4 | 140 | Moderate
44 | North | 211895172 | 01/04/2025 | 320 | F6.8802.../2320039 | Trip_Genset_Low_Voltage | Open | EXPRESS TOWERS PVT LTD | Espiem Engines & Machines (P) Limited - Agra |  | Cancelled-Double SR open | Cancelled | Sudhir Awasthi |  |  | 5 | CAN | 7 | 5 | 4 | 140 | Moderate
63 | North | 211900957 | 03/04/2025 | 125 | 4H.8052.C4../2520057 | fuel moter not working | Task Start | Radhika Jewelescrafts Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - JAIPUR | LR-1 | NRV not working so, replace the NRV after that issue resolve | Closed | Gourav sharma |  |  | 4 | NRV | 6 | 5 | 4 | 120 | Moderate
64 | North | 211900932 | 03/04/2025 | 30 | 3H.8902.../2320057 | Starting/Stopping Issue | Task Start | Deev Gen Set Sales & Services | Vidyut Engineers - New Delhi | 37 | Battery not working check and found 5 cell specific gravity found 1100 and 1150 and 1 cell 0 so, replace the battery | Closed | Kapil Solanki |  |  | 4 | Battery | 8 | 6 | 4 | 192 | Moderate
40 | North | 211897816 | 02/04/2025 | 500 | DV8.8501.C4../2320034 | Starting Issue And Abnormal Sound Issue And Self Starer Issue Call By Customer Name :-Ajay Kumar Pande Mobile No:-9549898615 | Closed | Sunil Healthcare Limited | Pratap Diesels Pvt. Ltd. - Alwar | 79 | Battery terminal dusty and XDBK 1, 2, 3 Connector loose so, tightness the same after that issue resolve | Closed | Gourav sharma |  |  | 5 | Battery | 8 | 6 | 4 | 192 | Moderate
5 | West | 211908032 | 05/04/2025 | 25 | GP3.8702.../2421910 | Power supply Issue Call By Customer Name :- Gayendr Singh1 Mobile No :- 9099167500 | Open | ICICI Bank | Unique Techno Services Pvt Ltd. - Jamnagar |  | Given up for cancellation | Open | Amit Shandilya |  |  | 2 | CAN | 7 | 5 | 4 | 140 | Moderate
120 | North | 211893071 | 01/04/2025 | 58.5 | T4.8941.../2421209 | Automation Issue. Call By Customer. Name:- NARINDER GARG. Mobile No.:-9878922199 | Open | JTL. Industries Limited | SAAN Royal Power Solutions Private Limited - Zirakpur | 68.58 | Under Cancellation | Cancelled | Ved Prakash Gupta |  |  | 6 | CAN | 7 | 5 | 4 | 140 | Moderate
121 | North | 211892905 | 01/04/2025 | 625 | DV0.8501.C4../2420133 | Coolant Leakage Issue. Call By Customer. Name:-Nile Kamal Mobile No.:- 9816638099 | Cancelled | ALMED LABORATORIES PVT LTD | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 24.33 | Under Cancellation | Cancelled | Ved Prakash Gupta |  |  | 6 | CAN | 7 | 5 | 4 | 140 | Moderate
34 | North | 211898677 | 02/04/2025 | 30 | 3H.8902.../2420952 | Battery voltage | Task Start | INDO ENGINEERING SERVICES | Espiem Engines & Machines (P) Limited - Aligarh | 104 | Battery voltage low, charge the battery and connect the battery charger after start the dg then issue resolve | Closed | Sudhir Awasthi |  |  | 4 | Battery Charger | 7 | 5 | 4 | 140 | Moderate
33 | North | 211898678 | 02/04/2025 | 30 | 3H.8902.../2420952 | i | Open | INDO ENGINEERING SERVICES | Espiem Engines & Machines (P) Limited - Aligarh |  | Cancelled-Double SR open | Cancelled | Sudhir Awasthi |  |  | 4 | CAN | 7 | 5 | 4 | 140 | Moderate
1 | West | 211905750 | 04/04/2025 | 250 | F6.8841.../2420066 | Leakage Issue | Closed | Sapat International Pvt. Ltd. | Natraj Power Tech - Indore | 92 | Coolant Leakage from radiator hose pipe and overflow the coolant from reservoir tank. | Closed | Vijay Patil |  |  | 2 | Radiator | 7 | 5 | 4 | 140 | Moderate
69 | North | 211899928 | 02/04/2025 | 58.5 | T4.8941.../2422360 | Loading issue Call By Customer Name-Bharat Gulati Number-9873914300 | Cancelled | NORTH INDIA ENGINEEING | Paluck Technologies Ltd. - Ghaziabad |  | Cancelled-Postpone visit | Cancelled | Kapil Solanki |  |  | 4 | CAN | 7 | 5 | 4 | 140 | Moderate
110 | North | 211897935 | 02/04/2025 | 40 | 3H.8951.../2420804 | Starting Issue Call By Customer Name :- Mr.Karan Singh Mobile No :- 8708008300 | Closed | E. M. E. S. S. Constructions. | SAAN Royal Power Solutions Private Limited - Panipat | 136 | Battery voltage found low connect charger,issue resolved after charging | Closed | Ved Prakash Gupta |  |  | 5 | Battery | 8 | 6 | 4 | 192 | Moderate
77 | North | 211904172 | 04/04/2025 | 30 | 3H.8902.../2320057 | BATTERY FITMENT | Task Start | Deev Gen Set Sales & Services | Vidyut Engineers - New Delhi | 37 | Replace the Battery under warranty | Closed | Kapil Solanki |  |  | 3 | Battery | 8 | 6 | 4 | 192 | Moderate
80 | North | 211903607 | 03/04/2025 | 40 | 3H.8951.../2420081 | Starting Issue Call By Customer Name Sahil Sharma NO:9953965999 | Closed | NEW BHARDWAJ ELECTRICAL WORKS | Paluck Technologies Ltd. - Faridabad | 462 | DG not start because Emergency alarm showing again and again then check and found Canopy Emergency NC point was open and wire was cut so, connect the same after that issue resolve | Closed | Kapil Solanki |  |  | 3 | CAN | 7 | 5 | 4 | 140 | Moderate
81 | North | 211903571 | 03/04/2025 | 125 | 4H.8052.C4../2520080 | Starting Issue Call By Customer Name Shivam Shivam NO:9599493914 | Cancelled | SHIVAM SALES | Paluck Technologies Ltd. - Ghaziabad |  | Under Cancellation - Out of scope | Cancelled | Kapil Solanki |  |  | 3 | CAN | 7 | 5 | 4 | 140 | Moderate
22 | North | 211893138 | 01/04/2025 | 82.5 | 5H.8901.../2420753 | Genset Trip | Closed | MONGA SWEETS PRIVATE LIMITED. | OVN Industries Private Limited - New Delhi | 12 | Air lock in fuel remove the air after that issue resolve | Closed | Kapil Solanki |  |  | 6 | Air Lock | 6 | 5 | 4 | 120 | Moderate
3 | West | 211909145 | 05/04/2025 | 125.4 | 4H.8041.../2420917 | STARTING PROBLEM | Task Start | DA Egg Industries. | Shree Engineering Service - Raipur | 1.46(LR) | The DEF pipe from supply module to dosing module was cut by rats. Hence it will be replaced on customer's payment basis. | Open | Vijay Patil |  |  | 1 | Supply Module | 7 | 5 | 4 | 140 | Moderate
115 | North | 211893503 | 01/04/2025 | 750 | DV2.8501.C4../2420131 | Fuel consumption issue | Open | GS PROMOTORS AND DEVELOPERS | SAAN Royal Power Solutions Private Limited - Zirakpur | 9.07 | Under Cancellation - No Issue in DG | Cancelled | Ved Prakash Gupta |  |  | 5 | CAN | 7 | 5 | 4 | 140 | Moderate
2 | East | 211902259 | 03/04/2025 | 2.8 | AP1.7003.../2400155 | Starting/Stopping Issue | Closed | PRADAN | Gangpur Sales and Services - BHUBANESWAR | 8 | SE found engine not start due to Battery terminal loose, tight the battery terminal issue resolved | CLOSED | Ujjwal Das |  |  | 3 | Battery | 8 | 6 | 4 | 192 | Moderate
98 | North | 211904241 | 04/04/2025 | 40 | 3H.8951.../2320091 | HIGHT TEMPERATURE ALARM CALL BY CUSTOMER NAME-Shubham Mittal NUMBER-9802626001 | Closed | Tisha Agro Industries LLP. | SAAN Royal Power Solutions Private Limited - Rohtak | 1017 | Engine temperature high alarm ; Radiator found choked due to silencer cladding found broken ; same mailed to concerned GOEM | Closed | Ved Prakash Gupta | GOEM issue |  | 3 | Radiator | 7 | 5 | 4 | 140 | Moderate
3 | East | 211901814 | 03/04/2025 | 15 | GP3.8501.../2420154 | Electrical Problems | Closed | Archana Jwellers | Revenus Industries Pvt. Ltd. - Midnapore | 67 | DG not starting while having proper battery voltage and found no fault code so checked for loose connection found ignition relay 2A wire found loose after tighten checked DG for 3-4 time found healthy in condition | CLOSED | Prosanjit saha |  |  | 3 | Battery | 8 | 6 | 4 | 192 | Moderate
29 | East | 211904789 | 04/04/2025 | 30 | 3H.8902.../2421037 | Leakage Issue | Task Start | Shine Enterprise | Hibreed Engineering Pvt. Ltd. - Nagaon | 791 | SE visited site and found coolant leakage due to water pump pulley thread damaged and the fan hit radiator and damaged it | CLOSED | Ujjwal Das |  |  | 2 | Water Pump | 7 | 6 | 4 | 168 | Moderate
12 | WEST | 211870250 | 27/04/2025 | 2.8 | AP1.7003.../2400129 | Starting Issue Call By Customer Name :- Anosh . Mobile No :- 8590600447 | Closed | Gold Plast | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 9.1 | Battery +ve wire connection found loose so tight the same, and issue solved. | Closed | Jagdeep Saini |  |  | 10 | Battery | 8 | 6 | 4 | 192 | Moderate
54 | East | 211899543 | 02/04/2025 | 15 | GP3.8501.../2520192 | Red lamp On Alarm Issue. Call By Customer Name:-Rajiv ... Mobile No:- 6203996756 | Closed | SHASHANK SINGH | Globalline India Services Private Limited - Begusarai | 16 | Due to emergency switch alarm found loose at canopy lamp and emergency switch connector loose after tightening properly issue resolved | CLOSED | Prabhakar Kumar |  |  | 4 | CAN | 7 | 5 | 4 | 140 | Moderate
10 | WEST | 211871559 | 27/04/2025 | 15 | GP3.8501.../2421275 | Other-1st service | Closed | Shalini Petroleum. | Dicksons Engineering Co.Pvt.Ltd. - AMRAVATI | 85 | Battey discharged due to loose connection from battery charger, tight the wire properly and issue solved. | Closed | Jagdeep Saini |  |  | 10 | Battery Charger | 7 | 5 | 4 | 140 | Moderate
8 | WEST | 211872754 | 28/04/2025 | 40 | 3H.8951.../2421746 | INSTANCE ID:-100804145 SITE ID:-6081 CALL BY CUSTOMER// DG ISSUE:-DG PROBLEM NAME:-SANDESH MORE NUMBER:-9405482653 | Closed | Axis Bank Ltd | Dhanashree Technocrats Pvt. Ltd. - Nasik | 3 | coolant leakage from radiator hose pipe , tight the clip issue resolved. | Closed | Jagdeep Saini |  |  | 10 | Radiator | 7 | 5 | 4 | 140 | Moderate
27 | North | 211881101 | 30/04/2025 | 5.5 | CC1.1013.../2400303 | Maintanance Due Alarm Issue Call By Customer Name :- Rajveer . Mobile No :-9602436354 | Cancelled | YUVTARA INTERNATIONAL PVT LTD | Pratap Diesels Pvt. Ltd. - BIKANER |  | Under Cancellation | Cancelled | Gourav Sharma |  |  | 8 | CAN | 7 | 5 | 4 | 140 | Moderate
4 | WEST | 211881139 | 30/04/2025 | 15 | GP3.8501.../2421283 | Red lamp Alarm Issue Call By Customer Name :-PRAVIN BHAVANE Mobile No:-8411051931 | Closed | SUPERINTENDENT OF POLICE | Dicksons Engineering Co.Pvt.Ltd. - Akola | 2 | Loose connection found between battery charger and battery so tight the wire . | Closed | Jagdeep Saini |  |  | 8 | Battery Charger | 7 | 5 | 4 | 140 | Moderate
52 | East | 211900969 | 03/04/2025 | 30 | 3H.8902.../2420655 | Maintenance Due Alarm Call By KGD Name :- Sheetal Gupta Mobile No :-6299024030 | Closed | ANURAG MEDICAL | HACS Engineering and Tech Private Limited - Hazaribagh | 90 | Found abnormal sound due to exhaust bellow bolt loose after tightening it found no abnormal noise | CLOSED | Prabhakar Kumar |  |  | 4 | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
2 | WEST | 211881934 | 30/04/2025 | 15 | GP3.8501.../2520418 | Under speed issue Call By Customer Name :- Shanil Mobile No :-9746670218 | Open | M. Tech Engineers | Mahalaxmi Diesels - Goa |  | cancelled | Closed | Jagdeep Saini |  |  | 7 | CAN | 7 | 5 | 4 | 140 | Moderate
37 | East | 211903364 | 03/04/2025 | 20 | GP3.8604.../2420069 | INSTANCE ID:-100740940 SITE ID:-I-BR-TEGR-ENB-9028 CALL BY CUSTOMER// DG ISSSUE:-DG PROBLEM NAME:-GOPAL KUMAR NUMBER:-8709475367 | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Begusarai | 1938 | Battery teminal loose that why DG was not cranking after tightening the terminal clamp issue resolved | CLOSED | Prabhakar Kumar |  |  | 3 | Battery | 8 | 6 | 4 | 192 | Moderate
39 | South | 211892939 | 01/04/2025 | 125.4 | 4H.8042.C4../2420002 | Starting Problem Call by : Customer Name : Rahim Contact : 9346476201 | Task Start | Haneef Scans & Interventions | Ultimate Power Source - Kurnool | 15 | Battery discharge due to EB supply not given | Closed | Mr. NandhaGopal |  |  | 6 | Battery | 8 | 6 | 4 | 192 | Moderate
13 | East | 211877402 | 29/04/2025 | 20 | GP3.8601.../2420165 | Starting Issue And Red Lamp On Alarm Call By Customer Name :-Ramesh Kumar Mobile No:-9934345077 | Closed | Ramesh Kumar Kesari | HACS Engineering and Tech Private Limited - Ranchi | 146 | DG not starting due to any loose connection in panel (SE is unable to connect the call) | CLOSED | Prabhakar Kumar |  |  | 9 | Loose Connection | 5 | 6 | 4 | 120 | Moderate
48 | East | 211902087 | 03/04/2025 | 10 | GP3.8301.../2420077 | Tripping Issue Call By Customer Name :- Sunil . Mobile No :-9006516463 | Closed | District Judge Gaya | Globalline India Services Private Limited - Gaya | 55 | found DG not cranking battery voltage foung ok so checked the start relay tighten its relay switch and coil point also tighten starter motor solenoid + wire thencranked DG started | OPEN | Prabhakar Kumar |  |  | 3 | Starter Motor | 7 | 4 | 5 | 140 | Moderate
47 | East | 211902275 | 03/04/2025 | 250 | F6.8841.../2420393 | Coolant Leakage Issue Call By Customer Name :-Faiz Mobile No:-7070520164 | Open | SCH Technologies Pvt. Ltd. | Globalline India Services Private Limited - Patna, Exhibition Road |  | coolant top issue - cancelled | CANCELLED | Prabhakar Kumar |  |  | 3 | CAN | 7 | 5 | 4 | 140 | Moderate
4 | East | 211884223 | 31/04/2025 | 160 | 6H.8475.../2420162 | Error code show | Closed | Ms Ankur Enterprise | Hibreed Engineering Pvt. Ltd. - Nagaon | 333 | cam sensor code 636,5- Engine Position Sensor-Current Below Normal but DG was running only code was triggering so replaced sensor but same issue so SE refitted the previous sensor after cleaning the senor and cam wheel and pressed the sensor female side pin after that flashed ECU now resolved found no code. | CLOSED | Ujjwal Das |  |  | 6 | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
3 | East | 211884528 | 31/04/2025 | 45 | 3H.8951.../2420194 | Starting Issue Call By Customer Name:-Goutam . No:-9097823443 | Task Start | awadh developers | Globalline India Services Private Limited - Patna | 1 | low battery voltage issue as at time commisioning customer had not provided the the mains supply | CLOSED | Prabhakar Kumar |  |  | 6 | Battery | 8 | 6 | 4 | 192 | Moderate
44 | East | 211902778 | 03/04/2025 | 20 | GP3.8604.../2420180 | Dg taking under volt alarm | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 465 | Under voltage alarm - due to loose connection of voltage sensing wire | OPEN | Prabhakar Kumar |  |  | 3 | Loose Connection | 5 | 6 | 4 | 120 | Moderate
21 | West | 211877533 | 29/04/2025 | 125.4 | 4H.8042.C4../2420003 | Starting Issue Call By Customer Name : Akshay Number : 9116556796 | Task Start | Manali Industries. | Shree Engineering Service - Jabalpur | 11.1 | DG not starting. No error code found in controller and iKonnect not connecting with communication error. Checked the C & D point voltage wrt ground-0VDC. Checked continuity of the CAN line found ok. Ignition supply- 13.1VDC. Checked the power supply between K1,K3 & K5 wrt ground. K01 & ground- 13V, K03 & ground- 0VDC and K05 & ground- 0VDC. | OPEN | Vijay Patil |  |  | 9 | CAN | 7 | 5 | 4 | 140 | Moderate
18 | North | 211883308 | 31/04/2025 | 125.4 | 4H.8041.../2420197 | Loading Issue Call by customer Name :Lalit Tyagi Number:9810138700 | Task Start | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad | 2403 | Fuel tank was very dirty then change the fuel filter but tank is not cleaning, so Engineer collect the fuel sample | open | Kapil Solanki |  |  | 7 | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
24 | North | 211881838 | 30/04/2025 | 750 | DV2.8501.C4../2420014 | Coolant Mix in oil Issue Call By Customer Name:- No:- | Task Start | Bharat Petroleum Corporation Ltd | Paluck Technologies Ltd. - Ghaziabad | 546 | Coolant mix with Engine oil | open | Kapil Solanki |  |  | 7 | Engine Oil | 7 | 5 | 4 | 140 | Moderate
41 | North | 211883109 | 31/04/2025 | 625 | DV0.8501.C4../2320017 | Starting/Stopping Issue | Open | M/s. Swayut Automation | Suraj Motor Store - Jammu | 9.1 | Under Cancellation | Cancelled | Ved Prakash Gupta |  |  | 7 | CAN | 7 | 5 | 4 | 140 | Moderate
8 | East | 211897675 | 02/04/2025 | 15 | GP3.8501.../2421173 | Flue sensor Issue. Call By Customer. Name:- PURNA TRIPATHY Mobile No.:- 8249811703 | Closed | PURNA CHANDRA TRIPATHY | Gangpur Sales and Services - BHUBANESWAR | 38 | SE found fuel sensor not working due to 1A wire in loose contact then tight the loose contact check fuel level battery earthing panel and all the external nut bolt's tightness then start the engine and engine run ok at Automation | CLOSED | Ujjwal Das |  |  | 5 | Battery | 8 | 6 | 4 | 192 | Moderate
8 | South | 211884480 | 31/04/2025 | 40 | 3H.8951.../2420234 | Leakage Issue | Closed | Amaze Travels Private Limited. | Madhu Engineering Sales & Service -Poonamallee,Chennai | 29 | Checked the leakage in cooler mounting side is leaking,then drain the k coolant,removed the oil cooler checked the orings is bulged then replace the new Oring ,then apply the k sealant out side oring ,then fixed the cooler tightness ok, then wait some time then top-up the k cool checked the level is found ok,then started the engine, checked the leakage is nil. | Closed | Mr. NandhaGopal | Engine issue |  | 6 | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
19 | South | 211883550 | 31/04/2025 | 58.5 | T4.8941.../2422423 | Coolant Leakage Problem Call by : Dealar Name : Paul daniel Contact : 9600334167 Customer name :Gurubalan Customer number :9080295943 | Closed | Thas Kitchen. | Bharath Diesel Sales and Service - Neyveli | 63 | Coolant leakag from radiator hose clamp. So try to retight the clamp but not tight properly,so removed the hose clamp replaced the new hose clamp. | Closed | Mr. NandhaGopal |  |  | 7 | Radiator | 7 | 5 | 4 | 140 | Moderate
63 | East | 211894255 | 01/04/2025 | 20 | GP3.8601.../2421201 | Low Battery Voltage Alarm and Red Light Alarm issue Call By Customer Name : Dheeraj Kumar Number : 9122320667 | Cancelled | Raava Keshri C/O Rishi Kumar | HACS Engineering and Tech Private Limited - Ranchi |  | Approved By ASM- Cancelled | CANCELLED | Prabhakar Kumar |  |  | 5 | CAN | 7 | 5 | 4 | 140 | Moderate
16 | South | 211883641 | 31/04/2025 | 25 | GP3.8702.../2421623 | Electrical Problems | Open | SOPAN O & M CO. PVT. LTD. | G-Care Diesels Private Limited - Ernakulam |  | AMF pannel issue .Need to Cancelled SR. | Open | Mr. Sanjaimon S |  |  | 7 | CAN | 7 | 5 | 4 | 140 | Moderate
2 | North | 211873757 | 28/04/2025 | 40 | 3H.8951.../2421356 | Door Look Issue Call By Customer Name :- KOUSHALA RAM Mobile No 7073577023 | Task Start | KOUSHALA RAM S/O PADMA RAM | Rajdhani Diesels and Electricals - Barmer |  | During transpotation canopy was damage | open | Gourav Sharma |  |  | 9 | CAN | 7 | 5 | 4 | 140 | Moderate
7 | East | 211898195 | 02/04/2025 | 30 | 3H.8902.../2420748 | Starting Issue. Call By OEM Name:-Sujit Kumar Nayak Mobile No:-7978972767 | Cancelled | M/S Shree Mahavir Enterprises | Gangpur Sales and Services - Bhubaneswar |  | Not able to contact with the customer,so cancel the SR | CLOSED | Ujjwal Das |  |  | 5 | CAN | 7 | 5 | 4 | 140 | Moderate
5 | East | 211899866 | 02/04/2025 | 30 | 3H.8902.../2421182 | Automation Issue Call By Customer Name : Number : 7718838463 | Closed | Abis Exports India Pvt Ltd. | Gangpur Sales and Services - Keonjhar | 121 | SE Found Automation issue due to 11 no wire loose connection, after that tight the connection issue resolved | CLOSED | Ujjwal Das |  |  | 4 | Loose Connection | 5 | 6 | 4 | 120 | Moderate
35 | South | 211893043 | 01/04/2025 | 250 | F6.8841.../2420433 | Battery Problem Call by : Customer Name :Nishad Contact :6282412855 | Task Start | Eram Property Network Private Limited | G-Care Diesels Private Limited - Ernakulam | 3 | Found input connection form main EB to battery charger is cut off checked and rectified the problem with customer electrical person .Now battery charger working (27.1 )found normal | Closed | Mr. Sanjaimon S |  |  | 6 | Battery Charger | 7 | 5 | 4 | 140 | Moderate
62 | East | 211894466 | 01/04/2025 | 125.4 | 4H.8041.../2420938 | Heating issue Call by Customer Name - Ankit Number - 6206638122 | Cancelled | Shantidoot Infra Services Pvt. LTd. | HACS Engineering and Tech Private Limited - Ranchi |  | Machine Shift to Other Territ- cancelled | CANCELLED | Prabhakar Kumar |  |  | 5 | CAN | 7 | 5 | 4 | 140 | Moderate
37 | South | 211892969 | 01/04/2025 | 25 | GP3.8702.../2420171 | Leakage Issue | Task Start | Universal Farm House | Bharath Diesel Sales and Service - Pattanur | 191 | Found light leakage from radiator bottom hose side, so hose clamp retight. No marking in Hose clamp | Task Start | Mr. NandhaGopal |  |  | 6 | Radiator | 7 | 5 | 4 | 140 | Moderate
19 | East | 211908631 | 05/04/2025 | 35 | 3H.8902.../2421674 | Fuel Issue ,Starting Issue Call By Customer Name:-Abhay Mobile No:-9934880692 | Task Start | Gurudev Faishon | Globalline India Services Private Limited - Bhagalpur | 92 | Dg not starting due to low battery voltage so for customer statisfaction arrange another battery then statted cranked DG started normally no issue in DG | CLOSED | Prabhakar Kumar |  |  | 1 | Battery | 8 | 6 | 4 | 192 | Moderate
17 | East | 211905232 | 04/04/2025 | 20 | GP3.8601.../2420372 | STARTING ISSUE CALL BY CUSTOMER NAME-Sudhir Kumar Patel NUMBER-9938250488 | Closed | Sudhir Kumar Patel | Gangpur Sales and Services - Jharsuguda |  | SE Found Engine not start due to Battery Charger not working, after that replace the battery charger engine running properly | CLOSED | Ujjwal Das |  |  | 2 | Battery Charger | 7 | 5 | 4 | 140 | Moderate
9 | East | 211894761 | 01/04/2025 | 125.4 | 4H.8042.C4../2520044 | Amber Lamp Alarm Call By Customer Name:-patel . No:-7978605139 | Closed | SHANTILATA HOSPITAL AND RESEARCH CENTRE PVT LTD | Gangpur Sales and Services - Jharsuguda | 23 | 516166,4095/2,4095/1 Reconnect the dosing modele connector and supply module connector | CLOSED | Ujjwal Das |  |  | 5 | Supply Module | 7 | 5 | 4 | 140 | Moderate
101 | North | 211902208 | 03/04/2025 | 58.5 | T4.8941.../2422443 | Electrical Problems | Closed | KIRTI TRADERS | SAAN Royal Power Solutions Private Limited - Sonipat | 28.4 | AVR Card fuse found blown so replace the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
114 | North | 211893564 | 01/04/2025 | 25 | GP3.8702.../2520281 | Loading issue Call By Customer Name :- Sandeep Mittal Mobile No :- 9888879276 | Closed | Arihant Solution | SAAN Royal Power Solutions Private Limited - Zirakpur | 20 | DG not operating in auto mode due to customer's pannel faulty ; same communicated to customer | Closed | Ved Prakash Gupta |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
49 | East | 211901322 | 03/04/2025 | 82.5 | 5H.8901.../2420706 | Automation issue | Closed | KALYAN JEWELLERS.. | HACS Engineering and Tech Private Limited - Deoghar |  | Mains issue due to which DG was not stopping (one phase voltage was dropping) after fixing it issue resolved | CLOSED | Prabhakar Kumar |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
50 | East | 211901075 | 03/04/2025 | 20 | GP3.8601.../2420266 | Electrical Problems | Open | Chakesang Baptist Church | Hibreed Engineering Pvt. Ltd. - Jorhat |  | visit pending | OPEN | Ujjwal Das |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
51 | East | 211901067 | 03/04/2025 | 82.5 | 5H.8901.../2420155 | Electrical Problems | Open | G. Kiba. . | Hibreed Engineering Pvt. Ltd. - Jorhat |  | visit pending | OPEN | Ujjwal Das |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
58 | East | 211898531 | 02/04/2025 | 20 | GP3.8601.../2421673 | Red Lamp on Issue Email By - KGD Name -Power Generators | Closed | Oil Bank | Almas Engineers - Dibrugarh | 96 | Emergency stop switch wire loose at it NO NC point after tightening issue resolved | CLOSED | Ujjwal Das |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
66 | East | 211893629 | 01/04/2025 | 30 | 3H.8902.../2421628 | Electrical Problems | Closed | Vibrant Induction Private Limited | Hibreed Engineering Pvt. Ltd. - Guwahati | 38 | 516166 code - customer hotshutdown the DG so educated him not do so so cleared code issue resolved | CLOSED | Ujjwal Das |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
109 | North | 211898119 | 02/04/2025 | 40 | 3H.8951.../2421785 | Starting/Stopping Issue | Closed | Axis Bank Ltd | SAAN Royal Power Solutions Private Limited - Rohtak | 3 | Starting Relay found in loose condition in AMF Pannel for Auto starting so re-fitted the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 5 | Relay | 5 | 4 | 3 | 60 | Low
53 | East | 211900224 | 02/04/2025 | 125.4 | 4H.8042.C4../2420906 | Dg tripping on protect lamp on alarm Email By KGD Name:-Gaurav Patil | Cancelled | Perennial Technologies Pvt. Ltd | HACS Engineering and Tech Private Limited - Ranchi |  | Cust Aprvl not receive on time | CANCELLED | Prabhakar Kumar |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
105 | North | 211900965 | 03/04/2025 | 320 | F6.8802.../2320026 | Starting issue | Open | JAYCEE CASTALLOYS (P) LTD. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 173.39 | Output volatge found very low and DG tripped withing 20 second with under voltage alarm ; electrical engineer will visit Today | Open | Ved Prakash Gupta |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
106 | North | 211899572 | 02/04/2025 | 200 | 6H.8435.../2420052 | Electrical Problems | Closed | Amar Hospital | SAAN Royal Power Solutions Private Limited - Zirakpur | 3 | SR opened for Synchronisation | Closed | Ved Prakash Gupta |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
108 | North | 211898562 | 02/04/2025 | 62.5 | T4.8941.../2320267 | Voltage Fluctuation | Closed | Punia Maternity and Orthopaedics Hospital | SAAN Royal Power Solutions Private Limited - Hisar | 221 | Oil leakage found from turbo outlet from exhaust turbo to sump near sump so re-fitted the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
46 | East | 211902355 | 03/04/2025 | 160 | 6H.8475.../2420088 | Automation issue Call By Customer Name:- Vikas Singh No:- 9472916046 | Closed | Urban Development & Housing Department Bihar | Globalline India Services Private Limited - Patna |  | Automation issue relay issue | CLOSED | Prabhakar Kumar |  |  | 3 | Relay | 5 | 4 | 3 | 60 | Low
55 | East | 211899406 | 02/04/2025 | 25 | GP3.8702.../2520143 | Self faulty | Cancelled | ATC Telecom Infrastructure Private Limited | Globalline India Services Private Limited - Siwan |  | SR opened by mistake | CANCELLED | Prabhakar Kumar |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
56 | East | 211898870 | 02/04/2025 | 30 | 3H.8902.../2421552 | automation issue Called by Customer Name:- rakesh singh Mobile No:- 9110021229 | Closed | ANJU DEVI | Globalline India Services Private Limited - Muzaffarpur | 30 | Automation issue due -tive sensing wire loose after tightening issue resolved | CLOSED | Prabhakar Kumar |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
67 | East | 211893262 | 01/04/2025 | 250 | F6.8842.C4../2420080 | Genset Lock out issue and statring issue Called by customer Name : Hirak Jyoti Kakati Number : 8638070728 | Closed | Achyut Promoters And Builders Private Limited | Hibreed Engineering Pvt. Ltd. - Nagaon | 22 | Emergency switch alarm found it was pressed after releasing it issue resolved found ok | CLOSED | Ujjwal Das |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
103 | North | 211901154 | 03/04/2025 | 30 | 3H.8902.../2421481 | Starting/Stopping Issue | Completed | SANT MALHOTRA | SAAN Royal Power Solutions Private Limited - Zirakpur | 33 | VMR supply wire found broken so repaired the same & resolve the Issue ;no issue in DG | Closed | Ved Prakash Gupta |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
38 | East | 211903233 | 03/04/2025 | 20 | GP3.8601.../2421222 | Starting Problem Call by : Customer Name :Navinkumarsinha Contact :8825329065 | Closed | Riya Fuels | HACS Engineering and Tech Private Limited - Daltonganj |  | Emergency switch alarm so cheked all connection and refitted properly then issue resolved | CLOSED | Prabhakar Kumar |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
116 | North | 211893469 | 01/04/2025 | 40 | 3H.8951.../2421021 | Start delay issue | Closed | RAKESH GARG. | Gen Powers - Bathinda | 30 | Auto starting wire of 1C2 found loose on push-button so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211898363 | 02/04/2025 | 40 | 3H.8951.../2421775 | Leakage Issue | Closed | JHAJHARIA NIRMAN LIMITED | Revenus Industries Pvt. Ltd. - Howrah | 762 | SE Found engine run is normal but some time running condition time engine rocker cover site lube oil leakage then check rocker cover bolt tightness found 2 rocker cover bolt broken after that change the rocker cover bolt and fitted rocker cover ,issue resolved no leakage found in DG | CLOSED | Prosanjit saha |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211893327 | 01/04/2025 | 15 | GP3.8501.../2422050 | Fuel Leakage Issue Call By Customer Name : Apurba Number : 9599803318 | Closed | MAA SILVER CASTING & JEWELLERY | Revenus Industries Pvt. Ltd. - Hooghly | 2 | SE Found no leakage in DG,Engine running properly | CLOSED | Prosanjit saha |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
100 | North | 211902237 | 03/04/2025 | 15 | GP3.8501.../2420032 | Starting/Stopping Issue | Closed | SHALLA RAM ICE & COLD STORAGE | SAAN Royal Power Solutions Private Limited - Sonipat | 332.4 | Starting issue due to MCB found in trip condition(at F2 of 32 Amp) on site so corrected the same & same communicated to customer | Closed | Ved Prakash Gupta |  |  | 3 | MCB | 5 | 4 | 3 | 60 | Low
12 | East | 211904557 | 04/04/2025 | 625 | DV0.8501.C4../2420072 | Sound/Vibration Issue | Task Start | M/s. Sri Durga Condev P. Ltd. | Gangpur Sales and Services - Cuttack | 46 | SE found V Belt was loose, after that tightening the belt issue resolved | CLOSED | Ujjwal Das |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
8 | West | 211911801 | 06/04/2025 | 58.5 | T4.8941.../2422018 | STARTING ISSUE CALL BY CUSTOMER NAME-NARAYAN NUMBER-8605820586 | Task Start | R D Mart Washim | Dicksons Engineering Co.Pvt.Ltd. - Akola | 71 | emergency alarm showing repeated time so need to check. | Open | Jagdeep Saini |  |  | 0 | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211908338 | 05/04/2025 | 25 | GP3.8702.../2420223 | Voltage Fluctuation | Open | Hindustan Petroleum Corporation Limited (HPCL) Durgapur West Bengal | Revenus Industries Pvt. Ltd. - Asansol |  | Today SE Will visit Site | OPEN | Prosanjit saha |  |  | 1 | Unknown | 1 | 1 | 10 | 10 | Low
14 | East | 211906628 | 04/04/2025 | 125.4 | 4H.8041.../2421001 | Automation Issue Call By Customer Name : Vipul Kumar Thacker Number : 7008011142 | Task Start | Vipul Securities. | Gangpur Sales and Services - Bhubaneswar |  | Update Pending | CLOSED | Ujjwal Das |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211905349 | 04/04/2025 | 125.4 | 4H.8041.../2420883 | Uria level issue Called by customer Name : S Kundu Number : 9732167247 | Open | Shree Krishna Construction | Revenus Industries Pvt. Ltd. - Purulia |  | Visit Pending | OPEN | Prosanjit saha |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
18 | East | 211908774 | 05/04/2025 | 10 | GP3.8301.../2420087 | Oil Leakage Issue. Call By Service Dealer . Name:-Yashika Mobile No.:- 9693063331 | Task Start | AKSHAYPATRA EQUIPMENTS PVT.LTD. | HACS Engineering and Tech Private Limited - Jamshedpur | 1745 | Update Pending | CLOSED | Prabhakar Kumar |  |  | 1 | Unknown | 1 | 1 | 10 | 10 | Low
20 | East | 211908465 | 05/04/2025 | 58.5 | T4.8941.../2420624 | Expansion bellow broken | Closed | Yadav Tent House | Globalline India Services Private Limited - Darbhanga | 264 | This was an old issue expansion bellow damage recreated to change it now properly fitted it no misaligment. | CLOSED | Prabhakar Kumar |  |  | 1 | Unknown | 1 | 1 | 10 | 10 | Low
21 | East | 211908095 | 05/04/2025 | 10 | GP3.8301.../2420609 | TRIPPING ISSUE CALL BY CUSTOMER NAME-PARSHRUM SINGH . NUMBER-9151061241 | Closed | AKSHAYPATRA EQUIPMENTS PVT LTD | HACS Engineering and Tech Private Limited - Jamshedpur | 76 | Emergency switch alarm - reconnected emergency switch NO NC wire also remove its locking screw and after refitted then issue resolved | CLOSED | Prabhakar Kumar |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
24 | East | 211906746 | 04/04/2025 | 20 | GP3.8601.../2421201 | RED LAMP ALARM CALL BY CUSTOMER NAME : NUMBER : | Task Start | Raava Keshri C/O Rishi Kumar | HACS Engineering and Tech Private Limited - Ranchi | 51 | Red alarm due to emergency switch so checked all conector refitted after applying tie then issue resolved | CLOSED | Prabhakar Kumar |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
25 | East | 211906384 | 04/04/2025 | 30 | 3H.8902.../2420703 | AMF panel not working Email By KGD Name :-Power Generators | Open | Njilo Semp | Hibreed Engineering Pvt. Ltd. - Jorhat |  | visit pending | OPEN | Ujjwal Das |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
26 | East | 211905345 | 04/04/2025 | 58.5 | T4.8941.../2422338 | Maintanance due alarm issue Called by customer Name ; Vimal ku Number : 9546817343 | Open | Vimal Engineering | Globalline India Services Private Limited - Siwan |  | Tele discussion -Visit not req | CANCELLED | Prabhakar Kumar |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
27 | East | 211905227 | 04/04/2025 | 7.5 | D3.8305.../2400115 | Battery not charging during Issue Email By - KGD Name - Arup Kr. Ray | Open | M/S S.S Enterprise | Johnson Power Sales & Service - AIZAWAL |  | visit pending | OPEN | Ujjwal Das |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
30 | East | 211904283 | 04/04/2025 | 10 | GP3.8301.../2420243 | TRIPPING ISSUE CALL BY CUSTOMER NAME-SUJIT SIR NUMBER-7001684296 | Open | Ganapati Construction Company | Green Powerline - Dhemaji |  | visit pending | OPEN | Ujjwal Das |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
119 | North | 211893108 | 01/04/2025 | 125.4 | 4H.8041.../2420250 | Oil Leakage issue | Task Start | Dr. Narinder Grover | Gen Powers - Bathinda | 108.42 | Oil leakage found from DG due to Main Oil seal found suspected to be damaged ;Dealer arranging for same Images Required | Open | Ved Prakash Gupta |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
32 | East | 211903815 | 03/04/2025 | 250 | F6.8841.../2420130 | Test | Cancelled | Saraighat Offset Press. | Hibreed Engineering Pvt. Ltd. - Guwahati |  | SR opened by mistake | CANCELLED | Ujjwal Das |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
33 | East | 211903636 | 03/04/2025 | 125.4 | 4H.8042.C4../2420906 | Dg tripping on protect lamp on alarm Email By KGD Name:-Gaurav Patil | Open | Perennial Technologies Pvt. Ltd | HACS Engineering and Tech Private Limited - Ranchi |  | visit pending | OPEN | Prabhakar Kumar |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
34 | East | 211903579 | 03/04/2025 | 5.5 | CC1.1013.../2400453 | Low oil pressure alarm issue Email By - KGD Name -Surekha Auti | Closed | DEPUTY COMMANDANT | Globalline India Services Private Limited - Darbhanga | 40 | LLOP- switch alarm triggered on the display so checked and refitted it after tigtening the female side pin then checked found ok | CLOSED | Prabhakar Kumar |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
118 | North | 211893172 | 01/04/2025 | 40 | 3H.8951.../2420654 | Starting/Stopping Issue | Closed | Girdhar ENT. Hospital | SAAN Royal Power Solutions Private Limited - Hisar | 22 | Starting issue due to wire found loose on self-starter so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
117 | North | 211893312 | 01/04/2025 | 40 | 3H.8951.../2421627 | Starting/Stopping Issue | Closed | TARANPREET SINGH | MegaGen Services Pvt. Ltd. - Ludhiana | 15 | Installation for automation has been installed & trial taken in Auto mode for 2-3 times | Closed | Ved Prakash Gupta |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
39 | East | 211903199 | 03/04/2025 | 5.5 | CC1.1013.../2400156 | tripping issue Call by Service Dealer Name - Parsuram Singh Number -9151061241 | Closed | Swapan Electrical. | HACS Engineering and Tech Private Limited - Jamshedpur | 1090 | RPM dropping issue - so se adjusted the RPM by its actuator then found ok | CLOSED | Prabhakar Kumar |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
40 | East | 211902935 | 03/04/2025 | 10 | GP3.8301.../2420457 | Starting Issue Email By - KGD Name - Arup Kr. Ray | Task Start | GIRIN DEKA | Hibreed Engineering Pvt. Ltd. - Guwahati | 10 | contactor faulty- not working wire after proper voltage so replaced after that issue resolved | CLOSED | Ujjwal Das |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
42 | East | 211902827 | 03/04/2025 | 5.5 | CC1.1013.../2400158 | Tripping Issue Call By BY Service Dealer Name:- Yashika Mobile No:- 9693063331 | Closed | Swapan Electrical. | HACS Engineering and Tech Private Limited - Jamshedpur | 383 | RPM dropping issue - so se adjusted the RPM by its actuator then found ok | CLOSED | Prabhakar Kumar |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
45 | East | 211902389 | 03/04/2025 | 5.5 | CC1.1013.../2400152 | TRIPPING ISSUE CALL BY SERVICE DEALER NAME-PARSHRUM SINGH NUMBER-7004351210 | Closed | Swapan Electrical. | HACS Engineering and Tech Private Limited - Jamshedpur | 381 | RPM dropping issue - so se adjusted the RPM by its actuator then found ok also found MCB wire loose so tighten it | CLOSED | Prabhakar Kumar |  |  | 3 | MCB | 5 | 4 | 3 | 60 | Low
11 | East | 211891562 | 01/04/2025 | 2.8 | AP1.7003.../2400148 | overheating & current issues Email By - KGD Name -Saktimay Satpathy | Closed | RANJIT TENT HOUSE | Gangpur Sales and Services - BHUBANESWAR | 27 | Engine overheating due to not getting proper ventilation | CLOSED | Ujjwal Das |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211876075 | 28/04/2025 | 160 | 6H.8475.../2420467 | Automation issue Call By Customer Name : Prabhat Kumar Number : 8077946512 | Closed | VMC. Fartilizers | Paluck Technologies Ltd. - Ghaziabad | 49 | Under Guide to the customer on Call | Closed | Kapil Solanki |  |  | 9 | Unknown | 1 | 1 | 10 | 10 | Low
96 | North | 211904734 | 04/04/2025 | 15 | GP3.8501.../2420767 | high battery voltage issue call by customer name : nagmeet number : 9814467777 | Open | BALDEV AUTO FUELS | MegaGen Services Pvt. Ltd. - Bathinda |  | Visit Pending | Open | Ved Prakash Gupta |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211883915 | 31/04/2025 | 20 | GP3.8604.../2420051 | INTANCE ID :-100740906 SITE ID :- I-BR-SAAR-ENB-9019 CALL BY CUSTOMER // DG ISSUE :- UNDER VOLTAGE PROBLEM NAME:-RATESH SIR NUMBER :-8340233128 | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 210 | Update Pending | CLOSED | Prabhakar Kumar |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211883743 | 31/04/2025 | 45 | 3H.8951.../2421129 | Silencer issue Call By Customer Name:-Rajesh . No:-9471465472 | Completed | A R ENTERPRISES | Globalline India Services Private Limited - Purnia | 1420 | expansion bellow found damage today SE will visit | OPEN | Prabhakar Kumar |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211877573 | 29/04/2025 | 5.5 | CC1.1013.../2400171 | Battery Issue R Phase Under Voltage Issue Call By Customer Name :- Badal kumar Singh Mobile No :- 7858925854 | Task Start | Mahadev Advertiser | Globalline India Services Private Limited - Darbhanga | 9 | Inverter module faulty - SE visited site and found no output voltage at inverter module so replaced then issue resolved | CLOSED | Prabhakar Kumar |  |  | 9 | Unknown | 1 | 1 | 10 | 10 | Low
17 | East | 211880474 | 29/04/2025 | 125.4 | 4H.8041.../2421029 | Oil leakage issue Call By Customer Name:Nursatam chetti Number:6371207771 | Open | KALYAN JEWELLERS INDIA LTD | Gangpur Sales and Services - Jharsuguda | 128 | SE found lub oil leakage due to dipstick loose Then proper tight the dipstick & start the engine found no leakage. | CLOSED | Ujjwal Das |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
18 | East | 211879815 | 29/04/2025 | 20 | GP3.8601.../2421180 | Starting Issue Call By Customer Name - GIRDHARI PATEL Number - 9937763236 | Open | GIRDHARI PATEL | Gangpur Sales and Services - Bargarh | 116 | Update Pending | CLOSED | Ujjwal Das |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
19 | East | 211879798 | 29/04/2025 | 250 | F6.8841.../2420114 | Coolant leakage | Open | S. A. Trading | Revenus Industries Pvt. Ltd. - Malda | 846 | SE Found coolant seepage at thermostat outlet hose clamp loose so tighten issue resolved | CLOSED | Prosanjit saha |  |  | 8 | Thermostat | 5 | 4 | 3 | 60 | Low
21 | East | 211877143 | 30/04/2025 | 125.4 | 4H.8042.C4../2420507 | Red lamp alarm issue & black smock issue Call By Customer Name :- Mahesh Kumar Mobile No :- 9911861177 | Open | Mahesh Kumar | K.C. Diesel Services - East Sikkim | 368 |  | OPEN | Prosanjit saha |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
3 | WEST | 211881840 | 30/04/2025 | 125.4 | 4H.8041.../2420541 | Starting Issue Call By Customer Name :- Mahesh .. Mobile No :- 9930262638 | Task Start | VIJAY SALES (INDIA) PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 541 | Error code 1761/16 Adblue level low so top up adblue and clear error code. | Closed | Jagdeep Saini |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
5 | WEST | 211879687 | 29/04/2025 | 125.4 | 4H.8042.C4../2420063 | Starting/Stopping Issue | Closed | Hukumchand Shantikumar Bros. | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 38 | Adblue lvl low so top up adblue | Closed | Jagdeep Saini |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
7 | WEST | 211877956 | 29/04/2025 | 200 | 6H.8435.../2420252 | Voltage Fluctuation | Closed | ISC Projects Pvt Ltd. | Mahalaxmi Diesels - Kolhapur | 104 | no issue with dg . | Closed | Jagdeep Saini |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
9 | WEST | 211872679 | 28/04/2025 | 320 | F6.8802.../2420355 | Load issue Call By Customer Name :- Sanjay No :- 9011008775 | Closed | Kutwal Foods Pvt.Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Choufulla,Daund | 12 | Customer side issue . | Closed | Jagdeep Saini |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
11 | WEST | 211870695 | 27/04/2025 | 40 | 3H.8951.../2421171 | Starting/Stopping Issue | Closed | Scaletek Rapidrise Ventures | Dhanashree Technocrats Pvt. Ltd. - Nasik | 28 | 5838,1- Engine Exhaust Gas Recirculation Valve Malfunction check connection found ok connect ikonnect and clear error code. | Closed | Jagdeep Saini |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
14 | WEST | 211869031 | 27/04/2025 | 30 | 3H.8902.../2421605 | Starting/Stopping Issue | Closed | M. Tech Engineers | Mahalaxmi Diesels - Goa |  | customer side issue . | Closed | Jagdeep Saini |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
15 | WEST | 211868728 | 27/04/2025 | 125.4 | 4H.8042.C4../2420812 | Mil Lamp On Issue Email By - KGD Name - Vishal Raut | Closed | SANJAY PLASTIC | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 40 | Adblue level low so top up adblue . | Closed | Jagdeep Saini |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
16 | WEST | 211884631 | 31/04/2025 | 20 | GP3.1021.../2420106 | INTANCE ID :-100744691 SITE ID :- I-GJ-SDPR-ENB-G001 CALL BY CUSTOMER // DG ISSUE :-CAPECITER NOT WORKING NAME :-Aakash NUMBER :-9016018658 | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 10.1 | Super Capacitor input voltage- 52V & Output voltage- 0V. So it needs to be replaced. | OPEN | Amit Sandlya | Failed part |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
17 | WEST | 211884577 | 31/04/2025 | 20 | GP3.1021.../2420113 | INTANCE ID :-100744687 SITE ID :- I-GJ-PTNN-ENB-G003 CALL BY CUSTOMER // DG ISSUE :- CAPECITER PROBLEM NAME :-Aakash SIR NUMBER :-9016018658 | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 52.1 | Super Capacitor input voltage- 52V & Output voltage- 0V. So it needs to be replaced. | OPEN | Amit Sandlya | Failed part |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
19 | WEST | 211883766 | 31/04/2025 | 160 | 6H.8475.../2420081 | AMBER LAB ALARM ON UNDER SPEED | Task Start | ADHARV CONSTRUCTION | Shree Engineering Service - Satna | 1235 | V belt loose so tightened the same. Commissioning Date:08-08-2024 & Paid CSP:20-02-2025 | Closed | Amit Sandlya | Failed part |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
22 | West | 211894559 | 01/04/2025 | 40 | 3H.8951.../2520226 | DG Issue | Task Start | ATC Telecom Infrastructure Private Limited | Natraj Power Tech - Barwani | 1.7 | DG starting issue due to low fuel level. | Closed | Vijay Patil |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
25 | West | 211893212 | 01/04/2025 | 500 | DV8.9313.../2420038 | Electrical Problems | Task Start | Powercare | Unique Techno Services Pvt Ltd. - Surat | 82 | 40ohms resistance installed in T6 sensor wiring. | OPEN | Amit Sandlya |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
4 | South | 211884702 | 31/04/2025 | 160 | 6H.8475.../2520017 | Starting/Stopping Issue | Closed | KALYAN JEWELLERS.. | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 74.33 | Dg trip with under speed alarm so checked & found Y- phase fuse burn replace the new phase issue resolve. | Closed | Mr. MD Saleem |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211884674 | 31/04/2025 | 200 | 6H.8435.../2420156 | ABNORMAL SOUND CALLBY CUSTOMER NAME- arjun sir NUMBER-8867766482 | Closed | RAMSONS TRENDSQUARES REALTY LLP | Surya Power Services - Bangalore | 45.12 | V- belt loose tighten the Same | Closed | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211884088 | 31/04/2025 | 125.4 | 4H.8041.../2420770 | Genset Trip | Task Start | MKC INFRASTRUCTURE LTD | Johnson Techno Sales & Services - Silchar | 16 | update pending | CLOSED | Ujjwal Das |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211884600 | 31/04/2025 | 20 | GP3.8601.../2421055 | Starting/Stopping Issue | Closed | NX SPORTS LLP | Surya Power Services - Bangalore | 27 | Start relay all wire tighten then start then Start the DG working ok | Closed | Mr. Anil Kumar H G |  |  | 6 | Relay | 5 | 4 | 3 | 60 | Low
2 | East | 211885145 | 31/04/2025 | 30 | 3H.8902.../2420815 | Starting Issue Email By Customer Name:-Abhay Mishra | Open | Dinesh Chandra R. Agrawal Infra Con Pvt. Ltd. | Johnson Techno Sales & Services - Agartala |  | visit pending | OPEN | Prabhakar Kumar |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
40 | North | 211883198 | 31/04/2025 | 15 | GP3.8501.../2421245 | Red Lamp Alarm Call By Customer Name:-Pravin Kumar No:-7082231333 | Task Start | BHARAT GENERAL STORE | Suraj Motor Store - Jammu | 409.81 | Visit Pending ; Remote Area | Open | Ved Prakash Gupta |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211870797 | 27/04/2025 | 20 | GP3.1021.../2420464 | INTANCE ID :-100784736 SITE ID :-I-UE-ABDD-ENB-0930 CALL BY CUSTOMER // DG ISSUE :-UNDER VOLTAGE PROBLEM NAME :-Aaand SIR NUMBER :-7355406531 | Open | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | Visit pending | open | Sudhir Awasthi |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211870352 | 27/04/2025 | 20 | GP3.1021.../2420385 | DG under Voltage alorm in GCU | Open | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | Visit pending | open | Sudhir Awasthi |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211869597 | 27/04/2025 | 125.4 | 4H.8042.C4../2420800 | Starting/Stopping Issue | Closed | PUNIHANI INTERNATIONAL | Vidyut Engineers - Noida | 22 | found DG set tripping After some time B Phase under voltage show Due to B Phase wire thimble removed in MCB After that We Repair the wire then issue resolve | Closed | Kapil Solanki |  |  | 10 | MCB | 5 | 4 | 3 | 60 | Low
9 | North | 211877968 | 29/04/2025 | 160 | 6H.8475.../2420467 | Automation issue Call By Customer Name :- Prabhat Kumar Mobile No :- 9313296404 | Closed | VMC. Fartilizers | Paluck Technologies Ltd. - Ghaziabad | 74 | Start time late so, adjust the timing with the panel after that issue resolve | Closed | Kapil Solanki |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211877592 | 29/04/2025 | 20 | GP3.1021.../2420364 | DG Issue | Open | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - LUCKNOW | 135 | Contactor was replace (Update pending) | open | Sudhir Awasthi |  |  | 9 | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211884003 | 31/04/2025 | 30 | 3H.8902.../2320053 | Starting/Stopping Issue | Open | Shree Organic Chem Industries Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 456 | DG was not start then check and found panel wiring was loose tightness to be all after that issue resolve | Closed | Gourav Sharma |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211883785 | 31/04/2025 | 160 | 6H.8475.../2520010 | Automation issue | Closed | JBX Enterprises LLP | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | Customer side panel timing issue | Closed | Kapil Solanki |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
14 | North | 211883593 | 31/04/2025 | 400 | DV8.8542.C4../2420154 | Power supply Issue Call By Customer Name : Prashant Sir Number : 9310103847 | Task Start | KESHAV INFOCOM PVT. LTD. | Vidyut Engineers - Noida |  | Wrong Report SR - DG running well Customer side panel issue | Closed | Kapil Solanki |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
16 | North | 211883508 | 31/04/2025 | 5.5 | CC1.1013.../2400355 | Leakage Issue | Task Start | SHRI TEJA ENTERPRISES | Pratap Diesels Pvt. Ltd. - BIKANER | 687 | Silencer was open and welding was broken | open | Gourav Sharma | Required photo |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211883357 | 31/04/2025 | 57 | T4.8941.../2420016 | Maintenance due Alaram Issue Call By Customer Name : Rajkumar Number : 9873308474 | Closed | KESHAV GENERATORS PVT LTD | Paluck Technologies Ltd. - Gurgaon | 305 | Maintenance due alarm reset the alarm after that issue resolve | Closed | Kapil Solanki |  |  | 7 | Maintenance | 4 | 3 | 2 | 24 | Low
19 | North | 211883149 | 31/04/2025 | 125.4 | 4H.8041.../2420764 | Tripping Issue Call By Customer Name :Madan . No :9899698568 | Task Start | Jai Mata Kalyani C/o. O/p. Group Housing Society Ltd. | OVN Industries Private Limited - New Delhi | 12 | XDBK1 1C2 wire was loose so tight all connections then started the dg and found running is ok and no leakage found in dg | Closed | Kapil Solanki |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
21 | North | 211883116 | 31/04/2025 | 320 | F6.8802.../2420041 | Starting issue Called by customer NAME ; SUDHIR Number : 8447621198 | Closed | M/S EINS TECHNIK PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 365 | found mcb trip so, supply not come after up the mcb then start the dg then issue resolve | Closed | Kapil Solanki |  |  | 7 | MCB | 5 | 4 | 3 | 60 | Low
23 | North | 211881860 | 30/04/2025 | 160 | 6H.8475.../2420020 | Fan belt broken Call By Customer Name :-Manoj Kumar Mobile No :- 9582943302 | Open | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad |  | Visit pending | open | Kapil Solanki |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
25 | North | 211881543 | 30/04/2025 | 45 | 3H.8951.../2420715 | Supply issue Call by : Customer Name : Srinivasa rav Contact : 9247214381 | Open | Ravi kumar | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
28 | North | 211881113 | 30/04/2025 | 200 | 6H.8435.../2420003 | Abnormal Sound Issue Call by Customer Name : Mohammad Amjad No : 8595636308 | Closed | Uppal-Chadha Hi-Tech Developers Private Limited | Paluck Technologies Ltd. - Ghaziabad | 115 | V-belt was loose so, tightness the same and some rubbing mark | Closed | Kapil Solanki |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
29 | North | 211881112 | 30/04/2025 | 20 | GP3.8601.../2420688 | Power Supply Issue Call By Customer Name - Anshul Sawhney Number - 9818258638 | Open | Mr. Lovkesh Sawhney | Vidyut Engineers - Noida |  | Visit pending | open | Kapil Solanki |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211880516 | 29/04/2025 | 82.5 | 5H.8901.../2420717 | Supply issue Call By customer Name:ANAY TRIPATHI Number :7052852688 | Task Start | SUNRISE ENGINEERS | Vidyut Engineers - Noida |  | Visit pending | open | Kapil Solanki |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211879861 | 29/04/2025 | 125.4 | 4H.8041.../2420197 | Loading Issue Call by customer Name :Lalit Tyagi Number:9810138700 | Closed | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad |  | Wrong Report SR - DG running well | Closed | Kapil Solanki |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
34 | North | 211879596 | 29/04/2025 | 15 | GP3.8501.../2421246 | Starting Issue Call By Service dealer Name :- Harish Ji Mobile No :- 9811482582 | Open | A.K.D.K. JAIN TRADING PVT LTD | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
35 | North | 211879472 | 29/04/2025 | 25 | GP3.8702.../2420031 | Starting Issue Call By Customer Name:-Mr. Mukesh kumar No:-9450017457 | Open | Lucknow City College. | S. R Engines Sales And Service - LUCKNOW |  | Visit pending | open | Sudhir Awasthi |  |  | 8 | Unknown | 1 | 1 | 10 | 10 | Low
39 | North |  | 31/04/2025 | 15 | GP3.8501.../2422153 | Red Alaram Issue Call By Customer Name : Ruban Sir Number : 9896469334 | Task Start | Indian Army | Suraj Moters Stores - Leh | 230.05 | Sweep stuck occurs frequently with engine hunting ; SR opened to replace the FIP | Open | Ved Prakash Gupta |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211885290 | 31/04/2025 | 20 | GP3.8601.../2420013 | Starting Problem Call by : Customer Name :Shamphukumar Contact :8825175551 | Task Start | Mr. Nirmal Jee. | Globalline India Services Private Limited - Aurangabad | 155 | update pending | CLOSED | Prabhakar Kumar |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
97 | North | 211904244 | 04/04/2025 | 500 | DV8.8501.C4../2420222 | starting issue | Task Start | Powercam Electricals Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 5 | SR opened for snychronisation | Closed | Ved Prakash Gupta |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211884436 | 31/04/2025 | 10 | GP3.8301.../2420223 | RED LAMP ALARM CALL BY CUSTOMER NAME-RAJESH SIR . NUMBER-9448405078 | Closed | Prabhavati Desai | KALA Care Global LLP - Ballari | 24 | Emergency switch activated re-correction the wire after checked engine running condition is ok.. | Closed | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
11 | South | 211884299 | 31/04/2025 | 20 | GP3.8601.../2421375 | Starting/Stopping Issue | Closed | Bangalore Generator | Surya Power Services - Kalyan Nagar | 51 | Maintenance due alarm is reset . | Closed | Mr. Anil Kumar H G |  |  | 6 | Maintenance | 4 | 3 | 2 | 24 | Low
25 | North | 211898995 | 02/04/2025 | 200 | 6H.8435.../2420065 | Automation Issue Call By Customer Name : Singh Number : 9784326968 | Open | Leadengage LLP | Rajdhani Diesels and Electricals - Jodhpur | 123 | Customer side panel issue so same educate the customer kindly check your panel | Closed | Gourav sharma |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
30 | North | 211898851 | 02/04/2025 | 58.5 | T4.8941.../2421947 | White Smoke Issue Call By Customer Name :-Pawan Kumar Mobile No :- 9811458226 | Task Start | INDER GENERATOR HOUSE.. | Vidyut Engineers - New Delhi | 373 | Blow by on the DG, Dealer arrange the blow by meter | open | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
37 | North | 211898501 | 02/04/2025 | 40 | 3H.8951.../2320076 | Excessive Smoke | Completed | PANDA INTERNATIONAL PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 546 | Found Engine was overheat and Radiator was chocked and Air filter was chocked So, replace the same after that issue resolve | Closed | Kapil Solanki |  |  | 4 | Air Filter | 4 | 4 | 3 | 48 | Low
68 | East | 211893109 | 01/04/2025 | 125.4 | 4H.8042.C4../2420942 | Door lock issue Call By Customer Name :- Prabhat Kumar Mobile No :- 7362000070 | Closed | Care Aastik | Globalline India Services Private Limited - Aurangabad | 15 | Adjusted the DG lock catcher issue resolved | CLOSED | Prabhakar Kumar |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211898171 | 02/04/2025 | 20 | GP3.8601.../2420798 | Starting Issue Call By Customer Name :-Avdesh Yadav Mobile No:-7905246982 | Open | HARI BANDHU TRUST | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
51 | North | 211894258 | 01/04/2025 | 40 | 3H.8951.../2420431 | starting problem Email By -Customer Name:-Manuj Jain | Task Start | Arihant Machinery Store | Vidyut Engineers - Noida | 262 | Maintenance due alarm, reset the alarm after that issue resolve | Closed | Kapil Solanki |  |  | 5 | Maintenance | 4 | 3 | 2 | 24 | Low
54 | North | 211901695 | 03/04/2025 | 160 | 6H.8475.../2520010 | Automation Issue Call By Customer Name:- Mansih Sir Mobile No:-9162533044 | Open | JBX Enterprises LLP | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 9 | Customer side panel issue so same educate the customer kindly check your panel | Closed | Kapil Solanki |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
60 | North | 211901134 | 03/04/2025 | 500 | DV8.8501.C4../2420020 | Emergency stop alarm issue Call By Customer Name :- Ajay Kumar Number :- 9958214785 | Task Start | ESQUIRE TECH.. | Vidyut Engineers - New Delhi | 98 | DG showing the Emergency alarm, check the wiring tightness to be all after that and check Element found ok (Under obsevation) | Monitoring | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
65 | North | 211900918 | 03/04/2025 | 200 | 6H.8435.../2420169 | Abnormal Sound issue Call By Customer Name:-Raj No:-9625182534 | Task Start | Macro Auto Tech. | Paluck Technologies Ltd. - Faridabad | 60 | Fan belt loose tightness the belt after that issue resolve | Closed | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
66 | North | 211900226 | 02/04/2025 | 750 | DV2.8501.C4../2420018 | Door Lock Issue Email By OEM Name:-Rakesh Kumar | Task Start | MEDICAL SUPRINTENDENT | OVN Industries Private Limited - New Delhi | 44 | Door lock not working properly then replace the door lock after that issue resolve | Closed | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
68 | North | 211900078 | 02/04/2025 | 58.5 | T4.8941.../2422886 | Starting issue Call By Customer Name:- Sarlabh Agarwal No:- 9756139069 | Closed | Praveen Kumar HUF | Deep Jyoti Electricals and Services - Moradabad | 15 | Found Relay 2A1 Wire loose in the panel tightness the same after that issue resolve | Closed | Sudhir Awasthi |  |  | 4 | Relay | 5 | 4 | 3 | 60 | Low
71 | North | 211904644 | 04/04/2025 | 20 | GP3.8601.../2420170 | Automation Issue Call By Customer Name :-Devendra Singh Mobile No:-9810938926 | Task Start | Devendra Singh Sodi | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 20 | Under speed alarm after reset the alarm then issue resolve found no any issue | Closed | Kapil Solanki |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
74 | North | 211904269 | 04/04/2025 | 82.5 | 5H.8901.../2320024 | Starting Issue Call by customer Name :harshwardhan Number :8700373053 | Task Start | FLY BY NIGHT | Paluck Technologies Ltd. - Faridabad | 422 | Emergency alarm, when check the panel emergency wiring was loose due to which the engine was shutting down due to emergency wiring tightened and tight with belt after started the DG running well | Closed | Kapil Solanki |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
79 | North | 211904113 | 04/04/2025 | 30 | 3H.8902.../2320145 | Electrical Problems | Open | NAVJYOTI INDIA FOUNDATION | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
82 | North | 211903337 | 03/04/2025 | 15 | GP3.8501.../2421057 | Starting/Stopping Issue | Closed | KANSAI NEROLAC PAINTS LIMITED | S. R Engines Sales And Service - Gorakhpur | 375 | Main MCB was trip because in the changeover wire was shot correct the same after that issue resolve | Closed | Sudhir Awasthi |  |  | 3 | MCB | 5 | 4 | 3 | 60 | Low
86 | North | 211904149 | 04/04/2025 | 250 | DV8.9840.../2420017 | Abnormal Sound Issue Call By Customer Name Amit yadav Mobile No:Ramesh Yadav | Closed | Sri Krishna Polymer Industries Pvt. Ltd | Vidyut Engineers - Noida | 22 | Gas Engine- Error code show reset required so, today visit again | Open | Kapil Solanki |  |  | 3 | Unknown | 1 | 1 | 10 | 10 | Low
87 | North | 211905209 | 04/04/2025 | 30 | 3H.8902.../2421184 | starting issue call by customer name : Shankar Jha number : 7210338609 | Task Start | KEYLANCE | Vidyut Engineers - Noida | 10 | Emergency switch was pressed condition so realeased the same after that issue resolve | Closed | Kapil Solanki |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
88 | North | 211899655 | 02/04/2025 | 20 | GP3.8601.../2320046 | Low Speed Alam Call By Customer Name : DEEPAK UMMAT Number : 9953160591 | Closed | D. V. Water Harvesters Company | Vidyut Engineers - Noida | 181 | Found in panel Fues was faulty so, change the fues then issue resolve | Closed | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
89 | North | 211900974 | 03/04/2025 | 125.4 | 4H.8041.../2420125 | Leakage Issue | Task Start | ATTIC PRODUCTS PRIVATE LIMITED | Vidyut Engineers - Noida | 146 | 2nos breather pipe hose was damage so, replace with clamp after that issue resolve | Closed | Kapil Solanki |  |  | 4 | Unknown | 1 | 1 | 10 | 10 | Low
92 | North | 211905803 | 04/04/2025 | 125.4 | 4H.8041.../2420151 | Oil Leakage issue Call By Customer Name:-Sandeep No:-9729205181 | Task Start | SHRI SHAKTI ENTERPRISES | SAAN Royal Power Solutions Private Limited - Sonipat | 592.46 | Oil leakage found from rocker cover ; tightened the bolts of same ; gasket need to replace | Closed | Ved Prakash Gupta |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
95 | North | 211905157 | 04/04/2025 | 15 | GP3.8501.../2421347 | Starting/Stopping Issue | Closed | VICTOR POWER SOLUTION | SAAN Royal Power Solutions Private Limited - Rohtak | 352 | High Fuel level alarm occurred due to fuel top-up more than specified ; same communicated to customer | Closed | Ved Prakash Gupta |  |  | 2 | Unknown | 1 | 1 | 10 | 10 | Low
21 | North | 211893216 | 01/04/2025 | 500 | DV8.9313.../2420040 | Electrical Problems | Open | Powercare | R K Engineers - Muzaffarnagar |  | Visit pending | open | Sudhir Awasthi |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211884362 | 31/04/2025 | 15 | GP3.8501.../2421371 | Starting Problem Call by : Customer Name :Surya Contact : 9538367009 | Closed | Shobha Rani K | Surya Power Services - Kalyan Nagar | 73 | Engine not starting in automode due to sensing wire loose issue,then removed the sensing cable & refitted properly & started the engine found running condition is normal. | Closed | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
19 | North | 211893253 | 01/04/2025 | 57 | T4.8941.../2320001 | fan Belt Brocken issue Call By Customer Name :- Sachin Mobile No :- 8440878184 | Closed | Shivoham Hospital & Trauma Centre | Pratap Diesels Pvt. Ltd. - Bhiwadi | 544 | Fan belt broken so change the belt after that issue resolve | Closed | Gourav sharma |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
16 | North | 211893686 | 01/04/2025 | 82.5 | 5H.8901.../2420598 | Automation Issue Call By Customer Name : Raghav Number : 9867210241 | Task Start | BLV Healthcare Pvt Ltd | Pratap Diesels Pvt. Ltd. - Bhiwadi | 29 | Auto connection not done so, connect the Auto wire after that issue resolve | Closed | Gourav sharma |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
12 | South | 211884049 | 31/04/2025 | 82.5 | 5H.8901.../2420118 | Starting Problem Call by : Customer Name :Venkatesh Contact :7736551844 | Closed | GENLITE ENGINEERING PVT LTD | Madurai Electro Controls - Tenkasi | 116 | Visited the site checked the engine is running condition is found ok. ATS control panel problem. Its not comes under KOEL scope other make. | Closed | Mr. NandhaGopal |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
13 | South | 211884042 | 31/04/2025 | 125 | 4H.8052.C4../2520063 | Starting Issue Call By Customer Name :- RADHA SRINIVAS Mobile No :- 9148094989 | Task Start | B RADHA SRINIVAS | Prasad Power Engineers - Tumkur | 77 | Airlock issue due to low fuel level | Task Start | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
15 | South | 211883692 | 31/04/2025 | 82.5 | 5H.8901.../2420462 | AMF Panel Problem Call by : Customer Name :Mohan Contact :8754458988 | Closed | NM Hotels | Bharath Diesel Sales and Service - Salem | 32.56 | Customer side EB Sequence issue. CONTACT THE E.B PERSON TO RECTIFY THE ISSUE FOR PROPER AUTO RUN | Closed | Mr. NandhaGopal |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
18 | South | 211883544 | 31/04/2025 | 125.4 | 4H.8042.C4../2520073 | Emergency stop alarm | Closed | Raisha Technodesign Pvt. Ltd. | Ultimate Power Source - Hosur | 16 | Emergency Alarm checked & found wire loose so retighten the same | Closed | Mr. NandhaGopal |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
20 | South | 211883431 | 31/04/2025 | 15 | GP3.8501.../2421997 | Umber lamp Alaram Issue Call By Customer Name : PRAVEEN PATIL Number : 9481739531 | Closed | Mr. PRAVEEN PATIL | KALA Care Global LLP - Belagavi | 2 | 2802/4, 2791/14 error code so checked & found panel side wire loose. Need to take proper update | Closed | Mr. Anil Kumar H G |  |  | 7 | Unknown | 1 | 1 | 10 | 10 | Low
21 | South | 211893755 | 01/04/2025 | 125.4 | 4H.8042.C4../2420837 | Starting/Stopping Issue | Task Start | MODERN MATCHES PRIVATE LIMITED | Madurai Electro Controls - Virudhunagar | 34 | DG panel door not closed, remove the door lock and clip check and refitting, door lock problem this ok, engine running found ok. | Task Start | Mr. NandhaGopal |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
22 | South | 211893698 | 01/04/2025 | 30 | 3H.8902.../2421241 | Automation Issue Call By Customer Name : pradeep .. Number : 9663793637 | Open | PRADEEP K N | Surya Power Services - Kushalanagara |  | Visit pending | Open | Mr. Anil Kumar H G |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
25 | South | 211893604 | 01/04/2025 | 20 | GP3.8601.../2421471 | Tripping issue Call by Customer Name - Sanjeev Matade Number - 7411434402 | Task Start | Sanjeev R Matade | KALA Care Global LLP - Hubli |  | visit today since customer given appointment today | Task Start | Mr. Anil Kumar H G |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
29 | South | 211893400 | 01/04/2025 | 40 | 3H.8951.../2420091 | Call by : Customer Name : Satyanarayana Contact : 8861686363 | Open | Prashinitha Rao Eraballi | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | Visit pending | Open | Mr. MD Saleem |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low
30 | South | 211893161 | 01/04/2025 | 82.5 | 5H.8901.../2420806 | VOC - Tripping problem Customer Name -Dharani Customer Number-9611420663 Mode- SR Generated through CDI calling. | Open | Metal Work Pneumatic India Pvt Ltd | Surya Power Services - Peenya, Bangalore |  | Visit pending | Open | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
32 | South | 211893114 | 01/04/2025 | 25 | GP3.8702.../2421440 | servicing | Open | Vanita Petrol Park | KALA Care Global LLP - Vijayapura |  | Visit pending | Open | Mr. Anil Kumar H G |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
34 | South | 211893103 | 01/04/2025 | 25 | GP3.8702.../2420507 | DG not starting,DG not working -524247 | Task Start | ICICI Bank Limited | Electro Controls - Thiruvananthapuram |  | Visit pending | Open | Mr. Sanjaimon S |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
36 | South | 211893015 | 01/04/2025 | 62.5 | T4.8941.../2420646 | Battery Replacement Issue. Call By Customer. Name:-Sheela Mobile No.:- 9962972727 | Open | Shilpa Architects | Bharath Diesel Sales and Service - Ashoknagar |  | Visit pending | Open | Mr. NandhaGopal |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
38 | South | 211892946 | 01/04/2025 | 15 | GP3.8501.../2420493 | Starting Issue Call By Customer Name - seetharaman Number - 8925134916 | Task Start | Sai Enterprises, | Madhu Engineering Sales & Service - Teynampet,Chennai | 15 | Engine emergency button is press condition,so dg is not starting then release the emergency button,now no issues. Educate the customer. | Closed | Mr. NandhaGopal |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
40 | South | 211892899 | 01/04/2025 | 25 | GP3.8702.../2420268 | Power Supply Problem Call by : Customer Name :Senthilkumar Contact :9003869127 | Closed | Sd Infra Private Limited. | Bharath Diesel Sales and Service - Tiruchirappalli | 97 | Check the DG set output voltage is good R phase 238, Y phase 238, B phase 238, but control panel side neutral link connector side wire ferol number (NG) problem, so output voltage is not a proper, than cleaning the neutral link connector, than connected the wire ferol number (NG), than check the DG set working on good | Closed | Mr. NandhaGopal |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211869573 | 27/04/2025 | 500 | DV8.8501.C4../2420055 | Starting issue Called by Customer Name:Anuj Number :8930203483 | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 41 | DG running fine customer Mains side issue after check mains wire not connected | Closed | Kapil Solanki |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211869497 | 27/04/2025 | 500 | DV8.8501.C4../2420013 | Automation Issue call by customer name : Fahim number :9084764335 | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 49 | Found issue in amf panel wiring not connected | Closed | Kapil Solanki |  |  | 10 | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211893999 | 01/04/2025 | 58.5 | T4.8941.../2520476 | relay card issue | Completed | AARYAN VENTURA PVT LTD | OVN Industries Private Limited - New Delhi | LR | Relay card faulty Output supply not Given so, replace the same after that issue resolve | Closed | Kapil Solanki |  |  | 5 | Relay | 5 | 4 | 3 | 60 | Low
8 | North | 211893584 | 01/04/2025 | 125.4 | 4H.8041.../2320198 | Error Code Issue Call By Customer Name : Abdul Kasim Khan Number : 9582438101 | Task Start | BKDJ Packagings Pvt. LTD | Paluck Technologies Ltd. - Gurgaon | 500 | Maintenance due alarm reset the alarm | Closed | Kapil Solanki |  |  | 5 | Maintenance | 4 | 3 | 2 | 24 | Low
9 | North | 211885530 | 31/04/2025 | 160 | 6H.8475.../2420095 | Abnormal Sound Issue Call By Customer Name : Narendra Shah Number : 9824312486 | Closed | Shree Dwarikadhish Temple | Espiem Engines & Machines (P) Limited - Agra | 32 | V-belt loose tightness the same after that issue resolve | Closed | Sudhir Awasthi |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211886085 | 31/04/2025 | 125.4 | 4H.8041.../2420865 | Flickering | Closed | BALAR MARKETING PRIVATE LIMITED | Vidyut Engineers - Noida | 50 | Customer panel side issue supply not passing from the panel DG running ok | Closed | Kapil Solanki |  |  | 6 | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211893285 | 01/04/2025 | 57 | T4.8941.../2420083 | Starting/Stopping Issue | Task Start | JEET CONSTRUCTION | R K Engineers - Meerut | 72 | Found MCB off condition MCB on engine all parameter check engine on load running ok | Closed | Sudhir Awasthi |  |  | 6 | MCB | 5 | 4 | 3 | 60 | Low
38 | North | 211898337 | 02/04/2025 | 125.4 | 4H.8041.../2420221 | Oil leakage issue Call by customer Name:Sandip Number:9149824056 | Task Close | MUKESH RANJAN CONTRACTORS | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1764 | Found oil leakage from sump, so replace the sump after that issue resolve | Ompraksh | Kapil Solanki |  |  | 5 | Unknown | 1 | 1 | 10 | 10 | Low