## SPN
SR.No. | Zone | Incident no | Creation Date | KVA | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Run hours | Observation | Incident Status | ASM Name | HO remark | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Component | Severity (S) | Occurrence (O) | Detection (D) | RPN | Priority
12 | South | 211642000 | 25/01/2025 | 40 | 3H.8951.../2421079 | ErrorCode Problem Call by : Customer Name :Dhinesh Kumar Contact :9442651353 | Closed | PKP Educational Trust | Electro Controls - Erode | 7 | VISITED THE SITE FOUND ERROR CODE DISPLAYED SPN 5838 FMI-1,SPN 2791 FMI 18, SO flash the ECU after checking parameters | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
17 | North | 211711886 | 13/02/2025 |  | GP3.8501.../2520007 | Fuel Rack Position Short | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | LR-1.2 | Found error code show SPN/FMI 1210/4 then check 2&3pin connector continuity found in D1 wire not get the Continuity then change the new wiring harness then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
14 | East | 211733381 | 19/02/2025 | 125.4 | 4H.8042.C4../2420006 | Starting/Stopping Issue | Task Start | KALYAN JEWELLERS INDIA LTD | K.C. Diesel Services - SILIGURI | 385 | SE found code (SPN-516166 FMI -0) ,(SPN-1761FMI-16) after that top up the DEF level and clear the code Issue resolved | CLOSED | Prosanjit saha | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
98 | South | 211692075 | 07/02/2025 | 200 | 6H.8435.../2420081 | Starting/Stopping Issue | Open | Nanki Automotives & Enterprises Pvt Ltd. | KALA Care Global LLP - Hubli | 80 | As per the customer's complaint, we are attending the site and observed the dg error code SPN 516166 FMI 0 We connected the tool and cleared the error code and top-up the AdBlue and top-up the coolant and then started the dg running is ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
89 | South | 211690416 | 06/02/2025 | 30 | 3H.8902.../2422181 | EGR Valve Malfunction error | Closed | S.ARORA | Electro Controls-Tirupur | 5 | visited the site inspected the engine check the problem EGR malfunctioning spn2791/1, 5838/1.AS per koel advice We have created one 30kva.EGR_Dummy SR in ikonnect then we flash and cleared the fault. Started the lested found ok | Closed | Mr. Sanjaimon S | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
88 | South | 211690465 | 06/02/2025 | 82.5 | 5H.8901.../2420591 | Error showing in controller | Closed | Rudhra Dental Clinic | Bharath Diesel Sales and Service - Salem | 27 | FOUND SPN 6595 ,FMI 0.,ERROR SHOWN IN CONTROLLER. ERROR CODE CLEARED WITH IKONNECT. CHECKED THE D.G ON/OFF AND WORKING FINE.ALSO CHECKED THE NOX SENSOR AND TEMPERATURE SENSOR LOOSEN. IT HAS BEEN TIGHTEN. | Closed | Mr. NandhaGopal | [9 empty] | NOx Sensor | 9 | 7 | 6 | 378 | High
74 | South | 211694038 | 07/02/2025 | 125.4 | 4H.8042.C4../2420468 | high temperature Alarm Issue Call By Customer Name:Mehaboob .. No :9746143389 | Closed | ORANGALLA PARAMBAN SHAJI | G-Care Diesels Private Limited - Malappuram | 42 | Engine high clnt temp fit alarm showing and shutdown issue SPN:110 FMI:16 and ecu flashing it found ok kept under observation for 2day engine working found ok check engine oil level radiator coolant level battery water level radiator air filter clean and refttted v belt tension correct check fuel hose radiator hose adblue level engine wiring panel wiring engine working found ok | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
70 | South | 211695306 | 08/02/2025 | 58.5 | T4.8941.../2423081 | Starting/Stopping Issue | Closed | Acecret Adhesions India Private Limited | Prasad Power Engineers - Mangalore | 332 | Engine not starting due to spn 2791,FMI 18,6 so clear the alam ,ecu calibration done and all so oil level is low so done thae oil service now DG running properly and all the parameters are found ok | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
57 | South | 211698410 | 09/02/2025 | 125.4 | 4H.8041.../2420261 | Engine not starting-Error code problem | Closed | Selvakumar | Bharath Diesel Sales and Service - Karaikal | 18 | Check the engine side fully.also checked the wiring found ok but engine not starting.because many error code SPN 51,3229,653,3029 found.so flashing the ECU and reprogrammed.After Flashed engine starting normally.engine performance is normal.checked the dg with load condition safety unit working normally. | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
50 | South | 211699331 | 10/02/2025 | 250 | F6.8841.../2420106 | Error Code Issue Call By Customer Name :- Abhishek .. Mobile No :-9164239659 | Closed | Sanoh India Private Limited | Surya Power Services - Bommasandra, Bangalore | 45 | Visit the site check the engine not starting due to spn 3364 FMI 8 clear the code and ecu flashing as done and check running found ok check the all parameters working engine running found ok | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
30 | South | 211706047 | 11/02/2025 | 30 | 3H.8902.../2420062 | Starting Issue Call By Customer Name - Ashok . Number - 7795509438 | Closed | Classic Associates | KALA Care Global LLP - Hubli | 25 | As per the customer's complete, we visited the site to observe the DG; it then did not start and then checked the alarm and the SPN 97 and FMI 5 and then checked the fuel water in the fuel sensor removed the connection and then cleared the sensor and corrected the communication pins reconnected the sensor and then cleared the alarm and then start the engine working good. | Closed | Mr. Anil Kumar H G | [9 empty] | Fuel Sensor | 7 | 6 | 5 | 210 | High
25 | South | 211707792 | 11/02/2025 | 10 | GP3.8301.../2420458 | engine not starting | Task Start | SUTARIA AUTO CENTRE | KALA Care Global LLP - Hubli | LR | As per we are cc sr attend the site then we are started the dg is not started because of error code showing in display. Then we are check the error code is SPN 110 AND FMI 0 and SPN 100 FMI 1 AND SPN 158 FMI 0 and SPN 190 FMI 1 and SPN 96 FMI 4 And then we are check the error code related sensor and wiring found is ok, then connect the 645C controller cable and programming the controller, and then start the dg running good | Task Start | Mr. Anil Kumar H G | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
13 | South | 211709720 | 12/02/2025 | 20 | GP3.8601.../2421385 | Starting/Stopping Issue | Closed | CHANGALEERI FUELS | Electro Controls - Palakkad | 55 | Found starting problem due to Amber lamp- on, dm1 error spn2791 FMI 5 clear the alrm,but NCD and hooter on while starting ,then checked ecu program check the ecu wiring after , checking and trail running , engine starting performance found satisfaction | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
6 | East | 211702192 | 10/02/2025 | 30 | 3H.8902.../2422420 | Abnormal Sound Issue. Call By Customer. Name:-Parshant Byanth Mobile No.:-7551878476 | Open | Presidency Infracon LLP. | HACS Engineering and Tech Private Limited - Ranchi | 120 | SPN: 5838,FMI: 1, SPN: 2791,FMI: 31 fault code showing so SE check for EGR voltage continuity found OK so removed and Check EGR found clogging so cleaned and refitted issue then clear fault code issue resolved SE also recommended to operate DG above 30% load | OPEN | Prabhakar Kumar | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
19 | North | 211746698 | 22/02/2025 | 58.5 | T4.8941.../2423190 | Starting Issue Call By Customer Name :- Sandip morya Mobile No:-8459683275 | Task Start | The Samrat Palace | S. R Engines Sales And Service - Gorakhpur | 42 | SPN/FMI 2791/18, 5838/1 Flash the ECU after that issue resolve | Closed | Sudhir Awasthi | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
28 | North | 211704623 | 11/02/2025 | 200 | 6H.8435.../2420243 | Alarm Issue Call By Customer Name - SHIVRAJ ... Number - 8869907969 | Closed | Sri Chaitanya Seva Trust | Espiem Engines & Machines (P) Limited - Agra | 101 | Found low def level SPN/FMI 1761/16 , 5462/18 after that fill the DEF then clear the fault code then issue resolve | Closed | Sudhir Awasthi | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
10 | East | 211699675 | 10/02/2025 | 10 | GP3.8301.../2420135 | Low Voltage Alarm Issue Call By Customer Name :- KHEKTO . Mobile No :- 9863164425 | Open | Catsm | Hibreed Engineering Pvt. Ltd. - Jorhat | 2 | SPN: 2802,FMI: 4, SE checked and found F3 fuse(wire 2A - M2) which is used in ECU +ve supply wire was defective after replacing issue resolved. | CLOSED | Ujjwal Das | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
11 | West | 211713499 | 13/02/2025 | 40 | 3H.8951.../2421352 | Red Lamp On Alarm Issue Call By Customer Name :-Ujjal Bajaj Mobile No :-8879171661 | Closed | Mr.Ujjal Bajaj | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 32 | spn 2719/18 EGR issue showed so that all properly wires checked in voltage and continuity no issues in wiring connect ikonnect and clear error code. Calibrated the ECU. | Closed | Jagdeep saini | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
7 | South | 211713100 | 13/02/2025 | 0 | F6.8802.../2420306 | ECU MALFUNTIONING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the dg noticed the alarm for ecu malfunction, check the I connect DTC spn 4363 fmi 3 error display clear the error not done, after change the other ecu error not display | Task Start | Mr. NandhaGopal | Check ECU | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
9 | East | 211720900 | 15/02/2025 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, also found low DEF level alarm so top up and tighten all connection of control panel after that cleared code cleared issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
13 | West | 211707558 |  | 40 | 3H.8951.../2421757 | AUTO START ISSUE | Closed | Gaikwad Develoipers | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 3 | spn 2719/18 EGR issue showed so that all properly wires checked in voltage and continuity no issues in wiring connect ikonnect and clear error code but still error code showing so flash the ecu. | Closed | Jagdeep saini | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
45 | North | 211717969 | 14/02/2025 | 15 | GP3.8501.../2420719 | Starting/Stopping Issue | Closed | Dela Chemical. | Industrial Power Solutions - LUDHIANA | 24 | SPN/FMI-2802/3, with Under speed alarm,Battery Voltage found ok,check the charging alternator & self-starter connection , found ok,reset the code & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
1 | West | 211732917 | 19/02/2025 | 25 | GP3.8702.../2421817 | Error code issue | Task Start | Jai Ashapura Container Terminals | Unique Techno Services Pvt Ltd. - Gandhidham | 12 | The customer complained that there was a problem in starting the genset in auto mode due to the error code. SPN/FMI- 7026/5(Meetering Unint) in controller & 7026/3 in iKonnect app. Tightened the 2A4(Fuel pump wire) on distribution block 2. Checked the Voltage on IMV- between both pins of IMV:10V, Between IMV 2A4 wire pin with respect to ground:13V and between 88 wire pin with respect to ground: 3V. Checked and refited the Engine and panel connector. And started the DG in manual & Auto mode, running OK. | Closed | Amit sandlya | [9 empty] | Fuel Pump | 8 | 6 | 5 | 240 | High
41 | North | 211720379 | 15/02/2025 | 40 | 3H.8951.../2421168 | error code problem | Closed | ICICI Bank Limited | SAAN Royal Power Solutions Private Limited - Zirakpur | 29 | SPN/FMI-2791/5 ,Related to EGR,Open the EGR Valve & found it jammed so clean the same by Diesel & re-fitted the same,DG running fine after clear code | Closed | Ved Prakash Gupta | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
38 | North | 211722528 | 16/02/2025 | 500 | DV8.8501.C4../2320026 | Genset locked out issue Call by Customer Name: Javed Number:7006686329 | Task Start | M/s. Mas Agro Fresh | Suraj Motor Store - Srinagar | 285 | SPN/FMI-1761/15 ; DEF Coupler found loose on site so re-connected the same & same educated to customer. | Closed | Ved Prakash Gupta | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
20 | NORTH | 211727071 | 17/02/2025 | 58.5 | T4.8941.../2423190 | AMF pannel istallation Call By Customer Name :- Sandip morya Mobile No:-8459683275 | Closed | The Samrat Palace | S. R Engines Sales And Service - Gorakhpur | 37 | SPN/FMI 5838/1 remove the EGR connector then again refitted issue resolve after clear the code | Closed | Sudhir Awasthi | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
14 | NORTH | 211728633 | 18/02/2025 | 500 | DV8.8501.C4../2320061 | Throthle body to be change | Closed | Goodworth Electronics Private Limited | Vidyut Engineers - Noida | 99 | Found SPN/FMI 3465/1 , 1761/15, 523584/15, 516166/0 clear the DTC but repeat a code 3465/1 after replace the throttle valve then issue resolve | Closed | Kapil Solanki | [9 empty] | Throttle Valve | 8 | 6 | 5 | 240 | High
2 | West | 211732676 | 19/02/2025 | 58.5 | T4.8941.../2423223 | Leakage Issue | Task Start | Mr. Mahindara | Unique Techno Services Pvt Ltd. - Baroda | 8 | SPN/FMI-2791/18,2791/01,5838/01 Flashed the ECU. This DG is mounted on vehicale. No any fuel leakage from fuel tank. | Closed | Amit sandlya | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
27 | South | 211720088 | 15/02/2025 | 320 | F6.8802.../2420228 | Error will come | Closed | SABARI WOOD AND PLYWOODS | Bharath Diesel Sales and Service - Karur | 13 | Visited the customer site checked the engine starting problem due to error code showing in controller SPN: 516166 /0ECU Internal fault so connected the I Konnect tool and clear the problem code , oil level checked ok fan belt tension checked ok radiator coolant level checked ok started the engine check with load found Running condition normal | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
7 | West | 211724872 | 17/02/2025 | 40 | 3H.8951.../2421166 | MIL lamp alarm Issue Call By Customer Name :- Mohammad anas patel Mobile No :-9770123628 | Open | Patel Poultry farm | Natraj Power Tech - Ratlam | 9.9 | SPN/FMI- 2791/1,5 & 5838/1 & 2802/3 Engineer visited on site without iKonnect tool. Checked the wiring continuity & cross continuity from ECU to EGR valve connectyor found OK. Load on DG- 5%. Today engineer will visit again. | Closed | Vijay patil | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
3 | NORTH | 211724189 | 17/02/2025 | 250 | F6.8841.../2320008 | Starting Issue Call By Customer Name :- Sughar Mobile No :- 8076601980 | Task Start | Charu Apparel Manufacturing Company Private Limited | Vidyut Engineers - Noida | 63 | Low def level alarm SPN/FMI 1761/16 | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
11 | West | 211726868 | 17/02/2025 | 30 | 3H.8902.../2422017 | CC SR | Task Start | Reliable Motors | Unique Techno Services Pvt Ltd. - Ankleshwar | CSP | SPN/FMI- 2791/18- Calibrated the ECU with Dummy file. Opend the ECU connector and found that 73(1 Injector pin) bent and wiring ECU connector pin was backed out from its position. | Closed | Amit sandlya | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
6 | North | 211733834 | 19/02/2025 | 82.5 | 5H.8901.../2420458 | Starting/Stopping Issue | Task Start | Mastersmith | Deep Jyoti Electricals and Services - Moradabad | 25 | Found SPN/FMI 516166/0, & DEF level low | Closed | Sudhir Awasthi | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
34 | North | 211732786 | 19/02/2025 | 35 | 3H.8902.../2422394 | Starting/Stopping Issue | Closed | Axis Bank Ltd | Suraj Motor Store - Srinagar | 19 | SPN/FMI-5838/1,2791/1 ;Related to EGR;found choked the same so clean the valve & re-fitted,DG running under load most of the time,same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
36 | North | 211732607 | 19/02/2025 | 125.4 | 4H.8042.C4../2420719 | Alarm issue | Closed | VIRENDER | SAAN Royal Power Solutions Private Limited - Sonipat | 47.8 | SPN/FMI-516166/0 ; ECU flt error,re-fit the ECU connector & remove the code;issue resolved | Closed | Ved Prakash Gupta | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
13 | South | 211712671 | 13/02/2025 | 160 | 6H.8475.../2420418 | High coolant temperature | Closed | KVR AUTO CARS PVT LTD | G-Care Diesels Private Limited - Kannur | 1483 | High coolant temperature flt+Abnormal sound, corrected the error code in ecu (SPN:110 FMI=0 )Customer complaining about abnormal sound issues, as per customer request site visited and found that fan belt is in loosen condition ,and current hmr is 148hours,so discussed the same matter with ASM Sanjaimon.s and as per his instructions fan belt tightened | Closed | Mr. Sanjaimon S | KRM Check | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
38 | North | 211742376 | 21/02/2025 | 40 | 3H.8951.../2320109 | tarting Issue Call By Customer Name :- Satish Kumar Mobile No :- 8803349159 | Task Start | Jammu Kashmir Cricket Association | Suraj Motor Store - Jammu | 23 | SPN/FMI-637/2 Clean the crank sensor & remove the code,run the DG,Issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Crank Sensor | 8 | 7 | 6 | 336 | High
2 | West | 211716720 | 14/02/2025 | 50 | T4.8941.../2423324 | ENGINE NOT STARTING | Task Start | Bharti Airtel Limited | Shree Engineering Service - Satna | LR | The SPN/FMI code 97/5 was displayed. Upon inspection, it was found that a wire in the engine controlle panel connector had become dislodged. This was corrected. Subsequently, a test was performed to address the engine WIF sensor error. While the original error was resolved, a communication error with the controller is now being reported. Checked the resistance and found 0ohm. No any parameters was showing in controller related to DEF. | OPEN | Vijay Patil | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
1 | East | 211704805 | 11/02/2025 | 30 | 3H.8902.../2420408 | Starting/Stopping Issue | Task Start | Shine Enterprise | Green Powerline - Dhemaji | 1031 | SPN 520528FMI 31, SPN 105 FMI 3, SP 5838 FMI 3/2/1 SPN 2791 FMI 1/31 were present in DTC so as per fault code description SE checked for the the EGR valve found jammed so replaced the EGR valve. | CLOSED | Ujjwal Das | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
13 | North | 211754970 | 25/02/2025 | 750 | DV2.8501.C4../2420098 | Mall Facing Alarm And Display Issue And Red Lamp On Alarm Call By Customer Name :- Devendra Singh Mobile No :-9891950132 | Task Start | Vodafone Idea Limited | Vidyut Engineers - New Delhi | 9 | SPN/FMI 4358/21, 523576/0 Check the complete def line found all ok but found return line to Def tank found blockage after clean the def line with hot water then trial on load near 1 hour found no issue | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
15 | WEST | 211757700 | 26/02/2025 | 125.4 | 4H.8042.C4../2420152 | Tripping Issue Call By Customer Name :- Krishna Yadav Mobile No :- 8999245339 | Task Start | PSOVL RAILONE PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Surat | 163 | SPN/FMI- 6595,0(Malfuntioning of Supply Module & Dosing Module) Checked the DEF line, dosing module & supply module. Nox sensor connector fitted again. Cleared the DTC. Under Observation. | Closed | Amit sandlya | [9 empty] | NOx Sensor | 9 | 7 | 6 | 378 | High
4 | East | 211757986 | 26/02/2025 | 82.5 | 5H.8901.../2420159 | Fuel Leakage Issue Email By KGD Name -Power Generators | Task Start | Radheshyam Tea Industries | Almas Engineers - Sivsagar | 49 | SPN 6595 FMI 0 additional dosing chk error , and SPN 516166 ECU flt pop on display so SE disconnected the dosing module and supply module connector and refitted properly then cleared code and tested for 2 3 time no fault code popup | CLOSED | Ujjwal Das | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
9 | East | 211676998 | 02/02/2025 | 30 | 3H.8902.../2420962 | Starting/Stopping Issue | Task Start | Guwahati Industrial Sales & Service. | M T Enterprises - Bomdila | 54 | SPN: 2791,FMI: 31, SPN: 5838,FMI: 1 cleaned EGR but EGR was jammed due to customer maximum time operate in DG no load ,today SE again visit site with new EGR | OPEN | Ujjwal Das | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
4 | West | 211678994 | 03/02/2025 | 40 | 3H.8951.../2421054 | Starting/Stopping Issue | Task Start | ATC Telecom Infrastructure Private Limited | Natraj Power Tech - Gwalior | 1 | SPN/FMI- 2802/4, Battery and charging alternator connections were checked, found OK. ECU power supply 4 and 6(+) were checked, no power supply was found, so all wires on distribution block XDBK2 were tightened and problem was solved. | OPEN | Vijay Patil | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
11 | South | 211682239 | 04/02/2025 | 320 | F6.8802.../2420189 | AMF Pannel Problem Call by : Customer Name :Ramachandharen Contact :9445727472 | Task Start | Cosmo City Residents Welfare Association | Bharath Diesel Sales and Service - Karappakkam | 58.1 | Visit the site checked the generator found engine tripping in ECU malfunction. Connect the ikonnect ERROR CODE showing SPN=4375/16 and removed the DEF tank filter checked the allingmant refitted and checked the other parameters found normal started the generator run with load found normal. | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
10 | North | 211681008 | 04/02/2025 | 58.5 | T4.8941.../2422858 | Egr jamed | Task Start | PROFFESSIONAL | Suraj Motor Store - Srinagar |  | SPN/FMI 2791/5 EGR valve jammed, Replace the same clear the code with i-konnect tool then issue resolve | Closed | Ved Prakash Gupta | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
7 | East | 211662254 | 30/01/2025 | 58.5 | T4.8941.../2422791 | Abnormal sound issue Call by customer Name: Amrendra Kumar Number:8873967757 | Task Start | apna awas const pvt ltd | Globalline India Services Private Limited - Patna | 14.2 | SPN: 2791,FMI: 1/6/18 fault code were present in Ikonnect so SE checked EGR it found ok no clogging then cleared Code and flash the ECU by normal app file code cleared issue resolved but in under observation as SE not flashed the dummy file so on next visit dummy file neede to flash. | CLOSED | Prabhakar Kumar | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
2 | West | 211745130 | 22/02/2025 | 15 | GP3.8501.../2421182 | Amber Lamp Alarm Issue Call By Service Dealer Name-Mukesh No.-7583889815 | Closed | Kalinga Commercial Corporation Limited | Shree Engineering Service - KORBA | 350.26 | This DG is in mining area. After starting for 5 minutes engine temperature went above 100 degrees and controller displayed SPN 602, FMI 16( high ECT warning), due to radiator external choke up, so radiator was cleaned. DG is in covered area. Engineer educated the customer. | Closed | Vijay patil | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
20 | South | 211685563 | 05/02/2025 | 250 | F6.8842.C4../2420081 | ECU MALFUNCTIONING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the dg ECU override time ECU malfunction alarm blinking, so connected the I connect check the spn 4363 fmi 3 error coad not clear, so need new ecu for checking | Tast Start | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
19 | West | 211695219 | 08/02/2025 | 58.5 | T4.8941.../2422980 | starting issue | Task Start | POPULAR MARKETING & SERVICES. | Unique Techno Services Pvt Ltd. - Dahej | LR | SPN/FMI-97/5(Water in Fuel_ Self test) Engine was not starting so checked and found sometimes power was getting to the sensor and sometimes not. Tightened the 2A1(4B) wire in distribution block 2. 2A4 (Fuel pump) wire should be in distribution block 2 while it was in distribution block 4 so fixed it. | Closed | Amit Shandilya | [9 empty] | Fuel Pump | 8 | 6 | 5 | 240 | High
4 | East | 211664444 | 31/01/2025 | 250 | F6.8841.../2420132 | Starting Issue. Call By Customer. Name:- Lasto Mobile No.:-6000647321 | Closed | M/S Majena Infra Project | Hibreed Engineering Pvt. Ltd. - Jorhat | 118 | SPN 1761 FMI 16 low urea level alarm so top up the DEF and cleared the code also educated customer to maintain minimum 50% DEF | CLOSED | Ujjwal Das | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
5 | North | 211758341 | 26/02/2025 | 125.4 | 4H.8041.../2320097 | Voltage issue Call By Customer Name :- Sandip Kumar Mobile No :- 9560094118 | Task Start | DAYA EXPO | Paluck Technologies Ltd. - Faridabad | 213 | SPN/FMI 1761/16 , 51/0 Low Def level alarm & Throttle val jammed top up the DEF then Flash the file & Clean the ITV issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
10 | North | 211754394 | 25/02/2025 | 750 | DV2.8501.C4../2420165 | DG Issue | Task Start | Vodafone | R K Engineers - Meerut | 103 | SPN/FMI 658/13 injector No. 8 show the open fault so, check physically found ok then clear the code after trial on load no any issue found | Closed | Sudhir Awasthi | [9 empty] | Injector | 9 | 8 | 5 | 360 | High
51 | North | 211694019 | 07/02/2025 | 30 | 3H.8902.../2421211 | Starting/Stopping Issue | Open | BHARAT GENERAL STORE | Suraj Motor Store - Jammu | 102.05 | SPN/FMI-2791/18;EGR High voltage ;will flash the same by tomorrow | Open | Ved Prakash Gupta | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
6 | North | 211704687 | 11/02/2025 | 82.5 | 5H.8901.../2320076 | Starting/Stopping Issue | Closed | Sandhu Construction | SAAN Royal Power Solutions Private Limited - Karnal | 2280 | SPN/FMI-6595/0 & 3031/14 ; Fopund ECU AVS Value 57600 so change the value to 25600,clean the dosing module with hot water & changed the AdBlue filter kit,clean the AdBlue tank & remove the code,run the DG on Load,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | West | 211744437 | 21/02/2025 | 125.4 | 4H.8042.C4../2420790 | Starting issue Called by customer Name : Brajesh Number : 9826249509 | Closed | NEHA AUTOMOBILES | Shree Engineering Service - Chhatarpur | 95 | SPN/FMI- 3031/14,Calibrated the ECU with dummy file. | Closed | Vijay patil | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
11 | West | 211741856 | 21/02/2025 | 58.5 | T4.8941.../2422344 | amber lamp alram Issue Call By Customer Name :- Ashok Sir Mobile No :- 9712906022 | Closed | SPACE GENERATOR | Unique Techno Services Pvt Ltd. - Hathijan | 660 | SPN/FMI- 2791/18 Calibrated the ECU. | Closed | Amit sandlya | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
12 | West | 211741844 | 21/02/2025 | 58.5 | T4.8941.../2423141 | red lamp alarm Call By Customer Name :- Aman ... Mobile No :-9664961222 | Task Start | Asian Paints. | Unique Techno Services Pvt Ltd. - Surat | 2 | SPN/FMI- 2791/18 Calibrated the ECU. | Closed | Amit sandlya | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
13 | South | 211641954 | 25/01/2025 | 82.5 | 5H.8901.../2420824 | Voltage Fluctuation | Closed | PR TIJO THOMAS | G-Care Diesels Private Limited - Ernakulam | 13 | Connect I Konnect tool and clear the error (SPN=3031,FMI =14 in I Konnect tool)code and checked engine Start and stopping after work DG started working available load now dg running performance satisfactory.voltage fluctuation not in this site . | Closed | Mr. Sanjaimon S | [9 empty] | Load | 8 | 6 | 5 | 240 | High
64 | South | 211744205 | 21/02/2025 | 40 | 3H.8951.../2421294 | Starting/Stopping Issue | Closed | Novella Jacqueline jays fitness | Surya Power Services - Kalyan Nagar | 20 | check the egr valve fault then remove fault code spn 3216-2 and FMI 18 the senor connection then check RECONNECT the wire and start the engine check the load and observe engine running condition normal. | Closed | Mr. Anil Kumar H G | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
38 | North | 211696803 | 08/02/2025 | 125.4 | 4H.8041.../2320108 | Starting Issue Call By Customer Name - Vijay Kumar Number - 9829973147 | Closed | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 170 | Found SPN/FMI 51/0 throttle valve jammed need to be replace SD team was EDO of ITV | open | Gourav Sharma | [9 empty] | Throttle Valve | 8 | 6 | 5 | 240 | High
1 | East | 211751675 | 24/02/2025 | 160 | 6H.8475.../2420432 | Protect Lamp alam Issue Call By Customer Name :- Mobile No :- | Task Start | V. Retail Ltd. | HACS Engineering and Tech Private Limited - Ranchi | 148 | ECU protect lamp 56166, inducement SPN: 520528,FMI: 31 alarm and Adblue level low alarm SPN 1761 SPN 18 need to topup the DEF and need to clear the code. visit pending | OPEN | Prabhakar Kumar | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
9 | North | 211751325 | 24/02/2025 | 125.4 | 4H.8041.../2420460 | Display Issue Call By Customer Name :- Sarjeet Ji Mobile No :- 9810090015 | Task Start | Ankur Generators | Vidyut Engineers - Noida | 173 | found Alarm show in Ems Display spn 516166 FMI 0 ECU flt After that We Re set the Alarm | Closed | Kapil Solanki | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
55 | South | 211653335 | 28/01/2025 | 125.4 | 4H.8041.../2420579 | Alarm issue Call by : Customer Name : Uthya Kumar Contact : 8610530397 | Closed | Sathana Mahal | Bharath Diesel Sales and Service - Karaikal | 27.4 | Inspected the DG set found. Error code spn 1761 FMI 16 checked the DEF level low alarm 36% so new DEF level filled found ok. Error code clear found ok | Closed | Mr. NandhaGopal | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
20 | West | 211733206 | 19/02/2025 | 500 | DV8.9313.../2400001 | Genset Trip | Task Start | SENIOR SECTION ENGINEERS | Transcreek Engineers Pvt. Ltd. - Mumbai | 607.22 | SPN/FMI - 522100, 7,522122,7 & 3513/3 Checked the continuity from DCU2 to Nox sensor, Can line & power supply found ok. Checked the temperature sensor continuity found OK. Suspected B bank NOx sensor need to be replaced.checked both Bank Urea tank level sensor resistance and observed that Bank A tank level resistance 86 & Bank B tank level resistance 76. SE observed the fuel leak from the diesel flow meter. After restricting fuel leak the errors 157/14, 3513/3 got cleared but the 522100/7, 522122/7 got uncleared. Suspected the Nox Sensor of the B bank is having the issue. | open | Jagdeep Saini | [9 empty] | NOx Sensor | 9 | 7 | 6 | 378 | High
70 | North | 211685649 | 05/02/2025 | 57 | T4.8941.../2320042 | Error code issue | Closed | Sceptre Medical India Pvt Ltd | SAAN Royal Power Solutions Private Limited - Sonipat | 786.45 | SPN/FMI-97/5 ; water in fuel sensor with protect Lamp on ; No water traces found after drain from water separator but carbon particle found in connector comes across ECU to Pannel;Clean the same & remove the code,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
55 | North | 211692823 | 07/02/2025 | 20 | GP3.8601.../2421115 | Red Light Alarm issue Call By Customer Name :- Ajaz Mobile No :- 7889926045 | Task Start | HILAL BAKERY.. | Suraj Motor Store - Srinagar | 15 | SPN/FMI-2791/18;check the EGR valve & clean the same but code exists yet;need to flash the same | Open | Ved Prakash Gupta | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
8 | North | 211757806 | 26/02/2025 | 40 | 3H.8951.../2420096 | Tripping issue Call by customer Name: Ramjna Number: 8130797147 | Task Start | Purvanchal Projects Pvt Ltd | Vidyut Engineers - Noida | 3213 | SPN/FMI 105/3 checked and found Intake Air Tmp -vlt high, checked Alarm Riset , start the Engine put on Load 20 minutes found ok. | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
56 | North | 211759803 | 26/02/2025 | 500 | DV8.9313.../2420024 | starting issue | Closed | RAIL COACH FACTORY RCF | Dynamic Engineering Services - Jalandhar | 1 | SPN/FMI-652/5 ; Injector 2 firing order alarm occurred in Power Car,change the injector,Crank & Cam sensor one by one but issue remains the same ,Change the wiring harness,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
54 | North | 211761579 | 27/02/2025 | 160 | 6H.8475.../2420104 | Error code issue | Task Start | Worldnext Realty LLP. | Industrial Power Solutions - LUDHIANA | 988 | SPN/FMI-2802/4,Battery Voltage low,V-belt found loose on site so replace with 4K belt & check tension found 121 HZ,Battery water level found slightly low so same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
1 | West | 211754913 | 25/02/2025 | 250 | F6.8842.C4../2520002 | Error Code Issue. Call By Customer. Name :- Jay Pokhya Mobile No :-8758222728 | Task Start | SUZLON GLOBAL SERVICES LIMITED | Unique Techno Services Pvt Ltd. - Jamnagar | 4.26 | SPN/FMI- 516166/0, Cleared the DTC & educated to the customer. | Closed | Amit Sandlya | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
39 | North | 211717472 | 14/02/2025 | 15 | GP3.8501.../2420328 | Amber Lamp Alarm Issue Call By Customer Name - Saksham No - 8700988806 | Task Start | Hra Rice Mills | Dynamic Engineering Services - Jalandhar | 67 | SPN/FMI-2802/4 ; Related to Battery,Battery Voltage found low(10.4V)New 75AH battery installation for testing purpose instead of 65AH battery as advise by koel team.Old Battery sent for testing to vendor | Closed | Ved Prakash Gupta | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
2 | West | 211754533 | 25/02/2025 | 250 | F6.8841.../2420409 | Genset Trip | Task Start | N. K. INFRASPACE | Unique Techno Services Pvt Ltd. - Baroda | 5 | SPN/FMI-516166/0 & 1761/16 Filled the DEF & cleared the DTC. | Closed | Amit Sandlya | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
12 | North | 211754055 | 25/02/2025 | 320 | F6.8802.../2420135 | CAM SENSOR FAULTY | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Fault code - SPN - 636 FMI - 8 ( Cam sensor fault) Engineer checked supply voltage at Sensor found 5 vdc and checked continuity of wiring harness found ok. then Sensor also replaced but problem not resolved. | open | Gourav Sharma | [9 empty] | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
11 | North | 211754244 | 25/02/2025 | 125.4 | 4H.8041.../2320094 | Oil sensor Issue. Call By Customer Name :-Gopal Mobile No :-8439579873 | Task Start | SS. Creation | Paluck Technologies Ltd. - Ghaziabad | 138 | SPN/FMI 1761/16 & 3031/14 Clear the DTC & flash the file issue resolve | Closed | Kapil Solanki | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
12 | West | 211736867 | 20/02/2025 | 200 | 6H.8435.../2420130 | Adblue issue | Closed | R.D.SAMANT CONTRACTORS PVT.LTD | Mahalaxmi Diesels - Ratnagiri | 19 | Error code P1079 , SPN 4225 FMI 2 pipe from tank to supply module found chocked so clean it with hot water and fitted . | Closed | Jagdeep Saini | [9 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
2 | WEST | 211737085 | 20/02/2025 | 250 | F6.8841.../2420175 | Add blue Consomtion Call By Customer Name :- Mobile No :- | Closed | SHREYA CONSTRUCTION | Dhanashree Technocrats Pvt. Ltd. - Jalgaon | 605 | SPN 4095 DEF not supply from supply module to dosing module , so changed the supply module. | Closed | ECU fault | [9 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
3 | West | 211728952 | 18/02/2025 | 125.4 | 4H.8042.C4../2420589 | Starting/Stopping Issue | Task Start | KP. Energy | Unique Techno Services Pvt Ltd. - Gandhidham | 312 | SPN/FMI- 516166/0 and 1761/14 Filled the DEF and cleared the DTC. | Closed | Amit sandlya | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
27 | North | 211746277 | 22/02/2025 | 125.4 | 4H.8042.C4../2420601 | Urea Level Issue | Completed | Bindal Cotex Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 33 | SPN/FMI-516166/0 with Amber Lamp On ; reset the DTC & run on load ,Issue resolved | Closed | Ved Prakash Gupta | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
6 | WEST | 211760420 | 26/02/2025 | 500 | DV8.9313.../2420038 | STARTING ISSUE | Task Start | Powercare | Unique Techno Services Pvt Ltd. - Surat | LR | SPN/FMI- 100/3 oil pressure sensor and low coolant level. Oil pressure and tem sensor found broken so EDO placed for the same. Radiator was empty of coolant. SE will visit today for controller data log. | Closed | Amit Sandlya | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
3 | WEST | 211717498 | 14/02/2025 | 30 | 3H.8902.../2420699 | Starting Issue Call By Customer Name Nayar .. No : 8291603287 | Closed | PERFECT FABRICATORS | Transcreek Engineers Pvt. Ltd. - Mumbai | 369 | Dg is not start due to air lock issue , remove air lock ,SPN 157 FMI 14( Pres relief vlv fault)Connect ikonnect and clear DTC. | closed | Jagdeep Saini | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
6 | East | 211691587 | 07/02/2025 | 160 | 6H.8475.../2420166 | Supply module issue | Task Start | M/s. Fifeo Energy Station | Green Powerline - Tezpur | 328 | SPN: 4376,FMI: 5, SPN: 4358,FMI: 2, SPN: 4095,FMI: 2, SPN: 1761,FMI: 17 so as per the fault code SE checked the supply module relative pressure in IKonnect found only 76 hPa - 300 hPa so checked the its voltage at connector found OK and cotinuity also found OK checked its filter all found OK, replaced supply module then started and checked relative pressue found 5002 hPa. | CLOSED | Ujjwal Das | [9 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
12 | North | 211712985 | 13/02/2025 | 40 | 3H.8951.../2520140 | Starting Problem | Closed | TARUN DUA | Vidyut Engineers - Noida | 6 | SPN/FMI 97/5 Check & found no any water traces in seprator after that clear the DTC | Closed | Kapil Solanki | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
5 | North | 211717931 | 14/02/2025 | 750 | DV2.8513.C4../2520001 | starting issue | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Found SPN/FMI 1244/3 error code Clear the DTC KG 1500 programming | Closed | Gourav Sharma | Details Required | [8 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
3 | East | 211702192 | 10/02/2025 | 30 | 3H.8902.../2422420 | Abnormal Sound Issue. Call By Customer. Name:-Parshant Byanth Mobile No.:-7551878476 | Open | Presidency Infracon LLP. | HACS Engineering and Tech Private Limited - Ranchi |  | SPN: 5838,FMI: 1, SPN: 2791,FMI: 31 fault code showing on KRM visit pending | OPEN | Prabhakar Kumar | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
3 | East | 211685802 | 05/02/2025 | 250 | F6.8841.../2420332 | Starting/Stopping Issue | Open | Bishop Westcot School | HACS Engineering and Tech Private Limited - Ranchi | 30 | SPN -3031 Fmi 1, SPN 516166 FMI 0 and SPN 1761 FMI 16 so cleared the code from DTC first two code cleared but SPN 1761 was there duet to the DEF level was 40 % so need to topup | CLOSED | Prabhakar Kumar | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
5 | North | 211704877 | 11/02/2025 | 25 | GP3.8702.../2420302 | error code | Open | Aryadhenu Misthanshala | SAAN Royal Power Solutions Private Limited - Hisar | 333.3 | SPN/FMI-636/8 ; Cam Sensor flt error ; check the continuity to sensor & voltage supply from ECU found ok,Flash the ECU but issue remains same,RRT team will attend | Open | Ved Prakash Gupta | [9 empty] | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
21 | West | 211693350 | 07/02/2025 | 160 | 6H.8475.../2420091 | Red Lamp Alarm & sound issue Call by : Customer Name :Kumar Contact : 9095810926 | Task Start | SOWPARNIKA PROJECTS AND INFRASTRUCTURE (P) LTD., | Shree Engineering Service - Satna | 70 | Low coolant level in radiator so filled the coolant. SPN/FMI- 110/3 So the coolant sensor connector was refitted and the DTC was cleared | Closed | Vijay Patil | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
14 | North | 211698546 | 10/02/2025 | 125.4 | 4H.8041.../2320090 | Starting Issue Call By Customer Name - Rajesh Kumar Number - 7042659373 | Task Start | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi | 3081 | Found SPN/FMI 4095/1, 4095/0, 4339/2, 3031/14 Check the DEF tank condition found ok, then check Inlet & Outlet line found ok, after trial on load the DG about 30 min. found No, any alarm but_ Found also Radiator chocked & Service due So, Educate the Customer for kindly cleaning the Radiator & Service due | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
8 | East | 211702192 | 10/02/2025 | 30 | 3H.8902.../2422420 | Abnormal Sound Issue. Call By Customer. Name:-Parshant Byanth Mobile No.:-7551878476 | Open | Presidency Infracon LLP. | HACS Engineering and Tech Private Limited - Ranchi |  | SPN: 5838,FMI: 1, SPN: 2791,FMI: 31 fault code showing on KRM visit pending | OPEN | Prabhakar Kumar | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
18 | West | 211745275 | 22/02/2025 | 40 | 3H.8951.../2420859 | Starting Issue Call By Customer Name :- Sandeep Poojari Mobile No :-9833132999 | Closed | SAI KESHAR RESIDENCY | Transcreek Engineers Pvt. Ltd. - Panvel | 19 | SPN 97 FMI 5 , reconnect the sensor and tighten the distribution block wire | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
72 | North | 211685282 | 05/02/2025 | 750 | DV2.8501.C4../2320030 | Tripping Issue Call By Customer Name - Santosh Number - 9588115616 | Closed | Shree Cement Ltd. | SAAN Royal Power Solutions Private Limited - Panipat | 152 | SPN/FMI-516166/0 , 656/3& 523576/0;DG was in running condition on site,Checkthe AdBlue Level & Line found ok,Check continuity in cylinder no.5 & 6 found ok,reset the alarm & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
36 | North | 211697077 | 08/02/2025 | 58.5 | T4.8941.../2421614 | Starting Issue. Call By Customer. Name:- Abhishek Mobile No.:-8550048008 | Closed | Hotel Gurukripa INN. | Espiem Engines & Machines (P) Limited - Agra | 37 | Found MCB wire loose in panel tightness the same & SPN/FMI 2802/4 & 97/5 clear the code then issue resolve | Closed | Sudhir awasthi | [9 empty] | MCB | 5 | 4 | 3 | 60 | Low
4 | East | 211693420 | 07/02/2025 | 125.4 | 4H.8041.../2420938 | Maintanance due alarm issue Called by customer Name : Shobit Number : 7549039250 | Task Start | Shantidoot Infra Services Pvt. LTd. | HACS Engineering and Tech Private Limited - Ranchi | 253 | SPN: 1761,FMI: 16 - Urea Tank Level low alarm, So SE top up the Adblue and restore the issue. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | West | 211735796 | 19/02/2025 | 320 | F6.8802.../2420178 | Starting Problem Call by : Customer Name :kuluthip Contact :8668566570 | Closed | MIMSR MEDICAL COLLEGE | KALA Care Global LLP - Latur | 114 | SPN 1761 FMI 16 Abdlue level low so top up adblue. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | West | 211691995 | 07/02/2025 | 58.5 | T4.8941.../2420788 | Starting Issue Call By Customer Name :- Yagnik Parmar Mobile No :-9904654660 | Closed | BND TECHNOLOGIES PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Vapi | 32 | SPN/FMI- 157/14 Tightened all wire connections in panel and started engine but did not start so replaced relay board. | Closed | Amit Shandilya | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
2 | West | 211746360 | 22/02/2025 | 125.4 | 4H.8041.../2420541 | Tripping Issue Call By Customer Name :- MAHESH JAGTAP Mobile No:-919930262638 | Closed | VIJAY SALES (INDIA) PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 397 | SPN 157 FMI 14 cheack all the connection connect ikonnect and clear error code. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | West | 211728693 | 18/02/2025 | 82.5 | 5H.8901.../2420327 | Error code | Task Start | METAL MORPHOSIS PRIVATE LIMITED | Shree Engineering Service - Raipur | 550 | spn 516166 fmi 0 connect ikonnect and clear error code. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211679229 | 03/02/2025 | 50 | T4.8941.../2420659 | Starting Issue Call By Customer Name : Virendra Singh No : 7889601565 | Task Start | Administrative Reforms Department Uttar Pradesh. | Deep Jyoti Electricals and Services - Moradabad | 212 | SPN/FMI 2802/4 , 157/14 DG Fail to start check and found voltage drop after that Relay will be interchange | Closed | Sudhir Awasthi | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
8 | North | 211754958 | 25/02/2025 | 250 | F6.8842.C4../2420013 | NCD lamp alarm | Closed | Arihant Machinery Store | SAAN Royal Power Solutions Private Limited - Sonipat | 228.1 | SPN/FMI-1761/16 & 516166/0 ,AdBlue level found low so top-up the same & remove the code ,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | North | 211673445 | 01/02/2025 | 57 | T4.8941.../2320042 | Starting/Stopping Issue | Closed | Sceptre Medical India Pvt Ltd | SAAN Royal Power Solutions Private Limited - Sonipat | 786.44 | SPN/FMI-97/2 Water in Fuel;drain fuel from water separator & found water traces in fuel,same found from tank also;clean the tank & water separator filter & run the DG after re-fill the Fuel ,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211675255 | 01/02/2025 | 320 | F6.8802.../2420279 | Genset Trip | Closed | Orchid Hospitality Services Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 41 | SPN/FMI-1761/16 ; Found AdBlue 18% ; Top-up the same & resolved the same | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211664604 | 31/01/2025 | 15 | GP3.8501.../2420094 | fuel alram | Closed | Dhani Power Solutions | SAAN Royal Power Solutions Private Limited - Rohtak | 109 | SPN/FMI-96/0 ; High Fuel Level ;Reduce some Fuel & same educated to customer to top-up fuel max. 95% | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | North | 211676829 | 02/02/2025 | 40 | 3H.8951.../2320061 | Starting Issue Call By Customer Name :- Aashu Jaiswal Mobile No :- 9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 715.35 | SPN/FMI 97/2 check in water seprator found no water traces in seprator check in tank found no issue so, clear the code then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | North | 211760643 | 26/02/2025 | 125.4 | 4H.8041.../2420606 | Tripping Issue Call By Customer Name :-Gurpreet Singh. Mobile No :-9536777118 | Task Start | JEET CONSTRUCTION | R K Engineers - Meerut | 245 | SPN/FMI 157/14, 4095/1, 110/3, 1761/16 Check & found override switch off then on the switch then issue resolve | Closed | Sudhir Awasthi | KRM Check | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
36 | North | 211764247 | 27/02/2025 | 82.5 | 5H.8901.../2320034 | Inspection/Maintenance | Closed | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 338 | Found SPN/FMI 1761/16 ,4375/3 ,6595/0 ,51/0 reset the alarm with i-konnect tool | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211763206 | 27/02/2025 | 125.4 | 4H.8041.../2320172 | Inspection/Maintenance | Closed | Petty Petal Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 498 | SPN/FMI 1761/16, 110/0 & Maintenance due alarm reset the alarm | Closed | Kapil Solanki | KRM Check | [8 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
8 | WEST | 211664638 | 31/01/2025 | 125.4 | 4H.8041.../2420093 | Under Speed Alarm Call By Customer Name - Vishal No - 9730711011 | Closed | Rhenus Contract Logistics India Private Limited | Transcreek Engineers Pvt. Ltd. - Bhiwandi | 153 | SPN: 1761 FMI: 16 ,Low adblue level , top up adblue level. | closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211674420 | 01/02/2025 | 400 | DV8.8542.C4../2420137 | ECU Amber Alarm Issue Call By Customer Name - Suresh Kumar Number - 9465181003 | Closed | RR JAIN INDUSTRIES | Industrial Power Solutions - LUDHIANA | 43 | SPN/FMI-523584/15;AdBlue Level Low in Tank 2 so advised same to fill AdBlue before it comes below 50% | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211678007 | 03/02/2025 | 125.4 | 4H.8042.C4../2420815 | Starting/Stopping Issue | Open | Sailaja Commercial Construction Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 39 | SPN: 3031,FMI: 14 - SCR Monitoring - Urea Tank Temperature - Bank 1 - Special In | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211748845 | 23/02/2025 | 125.4 | 4H.8042.C4../2420344 | Starting/Stopping Issue | Closed | Master Packaging | SAAN Royal Power Solutions Private Limited - Sonipat | 44.1 | SPN/FMI-516166/0 & also Fuel level showing wrong parameter (8% instead of 100%) due to float stuck so re-fitted the same & remove the code,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211699635 | 10/02/2025 | 125.4 | 4H.8041.../2320066 | Starting Issue Call By Customer Name :- Anil Kumar Mobile No :- 9971230939 | Task Start | VK GENSET & POWER SOLUTION | Paluck Technologies Ltd. - Gurgaon | 5249 | Found SPN/FMI 51/1 ITV jammed, When Engineer open the ITV connector then, DG running ok, but when he connect the connector then DG trip So, I suggest to replace the ITV | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211741951 | 21/02/2025 | 57 | T4.8941.../2320139 | STARTING ISUE Call By Customer Name :-Manish Mobile No :-9625939742 | Task Start | Msafe | Vidyut Engineers - Noida | 208 | SPN/FMI 157/14 PRV open fault then check & found 12RB1, RL2 Voltage drop so, check with other Relay found ok after need to Replace the Relay | open | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
5 | East | 211720900 | 15/02/2025 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
46 | North | 211717637 | 14/02/2025 | 25 | GP3.8702.../2420165 | Electrical Problems | Closed | Ms. Ranjit Kaur | SAAN Royal Power Solutions Private Limited - Zirakpur | 92 | SPN/FMI-97/5,Water in Fuel,clean the fuel filter & reset the code,DG running fine | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
44 | North | 211719610 | 15/02/2025 | 125.4 | 4H.8041.../2420234 | Tripping Issue Call By Customer Name - Ravindra Number - 8930092565 | Closed | T. Rituinsan | SAAN Royal Power Solutions Private Limited - Hisar | 77 | SPN/FMI-1761/16 ,Low AdBlue Level,Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211720900 | 15/02/2025 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
57 | North | 211758998 | 26/02/2025 | 250 | F6.8841.../2420411 | Code issue | Task Start | Winntra PEB And Roofing Systems Private Limited | SAAN Royal Power Solutions Private Limited - Sonipat | 45.11 | SPN/FMI-3031/14,I-Konnect tool not able to be connected so will attend Today again | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | NORTH | 211723321 | 17/02/2025 | 125.4 | 4H.8042.C4../2420571 | Amber lamp on alarm Call by Customer Name : Gajendra No : 8287266787 | Closed | AVON COATINGS | Paluck Technologies Ltd. - Faridabad | 3 | Found SPN/FMI 516166/0 reset thealarm | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | WEST | 211708564 | 12/02/2025 | 160 | 6H.8475.../2420307 | Error Code Issue Call By Customer Name :- Deepak Pawar Mobile No :-9975566453 | Closed | Khuspal Home Textile LLP. | Transcreek Engineers Pvt. Ltd. - Vasai | 19 | SPN=516166 FMI=0, SPN=1761 FMI=16, this codes are showing inform to customer for fill the adblue , and connect ikonnoect and clear code. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211720900 | 15/02/2025 | 82.5 | 5H.8901.../2420018 | Tripping issue Call By Customer Name - Sanjeeth Kumar Number - 7301692554 | Task Start | Nutan Construction | Globalline India Services Private Limited - Patna | 122 | SPN-3224 FMI 2,, SPN: 516166,FMI: 0 , SPN: 4225,FMI: 1,SPN: 51,FMI: 0, SE is not answering | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211720503 | 15/02/2025 | 320 | F6.8802.../2320073 | Alarms. E C U malfunc | Closed | Vedic Cosmeceuticals Private Limited | Vidyut Engineers - Noida | 124 | SPN/FMI 97/2 ,3364//8, 1761/16, 4225/1, 3031/14, 520527/16, 4365/2 Clear the DCT | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211750117 | 24/02/2025 | 160 | 6H.8475.../2320002 | Indicator Lamp Alaram Issue Call By Customer Name :- Harish Mobile No :- 9720331726 | Closed | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 94 | found Alarm show in Ems Display High Adblue temp flt spn 3031 & FMI 14 After that We Re set the Alarm and check the DG set found | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | North | 211721532 | 15/02/2025 | 125.4 | 4H.8041.../2320108 | Starting/Stopping Issue | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 171 | SPN/FMI 51/0 change the trottle valve but problem same, | Open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211737044 | 20/02/2025 | 125.4 | 4H.8042.C4../2420016 | loading Issue Call By Customer Name :- Akshay Jain Mobile No :- 8800616123 | Closed | STARCO METAPLAST PVT. LTD. | Paluck Technologies Ltd. - Ghaziabad | 63 | Adblue lavel low and code show spn 520528 fmi 31 , 1761/16, 516166/0 urea required with service due | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211699675 | 10/02/2025 | 10 | GP3.8301.../2420135 | Low Voltage Alarm Issue Call By Customer Name :- KHEKTO . Mobile No :- 9863164425 | Open | Catsm | Hibreed Engineering Pvt. Ltd. - Jorhat | 2 | SPN: 2802,FMI: 4,(ASE will update by morning) | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
29 | North | 211703686 | 10/02/2025 | 160 | 6H.8475.../2420394 | Starting issue Call By Customer Name ;- Rohit .. No;- 9634382881 | Closed | Tulsi Dham | Espiem Engines & Machines (P) Limited - Agra | 42 | Found V belt loose so, tightness the same & SPN/FMI 2802/4 & 516166/0 then clear thew code by I-konnect then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211707555 | 11/02/2025 | 58.5 | T4.8941.../2420013 | Error code issue Call By Customer Name :-Kamal Kanth Sare Number:- 9873088378 | Task Start | Vinod Kumar | Vidyut Engineers - Noida | 131 | SPN/FMI, 100/1 & 100/3 clear the code with i-konnect tool | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | North | 211745091 | 22/02/2025 | 200 | 6H.8435.../2420175 | Ncd Lamp ALarm Issue Call By Customer Name :-Nandkishor Sharma Mobile No :-7732910730 | Task Start | Decora Kitchen Interiors Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 39 | SPN/FMI-1761/16 ; AdBlue Level Low , on site found below 50%,Top-up the same & educate customer to keep AdBlue minimum 50% | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211699675 | 10/02/2025 | 10 | GP3.8301.../2420135 | Low Voltage Alarm Issue Call By Customer Name :- KHEKTO . Mobile No :- 9863164425 | Open | Catsm | Hibreed Engineering Pvt. Ltd. - Jorhat | 2 | SPN: 2802,FMI: 4,(today service cordinator will share update by end of day) | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | West | 211745275 | 22/02/2025 | 40 | 3H.8951.../2420859 | Starting Issue Call By Customer Name :- Sandeep Poojari Mobile No :-9833132999 | Closed | SAI KESHAR RESIDENCY | Transcreek Engineers Pvt. Ltd. - Panvel | 19 | SPN 97 FMI 5 , reconnect the sensor and tighten the distribution block wire | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211698894 | 10/02/2025 | 125 | F6.9840.../2420003 | Electrical Problems | Task Start | Venu Eye Institute & Research Centre. | Vidyut Engineers - New Delhi | 48 | found EUGO sensor faulty then we have change Lambada Make EUGO sensor and Extension pipe for catalyst outlet replace after that check engine working ok but alarm same SPN:3227 FMI:15 SE contact to ASE he say for flashing | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | West | 211719663 | 15/02/2025 | 40 | 3H.8951.../2420844 | Starting Issue Call By Customer Name :-RAM Mobile No :-7757992893 | Closed | HAWARE LEGACCY | Transcreek Engineers Pvt. Ltd. - Mumbai | 10 | active SPN 637 and FMI -2 which is related to crank sensor . So checked its voltage in wake up mode it is 2.5 vdc . So as per troubleshooting tree diagnostic increased its gap between flywheel and sensor then checked for four to five times, now it is found working properly. | Closed | Jagdeep saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
8 | North | 211738492 | 20/02/2025 | 82.5 | 5H.8901.../2320094 | Genset Trip | Task Start | RAO TENT HOUSE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 456 | Found SPN/FMI 51/5 & 51/0 ITV required Change | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | NORTH | 211722664 | 16/02/2025 | 250 | F6.8841.../2320050 | Error Code Issue. Call By Customer. Name:-Pradeep Yadav Mobile No.:-8368321282 | Open | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 260 | SPN/FMI 5461/0 reset the alarm & flash the file then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low

## Non-SPN
SR.No. | Zone | Incident no | Creation Date | KVA | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Run hours | Observation | Incident Status | ASM Name | HO remark | Unnamed: 15 | Unnamed: 16 | Unnamed: 17 | Unnamed: 18 | Unnamed: 19 | Unnamed: 20 | Unnamed: 21 | Unnamed: 22 | Component | Severity (S) | Occurrence (O) | Detection (D) | RPN | Priority
1 | South | 211646787 | 27/01/2025 | 58.5 | T4.8941.../2422434 | Alarm issue Call by : Customer Name : Abishek Contact : 9626957432 | Task Start | Visual Grammar Salon & Experiences India P Ltd | Madurai Electro Controls - Oomachikulam | 58 | No issue in DG. Engine side check. Panel board check. Check eventlog alarm. thare is no error issue. Start the engine running condition ok. No any issue. Engine oil check. Battery check. All parameters are working. Engine and alternator condition normal | Closed | Mr. NandhaGopal | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
9 | South | 211713043 | 13/02/2025 | 25 | GP3.8702.../2421014 | MCB Issue And Voltage Fluctuation Issue Call By Customer Name :- Varun Mobile No :-9036502705 | Closed | LAKSHMITHA FUELS | Surya Power Services - Bommasandra, Bangalore | 252 | Customer using unbalance load so voltage fluctuation & Mccb trip educated the customer for balance load. | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
11 | South | 211712687 | 13/02/2025 | 7.5 | D3.8305.../2400160 | Load Problem Call by : Customer Name :Joseph Contact :9526746426 | Task Start | JRM Ice Plant | Electro Controls - Thiruvananthapuram | 4 | Customer Using over load. Today customer electrician visit | Task Start | Mr. Sanjaimon S | [9 empty] | Load | 8 | 6 | 5 | 240 | High
14 | South | 211712529 | 13/02/2025 | 40 | 3H.8951.../2420713 | Battry problem Call by : Customer Name :Kashinath Contact :8618802728 | Task Start | Star Karavali Constructions | Vijayshree Diesel Sales and Service - Bijapur | 574 | Charging Alternator fuse blown | Closed | Mr. Anil Kumar H G | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
15 | South | 211717507 | 14/02/2025 | 200 | 6H.8435.../2420134 | Alarm Issue Call By Customer Name - Mahesh Number -6362924702 | Task Start | Nirmithi Kendra | Surya Power Services - Kalyan Nagar | 252 | 520527/16- Urea tank - Level-High - moderate severity, alarm adblue tank high level flt alarm top up the def then started the engine found running condition is normal… | Closed | Mr. Anil Kumar H G | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
19 | South | 211717216 | 14/02/2025 | 0 | F6.8842.C4../2420111 | AIR LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Attended the above site for air leakage complaint.Inspected the site,started the generator,in load condition air leakage found from the turbo and CAC inlet pipe joining clamp side because turbo and CAC inlet pipe not properly seated and clamp also not properly tightened so removed the clamp,then properly seated the turbo and CAC inlet pipe and retightened the clamp.Started the generator and tested with load condition.No air leakage found . Generator all parameters are found within the limit. | Task Start | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
23 | South | 211716825 | 14/02/2025 | 40 | 3H.8951.../2421616 | Starting Issue Call By Customer Name :-Pramod Sir Mobile No :-7022409095 | Task Start | AAKAAR PROPERTIES | Surya Power Services - Mysuru | 1.32 | Visit the site and start the engine check the ac voltage is found ok and neutral link damaged and replace with new one neutral link and check and load side ac voltage is found ok start and run the engine all working parameters condition is satisfied | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
27 | South | 211716573 | 14/02/2025 | 40 | 3H.8951.../2520043 | Error code issue Call by : Dealer Name :Senthil Contact :9524633437 customer no:9384374883 | Open | SUNBEAM GENERATORS PVT. LTD | Bharath Diesel Sales and Service - Chennai | LR | Visited the site checked the engine found error code 2791/18,2719/6 on the controller, checked the engine as per the error, checked the EGR valve connectors, and wiring harness found ok. checked the battery terminals tightness and distilled water found ok .the error code is coming, while ECU is over ride mode. then connected the ikonnect tool and clear the error code, start and checked the engine, checked the EGR valve parameters by using ikonnect app found normal, found the same error is coming repeatedly, then flash the ECU by using ikonnect app .then checked the engine oil level, coolant level, v belt tension found ok. start and checked the engine, checked the engine parameters by using ikonnect app found normal. | Closed | Mr. NandhaGopal | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
28 | South | 211716559 | 14/02/2025 | 58.5 | T4.8941.../2422797 | Maintenance Due Call by : Customer Name :Manoj Contact :8089660774 | Open | EVEREST GREEN KERALA | Electro Controls - Alappuzha | 270 | Check the engine found emergency stop issue. Automatically sensing the negative pulse to controller and get the engine shutdown. Loop additional supply from emergency switch to controller and resolve the issue. Now engine working normally | Closed | Mr. Sanjaimon S | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
7 | North | 211717870 | 14/02/2025 | 320 | F6.8802.../2320057 | Leakage Issue | Closed | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 253 | found coolant leakage from hose clamp loose tightness the same then issue resolve but found second problem Inlet manifold gasket was damage need to be replace | Open | Kapil Solanki | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
8 | North | 211717819 | 14/02/2025 | 125.4 | 4H.8042.C4../2520049 | STARTING ISSUE | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Found Charging alternator was faulty after replace then issue resolve | Closed | Gourav Sharma | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
25 | North | 211718880 | 14/02/2025 | 250 | F6.8841.../2420042 | Power Supply issue Call By Customer Name :- Vijay Kumar Mobile No :- 9795586504 | Open | Bharat Petroleum Corporation Ltd. Loni | Paluck Technologies Ltd. - Ghaziabad | 56 | Found load issue in DG 150 Amp. | Open | Kapil Solanki | Details Required | [8 empty] | Load | 8 | 6 | 5 | 240 | High
28 | North | 211721195 | 15/02/2025 | 125.4 | 4H.8041.../2420433 | Starting/Stopping Issue | Task Start | Payal Ceramics | Espiem Engines & Machines (P) Limited - Aligarh | 341 | found coolant leakage from hose clamp loose tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
31 | North | 211720641 | 15/02/2025 | 58.5 | T4.8941.../2421936 | Auto Panel Fiting Issue Call By Customer Name :-Akash Mobile No :- 7665379958 | Closed | SNA Prime Feed Private Limited | Pratap Diesels Pvt. Ltd. - Bhiwadi | 15 | DG CONTROLLER MAINS CONFRIGRATION DISABLE IN CONTROLLER AND DG START AUTO OR MANUAL MODE WIRE CONNECTON IN 11 NO | Closed | Gourav Sharma | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
34 | North | 211720305 | 15/02/2025 | 58.5 | T4.8941.../2420787 | Starting Issue Call By Customer Name :- Ram Saran Mobile No :-7982975198 | Closed | SETHI BUILDCON | Vidyut Engineers - New Delhi | 3621 | Battery discharge & found charging alternator fuse was defective replace the same & DG start by standby battery | Closed | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
38 | North | 211719874 | 15/02/2025 | 58.5 | T4.8941.../2421055 | Low Fuel Alarm Issue Call By Customer Name - Chandan Kumar Number - 7488306045 | Closed | N.K.ENTERPRISES | Paluck Technologies Ltd. - Faridabad | 67 | Found 1 & 2 No. point loose in controller so, tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
6 | South | 211713635 | 13/02/2025 | 45 | 3H.8951.../2421187 | Starting Problem Call by : Customer Name : Prasanth Contact : 9361474752 | Completed | PUSHKARAM AGENCY | Bharath Diesel Sales and Service - Pudukottai | 109 | 2791/18, 2791/6 Starting problem due MIL Lemp alarm due to check DM1 EGR valve alarm remove the EGR connector and reset alarm start dg running condition with load check up done. Engine oil level battery distillery water level radiator coolent level ok. | Closed | Mr. NandhaGopal | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
14 | East | 211701481 | 10/02/2025 | 7.5 | D3.8305.../2400159 | Starting/Stopping Issue | Closed | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - BHUBANESWAR | 135 | No issue in DG customer side underload issue | CLOSED | Ujjwal Das | [9 empty] | Load | 8 | 6 | 5 | 240 | High
2 | East | 211713520 | 13/02/2025 | 15 | GP3.8501.../2421004 | Red Lamp ON Alarm Issue Call By Customer Name - Anuj Number - 9122775005 | Closed | Prakash Construction | HACS Engineering and Tech Private Limited - Ranchi | 160 | EGR valve related code was due to the loose connection of its connector so refitted after cleaning it properly then checked and issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
2 | North | 211714225 | 13/02/2025 | 750 | DV2.8501.C4../2420149 | Starting Issue & ECU Lamp On Alarm. Call By Customer Name :- Krishan Kumar Sharma Mobile No :-7830295735 | Task Start | Infratech Solutions | Vidyut Engineers - Noida | 22.11 | Found DEF level 0% so, DG not start | open | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
43 | South | 211701818 | 10/02/2025 | 30 | 3H.8902.../2422347 | Line Rejection | Closed | MCBS | G-Care Diesels Private Limited - Ernakulam | LR | 2791/18,5838/1 Error code issue flash the ecu | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
44 | South | 211701796 | 10/02/2025 | 58.5 | T4.8941.../2421860 | Starting/Stopping Issue | Closed | Mr. Narendra Kumar Gehlot | Surya Power Services - Bommasandra, Bangalore | 8 | Visit the site check the engine problem is engine not starting due to alram showing ecu falt and mains phase reversied after setting in control mains phase reversied after re set the alarm after checking the engine all parameters after start the engine running coundtion ok. (516160/0,97/5) | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
59 | South | 211697127 | 08/02/2025 | 500 | DV8.8501.C4../2420107 | AMF Panel Problem Call by : Customer Name : shameer Contact : 7736142777 | Closed | Budget Foods Private Limited | G-Care Diesels Private Limited - Malappuram | 4 | Engine automation issue joint visit OEM and amf panel teams engine ecu avr controller settings correct synch panel commissioning not completed synch panel complaint | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
60 | South | 211697126 | 08/02/2025 | 500 | DV8.8501.C4../2420114 | AMF Panel Problem Call by : Customer Name : shameer Contact : 7736142777 | Closed | Budget Foods Private Limited | G-Care Diesels Private Limited - Malappuram | 4 | Engine automation issue joint visit OEM and amf panel teams engine ecu avr controller settings correct synch panel commissioning not completed synch panel complaint | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
61 | South | 211696773 | 08/02/2025 | 750 | DV2.8501.C4../2420089 | ECU on alarm issue Call by customer Name: Sanjay Number: 9036750680 | Closed | HINDUSTAN FOODS LIMITED | Surya Power Services - Mysuru | 10 | Visit the site check the ecu protect off engine getting off so check with tool it's showing buster 2 pump not working so replace with 2 buster pump and running the dg 30 min | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
63 | South | 211696603 | 08/02/2025 | 40 | 3H.8951.../2420210 | Under speed Issue Call By Customer Name :- Rudra gowda Mobile No:-9844748692 | Task Start | Neovision Lasik Centre. | Vijayshree Diesel Sales and Service - Bellary | 151 | attend the site check the dg and replaced the ECU new fitted found ok and ECU part no (T4.435.01.0) and started the engine running condition good and checked the all parameter found ok ds sir | Task Start | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
65 | South | 211696390 | 08/02/2025 | 7.5 | D3.8305.../2400160 | Starting Problem Call by : Customer Name :Josph Contact :9562456194 | Closed | JRM Ice Plant | Electro Controls - Thiruvananthapuram | 2 | Reached the site checked dg customer said voice in engine tripping.started the dg and given load . engine tripped showing over load.advise customer to contact local electrical team to correct the issue. | Closed | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
40 | North | 211719700 | 15/02/2025 | 625 | DV0.8501.C4../2420120 | Starting Issue Call By Service Dealer Name :-Babu lal Mobile No :-7042625890 | Closed | Budhiraja Electricals | Deep Jyoti Electricals and Services - Haldwani | 4.22 | Found Battery Voltage (8.9) Low and check DC Alternator wire Conection (W/L Excitation) Found Loose and proper tight and External Battery charger on and Battery charging mode on | Closed | Sudhir Awasthi | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
71 | South | 211695290 | 08/02/2025 | 30 | 3H.8902.../2420726 | Genset Trip | Task Start | Mr. Eric Alan Pais | Surya Power Services - Bommasandra, Bangalore | 43 | Visit the site check the engine oil level ok, radiator coolant level ok, battery distilled water terminal connection fuel hose ECU connection, panel wiring connection realy bord connection,doc connection,EGR connection after start the engine running coundtion ok. Under Speed issue. | Closed | Mr. Anil Kumar H G | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
73 | South | 211694207 | 07/02/2025 | 250 | F6.8841.../2420253 | Starting Issue Call By Customer Name :- Naheer Mobile No :-8697449853 | Closed | Ceerah | Surya Power Services - Kalyan Nagar | 10 | visited the site and checked the engine as per the customer complaint observed engine not starting due to alarm of coolant temperature fault ,reset the Alarm | Closed | Mr. Anil Kumar H G | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
80 | South | 211692971 | 07/02/2025 | 40 | 3H.8951.../2420927 | Diesel Leakage Problem Call by : Customer Name : Srikanth Contact : 9966223750 | Closed | Rakesh Kumar Jain | Sri Manjunath Technical Services - Narasaraopet | 9 | oil leakage at the supply pipe tighten the default screw related pipes after that Run the Genset all over genset is okay problem cleared.. | Closed | Mr. MD Saleem | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
81 | South | 211692907 | 07/02/2025 | 25 | GP3.8702.../2421253 | Alarm issue | Closed | Axis Bank Ltd | Surya Power Services - Kalyan Nagar | 8.5 | As per the customer complaint check the engine properly. Problem found in EGR VALUE. so remove the EGR valve connection and connect properly. Using the ikonnect tool to clear the DTC. Check the all parameters of engine found ok.2791/18,2791/1 | Closed | Mr. Anil Kumar H G | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
84 | South | 211690862 | 06/02/2025 | 40 | 3H.8951.../2421455 | Starting/Stopping Issue | Closed | Saasa, | Net Work Diesels - Sholinganallur | 18 | CHECKED THE ALARMS.FOUND EGR VLV MALFUNCTION WARNING IS SHOWING,IKONNECT TOOL IS NOT CONNECTING.CHECK OBD CONNECTOR.FOUND OBD PIN D & C IN LOOSE CONDITION.TEMPORARILY HELD THE CAN WIRES AND CONNECTED THE IKONNECT.CLEARED FAULT CODES.FLASHED THE ECU AS PER RRT RECOMMENDATION.STARTED ANDTESTED THE ENGINE ON NO LOAD AND WITH LOAD.FOUND ENGINE RUNNING HEALTHY,NO ALARM SHOWING RIGHT NOW.AS PER CUSTOMER DEMAND CHANGED THE MAINS UNDER VOLTAGE THRESHOLD AT 160V PH-N AS THIS IS LOW VOLTAGE AREA. | Closed | Mr. NandhaGopal | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
86 | South | 211690655 | 06/02/2025 | 160 | 6H.8475.../2420063 | Battery Charger Alternator issue Call By Customer Name :- Alstan Mobile No :- 9113267044 | Closed | AYATANA HOSPITALITIES PVT LTD COORG | Surya Power Services - Kushalanagara | 484 | Replace the new charging alternator assembly start and run the engine battery charging condition is good replace the item part number 3H.315.01.0.00 | Closed | Mr. Anil Kumar H G | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
91 | South | 211690252 | 06/02/2025 | 250 | F6.8841.../2420259 | Amber Lamp Alarm Call By Customer Name :- Suman ... Mobile No :-9154241020 | Closed | KKG. Electricals | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 17.51 | Checked the Controller in ECU Amber Lamp alarm Showing ECU Internal Fault, so Connect the tool And ECU flashing ok. | Closed | Mr. MD Saleem | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
92 | South | 211689253 | 06/02/2025 | 320 | F6.8802.../2420216 | ITV INLET GAS LEAKAGE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Attended the above site for inlet Throttle Valve(ITV) Gasket Replacement work.Started and inspected the generator and found that air leak noise from the inlet Throttle Valve (ITV) area so removed the ITV assembly and gasket found damaged so replaced the new ITV gasket.Then again started and tested the generator.No air leak noise found. | Closed | Mr. NandhaGopal | [9 empty] | Throttle Valve | 8 | 6 | 5 | 240 | High
72 | South | 211695225 | 08/02/2025 | 40 | 3H.8951.../2520043 | Error code issue Call by : Dealer Name :Prathap Contact :9384374883 customer name:SENTHIL contact number:9524633437 | Closed | SUNBEAM GENERATORS PVT. LTD | Bharath Diesel Sales and Service - Chennai | LR | 97/5, 2791/18,5838/1 error code issue.Checked the harness found ok then clear DTC. Again the EGR related code came so SE visit tomorrow and flash the ECU | Closed | Mr. NandhaGopal | Cut off check | [8 empty] | EGR | 9 | 7 | 5 | 315 | High
41 | South | 211702150 | 10/02/2025 | 125.4 | 4H.8042.C4../2420370 | Fuel Gauge Issue Email by KGD Name - GURUMURTHY | Closed | Nandana Foods Pvt. Ltd. | Surya Power Services - Bangalore | 14 | Observed the fuel level in tank 90% and showing in the controller KG 645 50% only due to fuel gauge stucked.Remove the fuel gauge and refitted same and checked fuel level showing controller and fuel gauge same and started the engine checked working condition ok | Closed | Mr. Anil Kumar H G | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
44 | North | 211719408 | 15/02/2025 | 125.4 | 4H.8042.C4../2420073 | Amber lamp on alarm issue Call by customer Name - Ajay Kumar No - 7518284445 | Closed | SHAKUNTLA SINGH | Deep Jyoti Electricals and Services - Bareilly | 211 | Found ECU flt alarm so, clear the Dtc then found no any alarm | Closed | Sudhir Awasthi | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
6 | East | 211718183 | 14/02/2025 | 15 | GP3.8501.../2421476 | Tripping Issue Call By Customer Name ANKIT KUMAR No : 8084352023 | Closed | ANKIT KUMAR | HACS Engineering and Tech Private Limited - Ranchi | 5.8 | No issue in DG, trip due to unbalance load, so SE suggested to balance the load | CLOSED | Prabhakar Kumar | [9 empty] | Load | 8 | 6 | 5 | 240 | High
19 | South | 211721387 | 15/02/2025 | 40 | 3H.8951.../2420887 | error code problem Call by : Customer Name :Harish Contact :9845595127 | Closed | KNND ASSOCIATES PVT.LTD. | Surya Power Services - Billekahalli | 31 | Controller display showing Maintenance alarm and I open setting and change the Maintenance date and hours and after reset the alarm and after started the engine running condition ok with observations. | Closed | Mr. Anil Kumar H G | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
20 | South | 211721363 | 15/02/2025 | 400 | DV8.8542.C4../2420078 | Starting Problem Call by : Dealer Name : Gaffer Contact : 7660011834 | Task Start | Tellapur Technocity Private Limited | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 29.7 | Check the voltage found ok after giving the load dg working on 50AMP after customer RMC mixer on that time dg 50AMP to 430AMP above load that time dg controller showing under voltage but dg not Stop customer RMC plant panel triping, Panel main mccb triping,mccb is 400AMP , more than 400AMP load taking that time mccb triping, asked customer to inform Panel person. | Closed | Mr. MD Saleem | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
21 | South | 211721320 | 15/02/2025 | 20 | GP3.8601.../2420064 | Maintenance due Call by : Customer Name :Srinivasa Rao Contact :9395500083 | Closed | Camp Office Kits Rmtk | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 138 | Checked the controller on and no switch not working so customer arranged the switch then connected the cabels then started the dg set then checked the found no leakeges checked the dg running condition ok | Closed | Mr. MD Saleem | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
22 | South | 211721008 | 15/02/2025 | 15 | GP3.8501.../2421449 | Automation Issue Call By Customer Name :-Mr. NAGESH Mobile No :- 8121006999 | Closed | Surya Nilayam | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 6.59 | Oil pressure sensor wire loose. Update pending | Closed | Mr. MD Saleem | [9 empty] | Oil Pressure Sensor | 8 | 6 | 5 | 240 | High
28 | South | 211720116 | 15/02/2025 | 20 | GP3.8601.../2421803 | ECU_INDUCEMENT | Closed | MNR GRAND | Laxmi Diesels - Visakhapatnam | 1.46 | ECU MALFUNCTION alarm so check ECU connection and all wiring connecters removed and again connect then start DG running good | Closed | Mr. MD Saleem | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
30 | South | 211719976 | 15/02/2025 | 58.5 | T4.8941.../2422499 | Voltage Fluctuation | Closed | Mkampss N. | Prasad Power Engineers - Mangalore | 19 | Voltage fluctuation for block load .every phase (90 amps). Advised the customer to replace with star delta starter for reduce block load. | Closed | Mr. Anil Kumar H G | [9 empty] | Block Load | 9 | 7 | 6 | 378 | High
34 | South | 211719570 | 15/02/2025 | 45 | 3H.8951.../2421187 | Starting Problem Call by : Customer Name :Prasanth Contact : 9843341615 | Closed | PUSHKARAM AGENCY | Bharath Diesel Sales and Service - Pudukottai | 111 | Check the DG set AMF Panel side auto sensing lines not a corrected, so corrected the AMF Panel side auto sensing lines, than check the DG set working on good in both modes, engine oil level ok belt condition ok Air filter ok battery distilled water level ok coolant level ok control panel side all lines good and power alternator side all lines good than check the DG set working on good in both modes recommended the battery distilled water level and fuel level. | Closed | Mr. NandhaGopal | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
44 | South | 211717678 | 14/02/2025 | 125.4 | 4H.8041.../2420672 | Genset Trip | Closed | BELLEVILLE PRODUCTION HOUSE PRIVATE LIMITED | Surya Power Services - Bommasandra, Bangalore | 38.1 | 3031/14 Error code flash the ECU with dummy file. Now ok. | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
45 | South | 211712756 | 13/02/2025 | 58.5 | T4.8941.../2423274 | Display coolant level is showing low Call by : Customer Name : Ravindra Contact : 9448147838 | Closed | DR.RAVINDRA BHATE | KALA Care Global LLP - Belagavi | 10 | checked all parameters found the coolant level low topup the same and started the dg set in good condition. | Closed | Mr. Anil Kumar H G | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
2 | South | 211729769 | 18/02/2025 | 160 | 6H.8475.../2420091 | Coolant Consumption Problem Call by : Customer Name :Kumar .. Contact :9095810926 | Task Start | SOWPARNIKA PROJECTS AND INFRASTRUCTURE (P) LTD., | Electro Controls-Coimbatore 2 | 97 | 5461/0 Error Code Found Crytal in mixer. Flash the ECU error code is cleared kept this under observation. | Task Start | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
7 | South | 211728917 | 18/02/2025 | 25 | GP3.8702.../2421628 | Electrical Problems | Task Close | St. KURIAKOSE ORTHODOX CHURCH | Electro Controls - Mavalikara | 9 | Checked the engine found emergency stop issue. Automatically sensing the negative pulse to controller and get the engine shut down. Loop additional supply from emergency switch to controller and resolve the issue. Now engine working normally. | Closed | Mr. Sanjaimon S | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
8 | South | 211728847 | 18/02/2025 | 30 | 3H.8902.../2420982 | Under Speed Problem Call by : Customer Name :S.VENKATACHALAM Contact :8124647906 | Task Start | S.Vengatachalam | Bharath Diesel Sales and Service - Puducherry | 13 | Checked the engine fuel line found ok (customer told sometimes only cranking that time alarm under speed control off and on started the engine auto or manual okay condition Crank hold time 5sec to 8 sec increased started the engine on load performance of the DG set found ok | Closed | Mr. NandhaGopal | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
8 | NORTH | 211729103 | 18/02/2025 | 125.4 | 4H.8042.C4../2420374 | Starting Issue & Display Issue Call By Customer Name :- Sanjeev Singh Number:- 7011941076 | Task Start | M/s India International House Ltd | Vidyut Engineers - New Delhi | 2.28 | Found in Controller positive wire was loose tightness the same So, sometimes DG not start | Closed | Kapil Solanki | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
12 | NORTH | 211728686 | 18/02/2025 | 125.4 | 4H.8042.C4../2420500 | Amber Lamp On Alarm Issue Call By Customer Name :- Lalu Number:- 9810130381 | Closed | SHREE NARAYAN PRINTS | Paluck Technologies Ltd. - Ghaziabad | 4 | Found Ecu fault alarm, clear the code & Battery charger connected | Closed | Kapil Solanki | ECU fault check | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
18 | NORTH | 211727554 | 17/02/2025 | 58.5 | T4.8941.../2520017 | Battery Call By Customer Name :- Om prkash . Mobile No :-7838203920 | Task Start | S.K. Generator | Paluck Technologies Ltd. - Faridabad | 140 | Found charging alternator was faulty because check & found outut voltage is 20V, so required to be repaired | open | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
15 | South | 211722599 | 16/02/2025 | 125.4 | 4H.8042.C4../2420295 | Oil Leakage Problem Call by : Customer Name : Shiva Contact : 8790971555 | Closed | Sri Vishnu Ready Mix Concrete | Ultimate Power Source - Nellore | 12 | DEF level low | Closed | Mr. NandhaGopal | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
14 | South | 211722687 | 16/02/2025 | 25 | GP3.8702.../2421390 | Alarm Issue Call By Customer Name: Shibil .. No:-9916247558 | Task Start | MAYURA BAKERY SWEETS AND JUICES | Surya Power Services - Peenya, Bangalore | 94 | 2791/18 , 5838/1 Flash ECU with dummy file | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
11 | South | 211723555 | 17/02/2025 | 125.4 | 4H.8042.C4../2420632 | AMf pannel problem Call by : Customer Name : Kannan Contact : 9443560833 | Task Start | KALYAN JEWELLERS | Madurai Electro Controls - Ramanathapuram | 7 | Visted the site and observed that engine triped due to earth fault. Neutral earthing and ground body earthing arranged improper way. As I informed to customer arranged proper Neutral earthing . Then Earth fault setting is increased current rate10%to 30%.after adjuted the setting.engine trial load condition normal. | Closed | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
8 | South | 211724638 | 17/02/2025 | 25 | GP3.8702.../2520221 | OIL PRESSURE SESOR FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the site noticed the oil pressure sensor failure, change the new oil pressure sensor solve the issue | Closed | Mr. NandhaGopal | [9 empty] | Oil Pressure Sensor | 8 | 6 | 5 | 240 | High
8 | East | 211717682 | 14/02/2025 | 20 | GP3.8604.../2420022 | VOC -Under Voltage Issue Customer Name -Mithlish Customer Number -7667904184 Mode- SR Generated through CDI calling. | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 658 | under voltage alarm was showing due to voltage sensing wire was loose at controller jack so tigthen issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
9 | East | 211717681 | 14/02/2025 | 125.4 | 4H.8042.C4../2420832 | Starting Issue Call By Customer Name - Dayji Number - 6009135708 | Open | Inahoto Yeptho | Hibreed Engineering Pvt. Ltd. - Jorhat | 89 | there was and 516166 code so SE cleared the code, and customer,s query was regarding white smoke but SE checked on no load there was minor white smoke for few second after that it was clear and on load there was no smoke. | OPEN | Ujjwal Das | [9 empty] | Load | 8 | 6 | 5 | 240 | High
10 | East | 211717124 | 14/02/2025 | 320 | F6.8802.../2420110 | Display issue Call by customer Name - Ikramul Hussain No - 7099469939 | Closed | Health Planet. | Hibreed Engineering Pvt. Ltd. - Nagaon | 40 | controller was not getting on, so SE checked voltage at controller 1&2 pin voltage found 0 volt so on inspection found X2(2C-2D) fuse burn because its rating was 2A and in wiring diagram it is recommeded to use 4A so SE replaced it by 4A. | CLOSED | Ujjwal Das | Goem Issue | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
16 | East | 211717445 | 14/02/2025 | 7.5 | D3.8305.../2400088 | Electrical Problems | Task Start | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - BHUBANESWAR | 36 | Customer side issue- unbalance load at certain time R -35 A, Y- 29 A, B- 9 A, suggested customer to distribute the load equally on all phases. | CLOSED | Ujjwal Das | Details Required | [8 empty] | Load | 8 | 6 | 5 | 240 | High
2 | WEST | 211718094 | 14/02/2025 | 125.4 | 4H.8042.C4../2420771 | Voltage Fluctuation issue Email By - KGD Name -Surekha Auti | Task Start | Rani Laxmibai Mulinchi Sainiki Shala & Jr. College | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 21 | load cable loose in AMF panel, tight the cable issue solved. | closed | Jagdeep Saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
6 | WEST | 211710121 |  | 25 | GP3.8702.../2420924 | Starting/Stopping Issue | Closed | ATC Telecom Infrastructure Private Limited | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 4 | controller do not give starting command so flash the controller with new program file, issue solved. | closed | Jagdeep Saini | Details Required | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
10 | WEST | 211720423 | 15/02/2025 | 320 | F6.8802.../2420165 | AIR LEAKAGE FROM ITV | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi | LR | Air was leaking from the throttle valve, so loosened the bolt and tightened it again, but the air leakage was still the same. Valve gasket needs to be replaced | OPEN | Amit Shandilya | [9 empty] | Throttle Valve | 8 | 6 | 5 | 240 | High
5 | East | 211718235 | 14/02/2025 | 125.4 | 4H.8042.C4../2420957 | DG Breakdown | Closed | AIRPLAZA RETAIL HOLDINGS PRIVATE LIMITED | Globalline India Services Private Limited - Siwan | 168 | Low urea level so topup urea and cleared code. customer using another brand urea so recommended customer to use KOEL urea and educated to maintain minimum 50% DEF level. | CLOSED | Prabhakar Kumar | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
11 | WEST | 211719504 | 15/02/2025 | 58.5 | T4.8941.../2422344 | Leakage Issue | Open | SPACE GENERATOR | Unique Techno Services Pvt Ltd. - Hathijan | 310 | There was coolant leakage from the coolant pipe from the EGR side so adjusted the clamp of the pipe but the problem was still there. Used extra clamp. | closed | Amit Shandilya | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
33 | WEST | 211720197 | 15/02/2025 | 30 | 3H.8902.../2421988 | Error Code Issue Call By Customer Name :- Tushar Sir Mobile No :- 9527640951 | Closed | DURGE HOSPITAL | DYNAPULSE ENGINEERING PRIVATE LIMITED - Choufulla,Daund | 2 | code 2791/18 EGR was taken out and cleaned and installed. Checked all the connections of EGR and they are ok. Then flashed the new software to the controller , now dg working ok . | closed | Jagdeep Saini | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
35 | WEST | 211723494 | 17/02/2025 | 250 | F6.8842.C4../2420048 | Red lamp on Alarm Issue. Call By Customer Name :- Santosh Gund Mobile No :-9309982063 | Task Start | Vikasak Vinode Infratech LLP | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 100 | DEF level low so top up DEF level. | closed | Jagdeep Saini | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
40 | WEST | 211727762 | 17/02/2025 | 40 | 3H.8951.../2520054 | Genset Trip | Completed | Blinkit. . | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 23 | Found unbalanced load in customer side , suggest the customer for balance the load. | closed | Jagdeep Saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
2 | NORTH | 211724698 | 17/02/2025 | 250 | F6.8841.../2320035 | Leakage Issue | Closed | PIECO INDIA ENGG CO PVT LTD | OVN Industries Private Limited - New Delhi | 10 | Found air lock in fuel line so, remove the air then issue resolve | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
20 | NORTH | 211722455 | 16/02/2025 | 200 | 6H.8435.../2420226 | Tripping issue Call by customer Name: Maha Singh Number: 9549233209 | Task Start | GURU GOBIND SINGH COLD MILLS | R K Engineers - Meerut | 2 | Found over load on the DG R326 Y319 B318 DG full load capacity 100% 278A 80% 222A Educate the customer For maintain the load According DG capacity | Closed | Sudhir Awasthi | [9 empty] | Load | 8 | 6 | 5 | 240 | High
2 | South | 211725862 | 17/02/2025 | 15 | GP3.8501.../2420778 | Genset Trip | Task Start | COASTAL WOOD RESORTS | Prasad Power Engineers - Udupi | 79 | Dg Tripping due To Over load The. inform the Customer | Task Start | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
5 | South | 211725070 | 17/02/2025 | 30 | 3H.8902.../2421780 | Line Rejection | Task Start | THANIKKAPPILLY FUELS | G-Care Diesels Private Limited - Ernakulam | LR | Attended the site . Inspected dg . Out Cabling and earthing are not done and was is in progress during the last visit hence couldn't commission the dg set. Now checked and load cabling and earthing works are completed.Dg is ready for commissioning. | Closed | Mr. Sanjaimon S | [9 empty] | Load | 8 | 6 | 5 | 240 | High
17 | WEST | 211709779 | 12/02/2025 | 125.4 | 4H.8042.C4../2420584 | Error code issue | Closed | Shri Machineries Stores | Natraj Power Tech - Chhindwara | 84 | Low DEF level | closed | Vijay Patil | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
25 | NORTH | 211726002 | 17/02/2025 | 58.5 | 6H.9840.../2420007 | Under Speed Alarm Issue Call By Customer Name :- M. D Afroj Number:- 8700479015 | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 12 | DG start check Red lamp - on alarm show on EMS DG trip check engine fuel value unload 52 so zpr se engine fuel value set ke 19 and DG on Load start check engine fuel value 40 DG normal (jark load and over load) | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
35 | South | 211705304 | 11/02/2025 | 125.4 | 4H.8041.../2420852 | Starting/Stopping Issue | Closed | K. V. G. Bank. | KALA Care Global LLP - Hubli | 40 | As per the customer's complaint, we attended and observed the DG was not started because the off-relay negative command was not coming to the ECU And then replaced the ECU connection cleaned it, then cleaned the battery terminals and then connected the cable and then started the dg running is good. | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
27 | South | 211707607 | 11/02/2025 | 10 | GP3.8301.../2420145 | Starting Problem Call by : Customer Name : Abrahan Contact : 7760093774 | Task Start | HILLCREST HAVEN | Electro Controls - Thodupuzha |  | 2791/0 Error code issue. Flash the ECU | Task Start | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
12 | North | 211694426 | 07/02/2025 | 160 | 6H.8475.../2420015 | Sound/Vibration Issue | Task Start | Lala Gela Ram Memorial Charitable Dental Hospital Society | OVN Industries Private Limited - New Delhi | 28.7 | Found fan belt loose tightness the same & top up the Def | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
14 | North | 211693897 | 07/02/2025 | 58.5 | T4.8941.../2421327 | Fuel Sensor Issue Email By - KGD Name -Rajesh Aggarwal | Task Start | Germinal Technologies P. Ltd. | Paluck Technologies Ltd. - Faridabad | 408 | Fuel level not proper showing the level, then remove the Fuel sensor & clean after refitted then issue resolve | Closed | Kapil Solanki | [9 empty] | Fuel Sensor | 7 | 6 | 5 | 210 | High
19 | North | 211693499 | 07/02/2025 | 500 | DV8.8501.C4../2420129 | Urea Alarm Issue & Power Supply Issue Call By Customer Name :- Anil Kumar Mobile No :-8427280370 | Task Start | S. S. Enterprises | Pratap Diesels Pvt. Ltd. - Bhiwadi | 95 | DM not proper working, Coolant line clamp was defective EDO for same | open | Gourav Sharma | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
24 | North | 211692641 | 07/02/2025 | 58.5 | T4.8941.../2420811 | Battery charging issue Call By Customer Name :- Ram Saran Mobile No :-7982975198 | Task Start | SETHI BUILDCON | Vidyut Engineers - New Delhi | 932 | Found Charging alternator fuse was foulty, so, replace the same | Closed | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
26 | North | 211691878 | 07/02/2025 | 160 | 6H.8475.../2420124 | Overheating issue | Closed | St. Aloysius High School. | Espiem Engines & Machines (P) Limited - KANPUR | 49 | Found low DEF level & Coolant level low in Recovery bottle, topup the DEF & Coolant then issue resolve | Closed | Sudhir awasthi | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
28 | North | 211691874 | 07/02/2025 | 125.4 | 4H.8042.C4../2420439 | Starting isuue Email By - KGD Name -Pradeep Tyagi | Task Start | Vasundhara Real Estates | Espiem Engines & Machines (P) Limited - Aligarh | 2 | Before a day DG commissioning, but Load cable not given from customer end & not the load trial aftyer a day load trial then he found NCD lamp burnt & controller display was blank & one connector was stick to controller | open | Sudhir awasthi | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
29 | North | 211691714 | 07/02/2025 | 125.4 | 4H.8042.C4../2420566 | Amber Lamp Alarm Issue Call By Customer Name- Pramod Verma Mo.No.- 9953272817 | Closed | DUTTA ENGG. WORKS | Paluck Technologies Ltd. - Faridabad | 23.34 | Low Adblue level, topup the def then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
30 | North | 211691655 | 07/02/2025 | 125 | F6.9840.../2420006 | Electrical Problems | Closed | C. S. Export | Vidyut Engineers - Noida | 51.52 | Found R phase fuse was defective replace the same then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
31 | North | 211691612 | 07/02/2025 | 160 | 6H.8475.../2420025 | Tripping issue Call By Customer Name :- Mustak Mobile No :- 9058614379 | Task Start | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 2280 | found charge fail, water in fuel,low addblue level ,ecu flt. Clean water from water sprater and v belt found loose tighten belt and alarm released from controller (Update pending) | open | Kapil Solanki | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
42 | North | 211695381 | 08/02/2025 | 58.5 | T4.8941.../2422811 | Tripping Issue Call By Customer Name :- Om Prakash Mobile No :-9927082889 | Closed | HANU DIAGNOSTIC CENTER | Espiem Engines & Machines (P) Limited - Agra | 54 | Found Air lock in fuel line remove the air & Service done | Closed | Sudhir awasthi | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
43 | North | 211695380 | 08/02/2025 |  | GP3.8702.../2520002 | Coolent Leakage issue | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | LR | Engine EGR coolant leakage from Coolant tube because o' ring was defective Now, send in GOEM | open | Sudhir awasthi | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
45 | North | 211695226 | 08/02/2025 | 200 | 6H.8435.../2420243 | Lamp on alarm Call by Customer Name : SHIVRAJ .. No : 8869907969 | Closed | Sri Chaitanya Seva Trust | Espiem Engines & Machines (P) Limited - Agra | 91 | Low Adblue level, topup the def then issue resolve | Closed | Sudhir awasthi | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
52 | North | 211693898 | 07/02/2025 | 15 | GP3.8501.../2420293 | Starting/Stopping Issue | Closed | Dr. Sandeep Malik. | SAAN Royal Power Solutions Private Limited - Hisar | 37 | Emergency stop alarm occurred ; NO & NC not working so bypass the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
53 | North | 211693472 | 07/02/2025 | 125.4 | 4H.8042.C4../2420956 | Leakage Issue | Closed | FANCY ENTERPRISES | Industrial Power Solutions - LUDHIANA | 19 | AdBlue leakage found due to DEF Tank Cap was not fitted after top-up the AdBlue by customer so same educated to customer | Closed | Ved Prakash Gupta | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
59 | North | 211692033 | 07/02/2025 | 500 | DV8.8501.C4../2420170 | Nox Upsttream issue | Task Start | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - kathua | 12 | Nox Upstream alarm occurs as soon as load reachs more than 100%,after replacement of sensor,wiring harness,DEF Line,silencer one by one issue remains same | Open | Ved Prakash Gupta | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
10 | North | 211686653 | 05/02/2025 | 125.4 | 4H.8041.../2320128 | Red lamp alram Call By Customer Name :- Yogesh . Mobile No:-8512095633 | Closed | KALYAN JEWELLERS INDIA LTD | OVN Industries Private Limited - New Delhi | 52.2 | Low Adblue level, topup the def then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
24 | West | 211691803 | 07/02/2025 | 500 | DV8.8501.C4../2420153 | Coolant Leakage Issue Email By - OEM Name -PAREKH | Task Start | Parekh Power Systems | Unique Techno Services Pvt Ltd. - Ankleshwar | 2 | Coolant leakage from dosing module. | Closed | Amit Shandilya | [9 empty] | Dosing Module | 8 | 6 | 5 | 240 | High
22 | West | 211693320 | 07/02/2025 | 5.5 | CC1.1013.../2400728 | Oil Leakage Issue Call By Customer KGD Name :- Satyam Satyam Mobile No :- 8448441908 | Closed | Ruhe Solutions Pvt. Ltd | Unique Techno Services Pvt Ltd. - Hathijan | 1.5 | Fuel leakage from fuel pipe bolt so tightened the same. | Closed | Amit Shandilya | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
10 | West | 211685448 | 05/02/2025 | 15 | GP3.8501.../2420546 | Starting/Stopping Issue | Closed | CUPID Limited | Dhanashree Technocrats Pvt. Ltd. - Nasik | 1449 | Attend site and replace new ECU due to fast crank time actuator rack stuck.started DG set found satisfied. | Closed | Jagdeep saini | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
19 | North | 211682540 | 04/02/2025 | 500 | DV8.8501.C4../2420041 | Low Coolant Level Issue & Starting Issue Call By Customer Name :- Sureshwar Mobile No :- 8130181206 | Task Start | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 4 | found coolant level low then top up coolant and file flashing ECU and DCU after that engine start and checked again engine found normal working with load | open | Kapil Solanki | ECU fault check | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
8 | East | 211684960 | 05/02/2025 | 30 | 3H.8902.../2420147 | Starting issue Call by customer Name: Pappu Kumar Das Number: 7002239755 | Task Start | M/s. Anupam Nirman P. Ltd. | Hibreed Engineering Pvt. Ltd. - Jorhat | 763 | 5838/1, 2791/31, 5838/3 code triggered on the display, so he check EGR to ECU continuity found ok voltage was also OK and also find EGR ok by removing it so he flashed the ECU by normal file code, cleared checked for 2-3 times found ok. | CLOSED | Ujjwal Das | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
1 | West | 211651452 | 28/01/2025 | 7.5 | D3.8305.../2400109 | engine oil leakakge problem | Closed | TMI Solutions. | Shree Engineering Service - KORBA | 26 | oil throw from breather at 13 amp load, engg run the engine approx 1 hrs but no oil throw observed. | Closed | Vijay Patil | Under Observation | [8 empty] | Load | 8 | 6 | 5 | 240 | High
3 | West | 211642869 | 25/01/2025 | 58.5 | T4.8941.../2422973 | Error Code Issue And MIL Lamp On Alarm Call By Customer Name :- Nikhi Mobile No :-9823983099 | Task Start | OMKAR ENTERPRISES | Transcreek Engineers Pvt. Ltd. - Wadkhal |  | EGR jammed issue 2791/18, customer is not agree to do any activity. | OPEN | Jagdeep Saini | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
1 | South | 211688897 | 06/02/2025 | 40 | 3H.8951.../2421632 | Under Speed Problem Call by : Customer Name :REGUNATHAN Contact :9447330310 | Task Start | IRIS,CHATHANNOOR | EMKAY MOTORS - Kollam | 15 | 2791,18- Engine Exhaust Gas Recirculation 1 Valve 1 Control 1-Low - moderate severity visit the site check allover engine,no under speed alarm in historyfound an alarm egr valveclear the alarm through controllerstart the engine found ok | Tast Start | Mr. Sanjaimon S | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
5 | South | 211688582 | 06/02/2025 | 15 | GP3.8501.../2420616 | Starting/Stopping Issue | Task Start | Amble Apartment. | G-Care Diesels Private Limited - Calicut | 49 | Run the engine found main alternator out put voltage low so adjusted voltage in AVR , checked engine rpm,hz,load after found ok engine at under observation. | Tast Start | Mr. Sanjaimon S | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
10 | South | 211688270 | 06/02/2025 | 82.5 | 5H.8901.../2420150 | Error code problem Call by : Customer Name : Satya Contact : 7702128945 | Task Start | Indian Red Cross Society. | Laxmi Diesels - Vizianagaram |  | 516166,0- ECU Fault-High - most severe . KRM Checked this fault code Active. Engineer visit pending. | Tast Start | Mr. MD Saleem | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
60 | North | 211691489 | 07/02/2025 | 35 | 3H.8902.../2421636 | Inspection/Maintenance | Task Start | RAYOU CONSTRUCTIONS PVT LTD | Suraj Motor Store - Jammu | 214 | Starting Issue , Checked & found DIG O/P connection on controller at 3 No. found loose so re-connected the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
13 | South | 211687978 | 06/02/2025 | 20 | GP3.8601.../2420497 | Starting Problem Call by : Customer Name :Raj kumar Contact :8608924888 | Completed | Meras Plugins Pvt. Ltd. | Net Work Diesels - Chennai | 56.5 | FOUND KG 645C SHOW RED LAMP ALARAM DUE TO EMERGENCY SWITCH ACTIVATED SO REALISED EMERGENCY SWITCH STARTED AND TESTED THE ENGINE WITH LOAD RUNNING PERFORMANCE SATISFACTION | Closed | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
26 | South | 211685156 | 05/02/2025 | 15 | GP3.8501.../2420605 | Inspection/Maintenance | Closed | Saju Paul | G-Care Diesels Private Limited - Ernakulam | 12 | Attended the site . Dg is shifted from another site .so customer need commissioning. As per the cute demand inspected the dg. Dg premises are neat and clean. Have sufficient ventilation. Dg is placed on a concrete structure. checked earth pits . informed customer to disconnect the interlinking between th earth pits. Canopy have no damages. All doors Hinges and locks are ok. Then checked engine oil ,level and condition is ok. coolant is at the required level in both radiator and compensatory bottle. Belt tension and air filter is good. Battery condition is ok. Earthings are ok. All foundation bolts checked . Radiator condition is ok.Fuel hoses , radiator hoses oil ,supply pipes ,hose clips are ok. Control panel wirings ,avr ,sensor wirings ,ecu all other wirings are educated customer about the dos and don'ts. Then started the dg and tested without load. no abnormal noise, hunting or leaks . Engine parameters and dg parameters are ok. Dg voltage, frequency are ok. exhaust smoke is ok.Thy load applied. But dg is overloaded. And reduced load to the safe load. Informed customer to keep the total load to the dg as per the rating. Other wise breakdown may occur.Now the dg is running normally.performance is good. | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | East | 211686858 | 05/02/2025 | 82.5 | 5H.8901.../2420453 | Amber red lamp alarm issue Called by customer Name : BIKASH Number : 9874144042 | Open | POWERMECH DIESELS | HACS Engineering and Tech Private Limited - Deoghar | 65 | Low adblue level alarm pop-up on display so on telephonic communication dealer told to topup operator topup about 10 Ltr urea but code was not clearing and when SE visited found DEF level only 35% so se checked the LQT sensor float and wash it by hot water and refittedproperly LQT sensor and it's connector the. found DEF level OK 80% issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
1 | WEST | 211678748 | 03/02/2025 | 125 | F6.9840.../2420009 | Automation Issue Call By Customer Name Manoj Jaiswal No : 9174153636 | Closed | Paras Auto Electricals | Natraj Power Tech - Bhopal | 52 | Customer complain that engine not start in the morning . SE checked the fuel line found ok but SE do not found any issue. Under observation. | OPEN | Vijay patil | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
6 | WEST | 211685166 | 05/02/2025 | 0 | T4.8941.../2422819 | WIRING HARNESS ISSUE | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | lR | Engine wiring harness connector wire was back out from its position so replaced the wiring. | Closed | Jagdeep saini | Vendor issue. | [8 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
1 | West | 211661551 | 30/01/2025 | 500 | DV8.9313.../2420037 | Throttle valve failure | Completed | RCF Kapurthalla | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 18 | Throttle valve pin damaged need to replace. | Closed | Jagdeep saini | [9 empty] | Throttle Valve | 8 | 6 | 5 | 240 | High
2 | West | 211666151 | 31/01/2025 | 500 | DV8.9313.../2400002 | Starting Problem | Task Start | RAIL COACH FACTORY RCF | Transcreek Engineers Pvt. Ltd. - Mumbai | 643 | Rail pressure sensor malfunctioning so replace with another on issue resolved. | Closed | Jagdeep saini | [9 empty] | Rail Pressure Sensor | 9 | 7 | 6 | 378 | High
9 | West | 211692147 | 07/02/2025 | 15 | GP3.8501.../2420886 | Leakage Issue | Closed | Shriram Petroleum | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | FUEL LEAKAGE FROM FUEL FILTER O RING , change the o ring. | Closed | Jagdeep saini | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
15 | South | 211687863 | 06/02/2025 | 0 | 4H.8042.C4../2421094 | ABNORMAL NOISE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected the dg notice the abnormal noise come from alternator (rubbing noise) side and burning smell | Tast Start | Mr. NandhaGopal | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
34 | South | 211705878 | 11/02/2025 | 58.5 | T4.8941.../2422697 | Starting/Stopping Issue | Task Start | Malli sai enterprises | Ultimate Power Source - Nellore | 3 | Visit the DG set ok checked oil level and filters condition ok battery digital water ok coolent level found ok checked all parameters working ok alaram ecu fault now we flash the ECU now working is fine | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
1 | East | 211695292 | 08/02/2025 | 20 | GP3.8604.../2420022 | INSATANCE ID:-100740957 SITE ID:-I-BR-JGDS-ENB-G002 CALL BY CUSTOMER:- DG ISSUE :-DG FUEL SENSOR FAULTY NAME:-Mrityunjay Singh NUMBER :-7667904184 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 650 | SE visited site and found fuel sensor issue, as per mechanical gauge its fuel was above 50% but in display found 20% and it was fluctuating frequently 40-15% so checked all connection related to the fuel sensor and found its fuel sensor connector was notproperly fitted so reconnected properly issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | Fuel Sensor | 7 | 6 | 5 | 210 | High
9 | East | 211685154 | 05/02/2025 | 20 | GP3.8604.../2420110 | RPM Issue | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Bhagalpur | 123 | Due natural disaster ( flood) DG submegerd in waterdue to which it cause an breakdown like its alternator got defective, starter motor, wiring harness, ECU,so on paid basis DG has been restored.After few Days DG was not starting showing under speed alarm so SE on inspection found its electric feed pump not working so it has been also replaced after that issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
1 | North | 211707867 | 11/02/2025 | 58.5 | T4.8941.../2421614 | Loading issue Call By Customer. Name:- Abhishek Mobile No.:-8550048008 | Task Start | Hotel Gurukripa INN. | Espiem Engines & Machines (P) Limited - Agra | 38 | Found Over current alarm in Event log, due to Unbalance load, same Educate the customer for balance the Load | Closed | Sudhir Awasthi | [9 empty] | Load | 8 | 6 | 5 | 240 | High
10 | North | 211706117 | 11/02/2025 | 750 | DV2.8501.C4../2420068 | Alarm Issue & Canopy Issue Call By Customer Name : Deepak No : 9588764272 | Task Start | Ace Power Management. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 11 | Found Multiple fault code After that flash the ECU & DCU then issue resolve | Closed | Kapil Solanki | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
14 | North | 211705856 | 11/02/2025 | 20 | GP3.8601.../2421130 | Starting Issue Call By Customer Name :- Satvenda , Mobile No :- 9926477553 | Closed | MR AMAN KUMAR | GLOBALVISION POWER SOLUTIONS PVT LTD - DEHRADUN | 11.4 | We found controller switch on wire damaged at site . We reconnect the fault wire . | Closed | Sudhir Awasthi | GOEM issue | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
17 | North | 211705795 | 11/02/2025 | 30 | 3H.8902.../2420045 | Starting/Stopping Issue | Closed | Jupiter Wheels Private Limited | OVN Industries Private Limited - New Delhi | 47 | Maintenace due alarm reset & Air lock in fuel line so, remove the air, Service due | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
18 | North | 211705743 | 11/02/2025 |  | 3H.8902.../2421133 | CONTROLLER DISPLAY ISSUE | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Found Controller display not working, so, replace the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
30 | North | 211703678 | 10/02/2025 | 500 | DV8.8501.C4../2320030 | Starting/Stopping Issue | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2255 | Found in Controller 18 no. wire was removed so, connect the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
34 | North | 211701610 | 10/02/2025 | 125.4 | 4H.8042.C4../2420013 | Inspection/Maintenance | Closed | BABA AMARNATH ENTERPRISES | Pratap Diesels Pvt. Ltd. - Bhiwadi | 516 | Low def level alarm after that clear the code & topup the DEF then issue resolve | Closed | Gourav Sharma | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
47 | North | 211708574 | 12/02/2025 | 125.4 | 4H.8041.../2420118 | Starting/Stopping Issue | Closed | Swastham Medicare LLP. | Vidyut Engineers - Noida | 227 | found DG set not starting Due to fuel motor DC supply wire thimbal broken After that We change the thimbal Re fitted the wire | Closed | Kapil Solanki | [9 empty] | Motor | 9 | 6 | 7 | 378 | High
9 | East | 211709511 | 12/02/2025 | 25 | GP3.8702.../2420896 | Genset Trip | Task Start | MAA TARINI ROLLER FLOUR MILLS LLP | Gangpur Sales and Services - BHUBANESWAR | 105 | Customer side issue- unbalance load at certain time R -35 A, Y- 29 A, B- 9 A, suggested customer to distribute the load equally on all phases. | CLOSED | Ujjwal Das | [9 empty] | Load | 8 | 6 | 5 | 240 | High
11 | South | 211710033 | 12/02/2025 | 25 | GP3.8702.../2421976 | AMF Pannel Problem Call by : Customer Name :MANIVASAGAM Contact :9840245980 | Completed | Manimozhi M | Net Work Diesels - Chennai | 5 | FOUND VOLTAGE ISSUE B PHASE FUSE FAILURE AND HOLDER LOOSE.CORRECTED THE SAME.REPLACED NEW FUSE.STARTED AND TESTED THE ENGINE WITH LOAD IN AUTO AND MANUAL MODE.FOUND ENGINE RUNNING PERFORMANCE SATISFACTORY. | Closed | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
12 | South | 211710008 | 12/02/2025 | 82.5 | 5H.8901.../2420356 | Error code | Closed | JR Garments., | Bharath Diesel Sales and Service - Dharmapuri | 34 | Checked the DG now dm2 error code(1761/16) addblue low and def tank add blue level 80 % so error code cleared and explain to customer side def tank level 50% above pls maintain and oil v belt coolant all hose and clips checked found ok started the engine found normal condition no leakage of air fuel oil and coolant performance of dg found normal condition | Closed | Mr. NandhaGopal | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
16 | South | 211709526 | 12/02/2025 | 5.5 | CC1.1013.../2400671 | Starting Problem Call by : KGD Name : Faizal Contact :9003012190 customer name: Syed Altaf Hussain contact number :9566230075 | Closed | Dr. Syed Altaf Hussain | Madhu Engineering Sales & Service - Teynampet,Chennai | 1.6 | Visit the site.check and analysis control panel board controller and Engine all parameters.checked dg auto start issue.analysis and checked dg control panel board ATS interface connected wiring issue due to damages so this problem so explain the customer need to be propper connection the ATS interface connection.also checked Engine all parameters and all safety function good.dg manual start stop running load trail found ok.dg running time noise and smoke and Vibration good.no leakages. | Closed | Mr. NandhaGopal | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
18 | South | 211709367 | 12/02/2025 | 58.5 | T4.8941.../2421934 | Output Supply issue Call By Customer Name :- Kamlesh Mobile No :- 9799498491 | Task Start | PRADEEPRAJ INFRA PRIVATE LIMITED | Sri Manjunath Technical Services - Ongole | 2056 | attend the check the dg dg is not starting..charge fail alarm.charaging alternator green colour wire clip loose contact I addjted the clamp and remove the battery wires and fitting the battery wires problem is ok start the dg checking all lekages and battery water check and belt and lub oil level check all electrical wire tight all parameters is ok engine condition ok | Closed | Mr. MD Saleem | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
20 | South | 211709266 | 12/02/2025 | 20 | GP3.8601.../2420619 | Electrical Problems | Closed | S. S. Logistics. | Bharath Diesel Sales and Service - Pattanur | 33 | (2791/5)Inspected the dg check the EGR value voltage ok , so flash the ecu after check the error code clear | Closed | Mr. NandhaGopal | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
22 | South | 211709062 | 12/02/2025 | 58.5 | T4.8941.../2422524 | LINE REJECTION | Task Start | Renukayalamma Sabha Bhavana | Prasad Power Engineers - Hassan | LR | Visited the site and check the engine then check the earthing connection earthing is not done then load cable work also pending panel board wiring also pending that 's why iam not complete this genset commissioning | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
7 | West Zone | 211704626 | 11/02/2025 | 400 | DV8.8542.C4../2420132 | RELAY CARD PROBLEM | Task Start | Radiant Power Projects | Unique Techno Services Pvt Ltd. - Baroda | LR | Engineer visited site and found that feed pump was not working after override. Controller did not show any fault code. Checked interface card and found RL1 (ECU main relay) coil supply is ok but switch point was not closing so relay was bypassed. The interface box needs to be replaced. (Egnition supply was not receving to ECU) | OPEN | Amit Shandilya | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | West Zone | 211698996 | 10/02/2025 | 160 | 6H.8475.../2420199 | Error Code issue Call By service dealer Name: : Hasmukh No : 7574845904 | Closed | V.S.SHAH & CO. | Unique Techno Services Pvt Ltd. - Baroda | 296 | Low DEF level and replaced the V belt. | CLOSED | Amit Shandilya | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
2 | West Zone | 211699270 | 10/02/2025 | 30 | 3H.8902.../2420462 | Tripping issue Call by Customer Name : Ramesh .. No 7202990873 | Closed | Rameshbhai Bhikhabhai Parmar | Unique Techno Services Pvt Ltd. - Baroda | 64 | Genset trip due under speed. The fuse of the controller voltage sensing line (RG1) was blown. | CLOSED | Amit Shandilya | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
1 | West Zone | 211703660 | 10/02/2025 | 750 | DV2.8501.C4../2420039 | STARTING ISSUE | Task Start | Bharat Petroleum Corporation Ltd. Madhya Pradesh | Natraj Power Tech - Indore | LR | Smoke issue. Oil/other fluid was coming from A bank exhaust side, so opened the nox sensor and found it was wet. Opened the rocker cover and found the valves were okay and took the exhaust manifold apart, exhaust manifold was dry and checked the turbo and found it okay. Nox value was showing -12PPM. Fitted all systems and took a trail, but no smoke. Need to replace the nox sensor and suspect dosing module. | OPEN | Vijay Patil | [9 empty] | NOx Sensor | 9 | 7 | 6 | 378 | High
5 | North | 211699601 | 10/02/2025 | 250 | F6.8841.../2320013 | Starting Issue Email by Customer Name - GAYATRI | Task Start | Gayatri Construction Machinery | Pratap Diesels Pvt. Ltd. - Bhiwadi | 436 | Found Radiator was chocked, send the quatation to the Customer & ECU amber lamp on clear the code then issue resolve | Closed | Gourav Sharma | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
13 | North | 211698851 | 10/02/2025 | 125.4 | 4H.8041.../2420510 | Starting/Stopping Issue | Task Start | SUNLIGHT ENGINEERS | OVN Industries Private Limited - New Delhi | 42.32 | Found air lock in fuel line so, remove the air then isssue resolve | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
15 | North | 211698217 | 09/02/2025 | 500 | DV8.8501.C4../2420105 | Urea Alarm Issue Call By Customer Name - Anuj Number - 8930203483 | Task Start | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4.8 | Low DEF level alarm reset the alarm with i-konnect tool then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
16 | North | 211698230 | 09/02/2025 | 500 | DV8.8501.C4../2420055 | Over Current Issue & Over Voltage Issue Call By Customer Name - Anuj .. Number - 8930203483 | Task Start | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 6 | Low DEF level alarm reset the alarm with i-konnect tool then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
17 | North | 211698215 | 09/02/2025 | 500 | DV8.8501.C4../2420013 | Over Current Issue & Over Voltage Issue Call By Customer Name - Anuj ... Number - 8930203483 | Task Start | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | Low DEF level alarm reset the alarm with i-konnect tool then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
18 | North | 211698205 | 09/02/2025 | 125.4 | 4H.8041.../2420215 | Alarm problem | Task Start | SM Partners | Vidyut Engineers - Noida | 15 | DM not sprey the DEF then check the physically after that found low load then Increase the load after that sprey the def & Clear the Error code | Closed | Kapil Solanki | ECU fault | [8 empty] | DEF | 8 | 7 | 5 | 280 | High
5 | East | 211698837 | 10/02/2025 | 58.5 | T4.8941.../2420350 | Under Speed Alarm Issue Call By Service Dealer Name :- Vikas Pradhan Mobile No :-8917400481 | Closed | Tulsi Nxt | Gangpur Sales and Services - Bhawanipatna | 108 | Customer side issue- unbalance load at certain time R -35 A, Y- 29 A, B- 9 A, suggested customer to distribute the load equally on all phases. | CLOSED | Ujjwal Das | [9 empty] | Load | 8 | 6 | 5 | 240 | High
2 | East | 211693964 | 07/02/2025 | 20 | GP3.8604.../2420021 | EB Contactor Faulty | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Bhagalpur |  | Customer have 53 Ampere load instead MC contactor burn out, as per SE voice root cause suspected root cause may be due to mains surge voltage, but found OK. | OPEN | Prabhakar Kumar | [9 empty] | Load | 8 | 6 | 5 | 240 | High
6 | East | 211698024 | 09/02/2025 | 125.4 | 4H.8041.../2420627 | Starting Issue Call by customer Name :- Rajesh Roy No :- 9337241741 | Open | TRILOKNATH ENTERPRISES | Gangpur Sales and Services - Berhampur | 12 | 2791/31code triggered on the display, so he check EGR to ECU continuity found ok voltage was also OK and also find EGR ok by removing it so he flashed the ECU by normal file code, cleared checked for 2-3 times found ok. | CLOSED | Ujjwal Das | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
4 | North | 211704893 | 11/02/2025 | 30 | 3H.8902.../2421747 | AUTOMATION ISSUE | Closed | Gurudwara Singh Sabha Dhanipind | Dynamic Engineering Services - Jalandhar | 3 | Auto starting issue due to mains supply installed from customer side single phase but in controller,setting was for three phase so change the setting tosingle phase & started DG in Auto mode,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
7 | North | 211704715 | 11/02/2025 | 500 | DV8.8501.C4../2320044 | Trip_Genset_High_Voltage | Closed | Veer Rice & General Mill, | SAAN Royal Power Solutions Private Limited - Karnal | 164 | On site,found DG reverse current after started DG so reset the controller & resolve the issue , customer's Solar pannel neutral common with DG | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
9 | North | 211702358 | 10/02/2025 | 15 | GP3.8501.../2420433 | Leakage Issue | Task Start | Hardeep Singh. | Megatron Engineers - Pathankot | 2.37 | Fuel leakage found on fuel suction line near DC Motor,clkamp found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Motor | 9 | 6 | 7 | 378 | High
10 | North | 211702350 | 10/02/2025 | 58.5 | T4.8941.../2520157 | Black smoke issue Call By Customer Name :- RAVI Mobile No:-9018466062 | Task Start | RAVI | Suraj Motor Store - Jammu | 10 | Black smoke issue , Check filters condition,found ok,checked Load found Load was low(1.5 KW) , so same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
9 | East | 211699349 | 10/02/2025 | 5.5 | CC1.1013.../2400366 | Abnormal voice issue Call by Customer Name : Himanshu Barik No 7848976414 | Task Start | Creative Image | Gangpur Sales and Services - BHUBANESWAR | 69 | Engine RPM was not going above 3000 and shutdown due to Under Speed Alarm and on running condition there was an abnormal sound at some where cylinder so after overhauling of head found the Piston's compression ring was not installed properly after that Piston,Piston O Ring,Bearing,Head Gasket ,Fuel Pump, Specail tool for opening fly wheel under EDO. | OPEN | Ujjwal Das | [9 empty] | Fuel Pump | 8 | 6 | 5 | 240 | High
10 | East | 211699129 | 10/02/2025 | 40 | 3H.8951.../2421575 | LINE REJECTION | Task Start | MANOJ KUMAR BARIK | Gangpur Sales and Services - Dhenkanal | 111 | There was no issue in DG as on first visit it was noticed that customer was using and 4mm sqr. cable use for welding machine operation and was approx. 30m long so at DG end alternator output voltage was 230 P-N but at end of load cable it was droppig to 180-170V so recommened to use 16 mmsqr. load cable after that when he start doing welding(1 phase machine) it operate for 5-6 min properly but after that welding machine doesnot operate/its elctrode does not flash and that time DG load does not cross 10 A load(but main point was that there was no any issue in DG because no hunting or rpm drop that time) after that further visit customer change the welding machine then tested DG found ok its suspected that there was and issue in customer,s welding machine | OPEN | Ujjwal Das | GOEM issue oil leakage | [8 empty] | Alternator | 7 | 5 | 6 | 210 | High
|  | 211705742 | 11/02/2025 | 125.4 | 4H.8041.../2320003 | Battery charge Issue Call By Customer Name :- Laksh Deka Mobile No:-7002690283 | Task Start | N.K. CONSTRUCTION & SUPPLIERS | Hibreed Engineering Pvt. Ltd. - Nagaon | 152 | Battery not charging issue - DG charging alternator fuse burn out after replacing issue resolved | CLOSED | Ujjwal Das | 4/7/2024 12:00:00 AM/ revalidation | 10/1/2025 11:59:00 AM Paid CSP | [7 empty] | Alternator | 7 | 5 | 6 | 210 | High
7 | East | 211696445 | 08/02/2025 | 15 | GP3.8501.../2420151 | Starting Issue & Emergency Stop Alarm Call By Customer Name :- Santosh Mobile No :-9658166969 | Open | M/S MAHARISHI RAM RAJ TRUST | Gangpur Sales and Services - BHUBANESWAR | 37 | SE check the DG.found the engine not getting start.due to emergency stop alarm.Then emergency alarm clear.all nut bolt ok.condition & vbelt ok.start the engine ok.load ok.running ok. | OPEN | Ujjwal Das | [9 empty] | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
11 | North | 211684329 | 05/02/2025 | 125.4 | 4H.8042.C4../2420513 | Maintenance due alarm Call By Customer Name Vijay Singh No : 9650783688 | Task Start | Krishna Build Estate Pvt Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 283 | Low def level so, top up the def then issue resolve clear the fault code | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
29 | North | 211729846 | 18/02/2025 | 82.5 | 5H.8901.../2320117 | Leakage Issue | Completed | The Hosteller Hospitality Private Limited | SAAN Royal Power Solutions Private Limited - Mandi | 117 | Coolant leakage found due to clamp found loose (Update Pending) | Open | Ved Prakash Gupta | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
33 | North | 211728647 | 18/02/2025 | 160 | 6H.8475.../2420105 | Fuel sensor issue | Closed | TROLLTECH ENGINEERING WORKS REG | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 327 | Fuel Level was variable showing on controller so open the guage & re-fitted,Issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
9 | North | 211754438 | 25/02/2025 |  | 4H.8042.C4../2520129 | STARTING ISSUE | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | found charging alternator wiring wrong connected change wiring w terminal to ig connector | Closed | Gourav Sharma | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
13 | North | 211754028 | 25/02/2025 | 125.4 | 4H.8042.C4../2520140 | CHARGING ISSUE | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | found charging alternator wiring wrong connected change wiring w terminal to ig connector | Closed | Gourav Sharma | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
14 | North | 211754012 | 25/02/2025 | 125.4 | 4H.8042.C4../2520131 | CHARGING ISSUE | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | found charging alternator wiring wrong connected change wiring w terminal to ig connector | Closed | Gourav Sharma | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
15 | North | 211753993 | 25/02/2025 | 40 | 3H.8951.../2320033 | White Smoke Issue Call By Customer Name :- Bajrang Bahadur Singh Mobile No:-9868356329 | Closed | Bajrang Singh | Vidyut Engineers - Noida | 201 | Found Unbalance load on the DG same Educate the customer for balancing the load | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
17 | North | 211753593 | 25/02/2025 | 20 | GP3.8601.../2421733 | Smoke Problem | Closed | S. R. Power Engineers | Vidyut Engineers - Noida | LR-2 | Main fuel line check found pipe was loose so, tightness the same then issue resolve | Closed | Kapil Solanki | GOEM issue | [8 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
27 | North | 211752362 | 24/02/2025 |  | DV8.8501.C4../2420298 | LINE REJECTION | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | 2 | Coolant level switch was faulty after replace the switch issue resolve | Closed | Gourav Sharma | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
30 | North | 211749789 | 24/02/2025 |  | 3H.8902.../2520051 | VOLTAGE FLAXIATION | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | 1 | Check the main alternator found AVR was faulty so replace the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
4 | West | 211716720 | 14/02/2025 | 50 | T4.8941.../2423324 | ENGINE NOT STARTING | Task Start | Bharti Airtel Limited | Shree Engineering Service - Satna | LR | Yesterday SE visited on site with controller & fitted it. But issue was same " Under speed" alarm. So after dissabled the Under Speed in controller, DG started but communication error was persisted. Engineer will visit today again. Control panel drawing required. | open | Vijay Patil | Panel drawing from GOEM | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
5 | West | 211738865 | 20/02/2025 | 5.5 | CC1.1013.../2400184 | Genset Trip | Closed | Ravii Talrejas & Associates | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 28 | DG trip due to overload. 24Ams. | Closed | Jagdeep Saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
7 | West | 211751956 | 24/02/2025 | 25 | GP3.8702.../2520112 | Genset Trip | Closed | SUYOG BUILDERS | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | CUSTOMER SITE LOAD ISSUE | Closed | Jagdeep Saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
8 | West | 211751671 | 24/02/2025 | 25 | GP3.8702.../2421916 | Display Issue & Timer Issue. Call By Customer Name :- Omakar Jadhav Mobile No :- 9595508001 | Closed | Gurudatta Hardware & Paints | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 17 | MIL LAMP ON , EGR MALFUNCTION DM1 , wiring and wire harness disconnerct for 5 min and then connect wiring , so alarm not shown in DM1 | Closed | Jagdeep Saini | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
2 | East | 211752701 | 24/02/2025 | 0 | 4H.8042.C4../2520044 | Charging Problem. | Task Start | ELMECH ENGINEERS | Revenus Industries Pvt. Ltd. - Howrah | LR | Charging Alternator Faulty,so charging alternator under EDO | OPEN | Prosanjit saha | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
3 | East | 211751738 | 24/02/2025 | 20 | GP3.8601.../2420482 | Leakage Issue | Completed | S. K. Jewellary | Revenus Industries Pvt. Ltd. - Hooghly | 52 | SE found fuel leakage from fuel filters due to faulty filter so arrange fuel filter then replace the Fuel filter then start engine and observe all parameters found engine runs normal without Leakage. | CLOSED | Prosanjit saha | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
5 | East | 211754982 | 25/02/2025 | 82.5 | 5H.8901.../2320089 | Leakage Issue | Closed | Citi Style | HACS Engineering and Tech Private Limited - Hazaribagh | 320 | As per the customer compalint there was coolant leakage but when SE visited site and found no as such issue,but coolant drops were may be during coolant topup. and checked DG found DG healthy in condition | CLOSED | Prabhakar Kumar | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
6 | East | 211754336 | 25/02/2025 | 30 | 3H.8902.../2420881 | Starting Issue Call By Customer Name :- Ritu . Mobile No :-6000478741 | Closed | KISHAN RATHI | Hibreed Engineering Pvt. Ltd. - Jorhat | 4 | Controller Was not getting on some time so checked the voltage at 1 &2 no. pin which was fluctuating (8-11V) so check DC on off switch there was loose connection after tightening issue resolved | CLOSED | Ujjwal Das | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
8 | North | 211754513 | 25/02/2025 | 82.5 | 5H.8901.../2420216 | INSTANCE ID :- 100769959 SITE ID :- 132 CALL BY CUSTOMER// DG ISSUE :- STARTING PROBLEM NAME :- Ajay .. NUMBER :-9205252431 | Task Start | Axis Bank Ltd | Vidyut Engineers - New Delhi | 24 | Air lock in fuel line so remove the air after that issue resolve | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
7 | North | 211754572 | 25/02/2025 | 58.5 | T4.8941.../2420787 | BATTERY CHARGING ISSUE | Task Start | SETHI BUILDCON | Vidyut Engineers - New Delhi | 3625 | Found charging alternator fuse faulty so, replace the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
15 | South | 211750435 | 24/02/2025 | 320 | F6.8802.../2420150 | Starting Issue Call By Customer Name :- Ramesh ... . Mobile No :-8088672337 | Closed | M/s. Star Infratech | Prasad Power Engineers - Tumkur | 120 | 1761/16, 516166/0 topup the adblue then clear the ECU. | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
8 | South | 211751972 | 24/02/2025 | 30 | 3H.8902.../2420888 | AMF PANEL PROBLEM Call by : Customer Name :Mr. Ramesh Contact :9731568358 | Task Start | Ramesh B. M. | Surya Power Services - Chikkaballapur | 101 | Found defective 2B3 CONTROL CABLE CONECTER LOOSEN CLIMPED | Closed | Mr. Anil Kumar H G | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
66 | South | 211742762 | 21/02/2025 | 58.5 | T4.8941.../2421637 | Starting/Stopping Issue | Closed | N. S. P. I. R. A. Management. | Laxmi Diesels - Visakhapatnam | 24 | Checked engine, control panel found &quot;Y&quot; phase wire burned at terminal connector at c.t coil, &quot;Y&quot; Phase c.t coil, controller kg 640 c burned, so Y Phase wire ,c.t coil,and controller 640 c to be replaced with new one. | Closed | Mr. MD Saleem | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
70 | South | 211741949 | 21/02/2025 | 58.5 | T4.8941.../2422423 | Coolant leakage | Closed | Thas Kitchen. | Bharath Diesel Sales and Service - Neyveli | 51 | Coolant leakage from hose clamp, tighten the clamp | Closed | Mr. NandhaGopal | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
74 | South | 211741462 | 21/02/2025 | 25 | GP3.8702.../2421866 | Starting issue Call by KGD Name - Prakash No - 9448476151 | Closed | Aura Care Hospital | Prasad Power Engineers - Shimoga | 38 | SPIN 2791.FMI.18 and then connect the I connect tool and clear the issue started the DG again same code fault flash the ECU, issue resolved | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
76 | South | 211741106 | 21/02/2025 | 160 | 6H.8475.../2420418 | Genset Trip | Closed | KVR AUTO CARS PVT LTD | G-Care Diesels Private Limited - Kannur | 1483 | Site visited and customer complaining about low fuel engine tripping issue at site so discussed the matter with ASE godson and as per his instructions ECU flashing done and 1 hour trail run completed ,also additional negative given from battery to controller site under observation | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
77 | South | 211741104 | 21/02/2025 | 40 | 3H.8951.../2421449 | AMF panel problem Call by : Customer Name : 9844420594 Contact : 9901803239 | Closed | SRI VEERABHADVESHWARA TEMPLE | Prasad Power Engineers - Shimoga | 17 | Visited the site and started the dg check display voltage was RY-258 YB- 260 BR- 258 comes so I set the voltage in KG640c controller AC voltage , High RY-285 ,YB-285, BR 285 set ,and again started the engine with load and agine started the dg check the sound and smoke is normal condition with engine working is good condition | Closed | Mr. Anil Kumar H G | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
10 | East | 211739071 | 20/02/2025 | 20 | GP3.8604.../2420180 | INSATANCE ID:-100742007 SITE ID:-I-BR-AGIN-ENB-9022 CALL BY CUSTOMER:- DG ISSUE :-DG GCU ALRAM NAME:-RATESH KUMAR NUMBER :- 8340233128 | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 141 | Fuel level sensor open alarm popuped on the display so SE tighten controller all jack screw related fuel and reconnected ECU connector and fitted properly then issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | North | 211741828 | 21/02/2025 | 500 | DV8.8501.C4../2420013 | Automation Issue Call By Customer Name :-Virender Kumar Number:- 7633873576 | Task Start | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 38 | Inducement intruptted - Today Engineer visit again | open | Kapil Solanki | [9 empty] | Inducement | 8 | 6 | 5 | 240 | High
8 | East | 211748869 | 23/02/2025 | 30 | 3H.8902.../2422023 | Alarm Issue Call By Customer Name :-Satpal Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS | Hibreed Engineering Pvt. Ltd. - Guwahati | 190 | Engine rpm fluctuation Customer side load unbalance R -15 A, Y- 21A, B -13 A, so approx 30% load unbalancing need to balance the load. | OPEN | Ujjwal Das | [9 empty] | Load | 8 | 6 | 5 | 240 | High
5 | North | 211745981 | 22/02/2025 | 250 | DV8.9840.../2420006 | Startig Issue And Preventive Maintenance Call By Customer Name :- Mobile No :- | Closed | The Ekta Vihar C/o. Operative Group Housing Society Ltd. | Vidyut Engineers - New Delhi | 13 | Gas Engine- Low Coolant level topup the coolant 3 Lit. after issue resolve | Closed | Kapil Solanki | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
19 | North | 211748709 | 23/02/2025 | 30 | 3H.8902.../2420044 | Starting/Stopping Issue | Task Start | Mr. Laykat Rai | Industrial Power Solutions - LUDHIANA | 139 | R-Phase under Voltage alarm occurred & DG was in running conditin on site ; check the Fuel line & wiring,found ok,Flash the controller & advised customer for change-over check | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
21 | North | 211747373 | 22/02/2025 | 25 | GP3.8702.../2420908 | Genset Trip | Closed | NITESH | SAAN Royal Power Solutions Private Limited - Shimla | 10 | Genset tripping issue due to mains fuse found faulty in Pannel due to jerk load; replace the same &resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
9 | West | 211734267 | 19/02/2025 | 58.5 | T4.8941.../2422543 | Starting issue Call By Customer Name :- Arun Mobile No :-9766262217 | Closed | SHRADDHA HATCHERY | KALA Care Global LLP - Aurangabad | 435 | Engine donot take load due to chocked fuel filter so change the filter. | Closed | Jagdeep Saini | 20-01-2025 | [8 empty] | Load | 8 | 6 | 5 | 240 | High
14 | West | 211738553 | 20/02/2025 | 58.5 | T4.8941.../2421607 | INSTANCE ID:-100777022 CUSTOMER SITE ID ;- 0018873 CALL BY CUSTOMER\\ DG ISSUE:- Coolant Leakage Issue NAME;-Anand Bhangire NUMBER:-9834828264 | Closed | ASCEND TELECOM | Mahalaxmi Diesels - Solapur | 513 | coolant leakage from hose clip tighten the clip . | Closed | Jagdeep Saini | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
16 | West | 211746083 | 22/02/2025 | 200 | 6H.8435.../2420154 | Starting/Stopping Issue | Closed | DOUNDE LALWANI INFRA PVT LTD | KALA Care Global LLP - Aurangabad | 56 | The engine was not taking load so the engineer found the fuel filter choked. Cleaned it and gave a quotation to the customer. The engineer will visit today for servicing. | Closed | Jagdeep Saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
19 | West | 211749743 | 24/02/2025 | 40 | 3H.8951.../2421190 | Genset Trip | Task Start | Technocraft Engineering. . | KALA Care Global LLP - Babhleshwar | 62 | Sometimes DG trips due to under speed. Checked the all panel wiring loose connection and fuel line. Miner leakage received from fuel returne pipe so EDO placed for the same. Low quantity of White smoke comes from the exhaust side in initial time at the 10Ams load. | open | Jagdeep Saini | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
3 | South | 211752685 | 24/02/2025 | 25 | GP3.8702.../2421964 | Starting Problem Call by : Customer Name :Arshand Contact :9847151622 | Task Start | HARIS.M | Electro Controls - Thiruvananthapuram | 6 | Dg tripped controller show in undervoltage.checked the resistance value in avr found 1.6 ohm .So removed avr and connected the float Avr then checked dg running properly without any issue.avr fault conformed need to replace avr underwarrandy. | Task Start | Mr. Sanjaimon S | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
6 | North | 211745910 | 22/02/2025 | 250 | DV8.9840.../2420003 | voltages incress issue Call By Customer Name :- Mahendra . Mobile No :-9560364465 | Task Start | Kundan Refinery P. Ltd. | Paluck Technologies Ltd. - Gurgaon | 6 | Gas Engine- Load analyse with jakson team | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
61 | South | 211745321 | 22/02/2025 | 125.4 | 4H.8042.C4../2420317 | Starting/Stopping Issue | Task Start | KMV Projects Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 50 | Self-motor pinion not rotating, self-motor wiil send to bosch for repairing | Closed | Mr. MD Saleem | [9 empty] | Motor | 9 | 6 | 7 | 378 | High
1 | South | 211758543 | 26/02/2025 | 58.5 | T4.8941.../2423256 | Starting/Stopping Issue | Task Start | Dr. K.M.K Varma | Surya Power Services - Bangalore | 1.53 | 2791/18, 5838/1,2791/6 Error Code. Flash the ECU | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
10 | South | 211757970 | 26/02/2025 | 10 | GP3.8301.../2420158 | AMF Panel problem Call by : Customer Name :Ranoj Contact :8590778828 | Task Start | ALICE MEDICAL CENTRE | G-Care Diesels Private Limited - Kannur | 59 | Attended the site, checked the engine, found that controller shows "red lamp on " alarm (190/8)and shutdown. Need for Flashing | Task Start | Mr. Sanjaimon S | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
21 | North | 211759771 | 26/02/2025 | 20 | GP3.8601.../2420087 | Red Lamp Alarm Issue Call By Customer Name :DK Singh No: 9415211226 | Task Start | WESTERN INDIA CORPORATION (NEW).. | S. R Engines Sales And Service - Gorakhpur | 3 | Found emergency Stop switch activated alarm in controller so dg set not starting then check found negative wire loose at connector then proper tight | Closed | Sudhir Awasthi | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
25 | North | 211758957 | 26/02/2025 | 57 | T4.8941.../2320250 | Cool and leakage | Closed | Shivmani Hospital | Paluck Technologies Ltd. - Faridabad | 241 | Found Coolant leakage from Coolant sensor because sensor was loose so, tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
28 | North | 211761808 | 27/02/2025 | 160 | 6H.8475.../2420024 | MCB Lamp Alarm And Over Current Alarm Call By Customer Name :- Sunil Mobile No:-7206727293 | Task Start | Tool Room Engineers LLP | Paluck Technologies Ltd. - Faridabad | 244 | Low Def level alarm, top up the DEF then issue resolve | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
29 | North | 211761737 | 27/02/2025 | 250 | F6.8841.../2420056 | Lood issu | Task Start | Shiva Steel | Pratap Diesels Pvt. Ltd. - Bhiwadi | 140 | Dg take the load Upto 80KW but Customer not give the more load, Load trial with Jakson team & Koel team | open | Gourav Sharma | [9 empty] | Load | 8 | 6 | 5 | 240 | High
34 | North | 211760638 | 26/02/2025 | 5.5 | CC1.1013.../2400528 | Leakage Issue | Task Start | AARUSHI CONSTRUCTION | Pratap Diesels Pvt. Ltd. - BIKANER |  | Starting problem fuel pump need to replace | Open | Gourav Sharma | [9 empty] | Fuel Pump | 8 | 6 | 5 | 240 | High
37 | North | 211763855 | 27/02/2025 | 20 | GP3.8601.../2421343 | Leakage Issue | Closed | AHUJA PLASTIC UDYOG | Paluck Technologies Ltd. - Faridabad | 2.3 | During comminsioning Coolant drop on the tank So, customer raise the complaint for leakage issue | Closed | Kapil Solanki | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
38 | North | 211763823 | 27/02/2025 | 58.5 | T4.8941.../2420950 | CONTROLLER REPLACE | Task Start | K. T. Power Sales and Services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 7.2 | Display blank but all parameter works ok not any problem so controller new file not match So controller not replaced | Open | Kapil Solanki | Failed Part | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
40 | North | 211763368 | 27/02/2025 | 58.5 | T4.8941.../2423313 | Starting/Stopping Issue | Task Start | Gagan Generators. | Vidyut Engineers - New Delhi | 244 | Air lock in fuel line so, remove the air then issue resolve | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
42 | North | 211763253 | 27/02/2025 | 57 | T4.8941.../2320062 | Fan belt broken issue Call by customer Name - Virendra Kumar No - 9717986906 | Task Start | AMIT SEHGAL | Vidyut Engineers - Noida | 335 | Found V-belt broken so, Change v-belt after DG start without load found normal | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
50 | North | 211762760 | 27/02/2025 | 400 | 6H.8439.../2420002 & 2420002 | Alternator broken issue Call by customer Name - Mehad . No - 8439789589 | Task Start | SKH Sila India Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 74 | Charging alternator found mounting bolts and I Bolt broken then change New Bolt | Closed | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
53 | North | 211761749 | 27/02/2025 | 20 | GP3.8601.../2420263 | Starting/Stopping Issue | Closed | Om Distributors | Gen Powers - Nabha,Patiala | 59 | DG Starting issue with low fuel alarm (12%) top-up the same & load found unbalance also(3.5,17,3.5) amp,same communicated to customer to re-check the load side for balancing the same | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
5 | WEST | 211761173 | 27/02/2025 | 20 | GP3.1021.../2420193 | INSTANCE ID:-100748744 SITE ID:-I-GJ-ABMC-ENB-9004 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-RAVI PARMAR NUMBER:-9081247452 | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Jamnagar | 59.11 | Customer complained that DG was tripping due to under voltage and even after running for 120 mins DG was not stoping , so engineer checked that limit was set to 270 mins in controller, so it was rectified. DG is running, stopping and starting properly. | Closed | Amit Sandlya | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
7 | WEST | 211757627 | 26/02/2025 | 25 | GP3.8702.../2421466 | Electrical Problems | Closed | Blue Corporate House | Unique Techno Services Pvt Ltd. - Surat | 30 | The load side neutral cable socket was burnt out so replaced it. | Closed | Amit Sandlya | [9 empty] | Load | 8 | 6 | 5 | 240 | High
1 | East | 211761699 | 27/02/2025 | 20 | GP3.8601.../2421194 | High Flue Alarm Issue & Tripping Issue. Call By Customer Name :- Viky Kumar Mobile No :- 7004929877 | Task Start | AMAR KUMAR | HACS Engineering and Tech Private Limited - Dhanbad | 61 | SE visited the site and High fuel level alarm and on discusing with the customer came to know that sometime this alarm trigger on the display so SE checked resistance for fuel sensor (10 ohm at 0% and 100 at 50-60% and 180 ohm at 100%) found ok all connection also found to be ok so SE suggested customer to maintain fuel level 30-85% as this DG is install on trolley so its suspected that due to this reason this alarm may raise. put it under observation if same will occue then need to flash ECU. | CLOSED | Prabhakar Kumar | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | East | 211764238 | 27/02/2025 | 20 | GP3.8601.../2421241 | Starting issue Called by dealer Name : Parshuram Number : 9942082266 | Task Start | Raunaq T. V. S. | HACS Engineering and Tech Private Limited - Jamshedpur | 63 | SE visited and found load unbalancing and in event log also found DG trip due to overload so recommended customer to balance the load and found no issue in DG.(R-16A, Y-26A, B-4.5A) | CLOSED | Prabhakar Kumar | [9 empty] | Load | 8 | 6 | 5 | 240 | High
19 | North | 211759955 | 26/02/2025 | 45 | 3H.8951.../2520060 | Genset Trip | Closed | Field Marshal Agency | Excel Diesel Private Limited - Faizabad | 2 | Air lock in fuel line so, remove the air & Clear the alarm then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
18 | North | 211760033 | 26/02/2025 | 125.4 | 4H.8041.../2420082 | Inspection/Maintenance | Task Start | Rmb Hydraulicand Allied Products | Paluck Technologies Ltd. - Faridabad | 403 | Found Def level low & fuel filter loose, tightness the same & topup the def | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
16 | North | 211760444 | 26/02/2025 | 15 | GP3.8501.../2420390 | Black Smoke issue Call By Customer Name :- Yogesh Khurana Mobile No :- 9654400665 | Task Start | Swami Enterprises | Paluck Technologies Ltd. - Faridabad | 32 | During starting time DG gives the Black smoke but when DG run about 10 to 15 minutes. Found no any issue | Closed | Kapil Solanki | [9 empty] | Black Smoke | 9 | 7 | 6 | 378 | High
12 | North | 211755225 | 25/02/2025 | 125.4 | 4H.8042.C4../2420059 | Electrical Problems | Closed | ECIL CO-OP. GROUP HOUSING SOCIETY LTD | OVN Industries Private Limited - New Delhi | 16.2 | found unbalanced load on dg and zark load due to construction work therefore customer all light flickering for 1-2 seconds so advised to the customer for your load is unbalanced please maintain load (Under observation) | Open | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
15 | South | 211755317 | 25/02/2025 | 0 | GP3.8702.../2520231 | FUEL LEAKAGE FROM LEAK OFF PIPE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Fuel leakage from leakoff pipe | Task Start | Mr. NandhaGopal | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
18 | South | 211755032 | 25/02/2025 | 25 | GP3.8702.../2420739 | Line Rejection | Task Start | ATC Telecom Infrastructure Private Limited | Electro Controls-Coimbatore 2 | LR | Rusted in Engine charging alternator and crank pully and fly wheel, Main alternator. Already inform to HO to pradeep sir | Task Start | Mr. Sanjaimon S | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
20 | South | 211754790 | 25/02/2025 | 30 | 3H.8902.../2421793 | Starting/Stopping Issue | Closed | Prashanth Reddy | Surya Power Services - Bangalore | 1.41 | 2791/18, 5838/1 error code flash the ecu | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
21 | South | 211754757 | 25/02/2025 | 58.5 | T4.8941.../2423012 | Starting/Stopping Issue | Closed | Sunil. | Surya Power Services - Billekahalli | 21 | 2791/18, 5838/1 error code flash the ecu | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
24 | South | 211754434 | 25/02/2025 | 20 | GP3.8601.../2420203 | White smoke Problem Call by : Customer Name : Yesu Contact : 6302687339 | Closed | S. R. Biz Spot. | Ultimate Power Source - Kurnool | 5 | White Smoke issue,Starting time only smoke is coming, So checked the fuel line properly now issue resolve. | Closed | Mr. NandhaGopal | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
25 | South | 211754349 | 25/02/2025 | 125.4 | 4H.8041.../2420759 | Starting/Stopping Issue | Task Start | C. Vasudeva Rao | Sri Manjunath Technical Services - Narasaraopet | 24 | Fuel Leakage from leakoff pipe, tight the leakoff pipe issue resolved | Closed | Mr. NandhaGopal | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
3 | East | 211758265 | 26/02/2025 | 5 | CP1.1003.../2400165 | STARTING KEY NOT WORKING PROPERLY | Task Start | North East Powerline Equipment Pvt.Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 1 | line rejection - SE visited and found ignition key not working so replaced it by new one and also found the 10 A fuse defective so replaced it also then problem resolved | CLOSED | Ujjwal Das | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
7 | South | 211758036 | 26/02/2025 | 750 | DV2.8501.C4../2420160 | FLYWHEEL BOLT DAMAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the dg noticed the flywheel Bolt all damage, change the new flywheel, alternator disk and bolt fixing and proper torque done, | Task Start | Mr. NandhaGopal | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
3 | North | 211758461 | 26/02/2025 | 320 | F6.8802.../2420229 | Coolant alarm issue | Closed | Welfare Association of Roman Court Residents | SAAN Royal Power Solutions Private Limited - Sonipat | 74.12 | Amber lamp alarm occurred due to coolant level found low so top-up the same & remove the code,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
4 | WEST | 211751733 | 24/02/2025 | 0 | GP3.8601.../2520293 | FUEL LEAKAGE | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Fuel leakage from benjo , so tighten the benjo issue solved. | Closed | Jagdeep Saini | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
9 | WEST | 211710229 |  | 0 | DV8.8501.C4../2420236 | STARTING ISSUE | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Can communication faliure , DCU parameter not showing proper so change the bank A DCU wiring harness. | Closed | Jagdeep Saini | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
13 | WEST | 211754717 | 25/02/2025 | 160 | 6H.8475.../2420076 | V Belt Loose | Task Start | Aarohi Enterprise. . | Unique Techno Services Pvt Ltd. - Ankleshwar | 69 | The charging alternator bracket bolt had fallen off on the DG bottom. So fitted the same bolt properly. | Closed | Amit sandlya | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
6 | South | 211761160 | 27/02/2025 | 30 | 3H.8902.../2420982 | UNDER SPEED ALARM ISSUE CALL BY CUSTOMER NAME ;- S.VENKATACHALAM .. MOB NO ;- 8124647906 | Task Start | S.Vengatachalam | Bharath Diesel Sales and Service - Puducherry | 22 | Under speed alarm. So SE Checked the fuel line found the airlock remove the airlock issue resolve. | Task Start | Mr. NandhaGopal | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
20 | South | 211758695 | 26/02/2025 | 25 | GP3.8702.../2421820 | ENGINE NOT STARTING-SARVANAN | Task Start | REVAMP POWER | Surya Power Services - Kalyan Nagar | LR | As per the customer complaint came and visit the site and checked the engine and all wiring connection on belong with kirloskar team Ashish and Abhishek so checked the ECU and all sensors then find out the issue ecu and oil sensor failure so inform to the kirloskar team and approval for new ECU and oil sensor replacement. Then replaced the new ECU and sensor now start and stop and running condition ok on with load and without load | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
2 | North | 211758659 | 26/02/2025 | 40 | 3H.8951.../2320018 | Tripping Issue Call By Customer Name :- Dev Mobile No :- 9813957180 | Task Start | SONYSALES PACKAGING INDIA PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 957 | Engine start but engine not running under speed shutdown saddnly then remove Air locking from fuel line then DG start and running ok but fuel filter assembly need to change and Banjo barsal also | Open | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
9 | North | 211757626 | 26/02/2025 | 58.5 | T4.8941.../2520085 | Coolant consumption issue Call By Customer Name :Prakash .. No :7982712453 | Closed | RAMACIVIL INDIA CONSTURCTION PVT. LTD | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 96 | Coolant low in recovey tank & Service due (CC done on 13/02/2025) | Closed | Kapil Solanki | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
7 | North | 211755096 | 25/02/2025 | 15 | GP3.8501.../2420350 | Starting/Stopping Issue | Closed | Vidya Devi Malik Kisan Sewa Kendre | SAAN Royal Power Solutions Private Limited - Hisar | 92 | DG Starting issue due to air locked found in Fuel line so release the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
30 | North | 211729582 | 18/02/2025 | 625 | DV0.8501.C4../2420079 | ECU alarm Issue Call By Customer Name :- Devendra Saini Mobile No :-8053353744 | Closed | HPL. Electric & Power Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat | 207.1 | ECU Protect alarm was showing in the DG display, then connected the CPCB4 Ikonnect tool and cleared all the code(516166/0 & 1761/16) , after that started the DG, the DG started and now the DG is running properly on load | Closed | Ved Prakash Gupta | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
57 | South | 211745728 | 22/02/2025 | 58.5 | T4.8941.../2421637 | display issue | Task Start | N. S. P. I. R. A. Management. | Laxmi Diesels - Visakhapatnam | 25 | checked control panel wiring and controller, Controller display not showing,And C T coil burn (y-phase), now new controller installation with programming then start and stop found ok | Closed | Mr. MD Saleem | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
47 | South | 211747882 | 22/02/2025 | 320 | F6.8802.../2420348 | Auto sensing problem | Closed | Jayabalan | Madhu Engineering Sales & Service - TIRUVALLUR | 37 | Auto start problem customer provide EB sensing but in controller setting is disable so enable the EB sensing on controller used with loptop now dg was checked in auto mode running condition found normal | Closed | Mr. NandhaGopal | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
26 | North | 211730472 | 18/02/2025 | 30 | 3H.8902.../2420940 | Starting/Stopping Issue | Closed | Bedi Saxena Service Station. | OVN Industries Private Limited - New Delhi | 17 | Found air in fuel line due to fuel filter was loose so, tightness the filter & remove the air then issue resolve | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
28 | North | 211730332 | 18/02/2025 | 30 | 3H.8902.../2420045 | Starting/Stopping Issue | Closed | Jupiter Wheels Private Limited | OVN Industries Private Limited - New Delhi | 48 | DG not started due to high coolant temperature alarm so check physically engine temperature and found normal so clear fault with i konnect tool then started the dg and found running is ok | Closed | Kapil Solanki | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
35 | North | 211732713 | 19/02/2025 | 125.4 | 4H.8041.../2420026 | Starting/Stopping Issue | Closed | Mohan Enterprises | SAAN Royal Power Solutions Private Limited - Karnal | 411 | Starting issue due to emergency stop alarm occurred,checked & found XC3 connector loose so tightened the same & reset the controller,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
37 | North | 211732600 | 19/02/2025 | 125.4 | 4H.8042.C4../2420180 | Fuel leakage issue | Closed | SHAKTI FOUNDARY | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 23 | Fuel leakage found from fuel return line due to joint found loose near tank,tightened the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
49 | North | 211713225 | 13/02/2025 | 15 | GP3.8501.../2420437 | Starting/Stopping Issue | Closed | Colonel Jayant Vij | SAAN Royal Power Solutions Private Limited - Zirakpur | 36 | DG Auto-starting issue due to Under speed alarm,check the fuel line ,found correct reset the alarm & run in auto-mode,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
50 | North | 211713089 | 13/02/2025 | 58.5 | T4.8941.../2421526 | Starting/Stopping Issue | Closed | Indian Army Hisar Haryana | SAAN Royal Power Solutions Private Limited - Hisar | 2 | PN/FMI-157/14& 97/5; CHECK the fuel condition,found ok.supply to WIF sensor to ECU through distribution block(XBDK)& Found that supply to WIF sensor with ferrule no.2A1(4B) were wrongly looped with -ve supply inXBDK 3( dummy to customer use);corrected same with +ve supply 2A1 in XBDK 2 & reset the codes | Closed | Ved Prakash Gupta | GOEM issue | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | East | 211734112 | 19/02/2025 | 30 | 3H.8902.../2420892 | Starting Issue Call By Customer Name :- Rawat Ji Mobile No :- 8637507378 | Open | LINKCON ENGINEERING PRIVATE LIMITED | Hibreed Engineering Pvt. Ltd. - Guwahati | 25 | today SE will visit site, EGR valve related code | OPEN | Ujjwal Das | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
16 | North | 211737543 | 20/02/2025 | 40 | 3H.8951.../2421709 | Starting/Stopping Issue | Closed | Purnima Verma Cold Storage Pvt. Ltd. | S. R Engines Sales And Service - LUCKNOW | 111 | Found Unbalance load from customer end R-0.4, Y-65.2, B-65.1 so, DG trip with over current alarm same educate the customer for balancing the load | Closed | Sudhir Awasthi | [9 empty] | Load | 8 | 6 | 5 | 240 | High
17 | North | 211737362 | 20/02/2025 | 500 | DV8.8501.C4../2420016 | Electrical Problems | Closed | PG ELECTROPLAST LIMITED | Vidyut Engineers - Noida | 79 | Over current alarm, Jumping load & over load issue | open | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
1 | WEST | 211734973 | 19/02/2025 | 30 | 3H.8902.../2422189 | Under speed alarm issue Call By Service Dealer Name :Yogesh no ;7722070416 | Closed | I P Laghu Udyog | Dhanashree Technocrats Pvt. Ltd. - Dhule | 11 | dg tripped by giving under speed alarm so flash the ECU . Under observation | Closed | [10 empty] | ECU | 10 | 9 | 7 | 630 | High
9 | WEST | 211737218 | 20/02/2025 | 40 | 3H.8951.../2420168 | Starting Issue Call By Customer Name :- Sachin Patel Mobile No :-9978386967 | Task Start | P. C. PATEL INFRA PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Baroda | 18 | The DG had a starting issue. After turning on the controller power supply, the controller would sometimes turn on and sometimes not. This also happened with the same relay. Tightened all the wires in the panel, but the issue persisted. Upon checking the engine and panel connector, Found that the 1C2(-) wire was backed out from its position. Reconnected it properly and started the engine. | Closed | Panel photo | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
15 | WEST | 211733299 | 19/02/2025 | 0 | DV8.8501.C4../2420236 | Adblue parameter not showing | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Communication Error. DEF parameter not showing so after replace the wiring problem solved. | Closed | [10 empty] | DEF | 8 | 7 | 5 | 280 | High
4 | North | 211742494 | 21/02/2025 | 500 | DV8.8501.C4../2420171 | ECU Alarm Issue Call By Customer Name :-Gaurav Arora No :-9810883428 | Task Start | Allied Engg. corporation | Paluck Technologies Ltd. - Faridabad | 335 | Low def level topup the def then found no any alarm | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
5 | North | 211742108 | 21/02/2025 | 250 | F6.8842.C4../2420067 | LINE REJECTION | Task Start | SHREE KRISHNA COLD STORAGE | Espiem Engines & Machines (P) Limited - Agra | LR-3 | Found Engine wiring harness all ground wiring was burnt, self starter was over heat , Today ASE visit | open | Sudhir Awasthi | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
7 | North | 211741887 | 21/02/2025 | 125.4 | 4H.8041.../2420215 | Trip_Genset_Low_Voltage | Closed | SM Partners | Vidyut Engineers - Noida | 16 | AC alternator burnt So, Joint Visit with Nidec team Now, Educate the customer all work on the chargeable basis | Closed | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
21 | North | 211732652 | 19/02/2025 | 320 | F6.8802.../2320057 | Leakage Issue | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 256 | Found inlet manifolt gasket was defective so, change the gasket | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
17 | North | 211732947 | 19/02/2025 | 125.4 | 4H.8041.../2420215 | Electrical Problems | Task Start | SM Partners | Vidyut Engineers - Noida | 16 | Check & found AC alternator burnt & main stator blast | open | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
13 | North | 211733088 | 19/02/2025 | 750 | DV2.8501.C4../2420013 | Fuel Sensor Issue Call By Customer Name :-Chandan .. Mobile No :- 9785742850 | Task Start | Homekraft Infra Pvt. Ltd. | Vidyut Engineers - Noida | 49 | DG set found fuel level not showing in controller Due to fuel sensor connection is wrong fitted in Ems After that Re fitted the correct connection and check fuel sensor proper fuel show in Ems Display | Closed | Kapil Solanki | GOEM issue | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
5 | North | 211733839 | 19/02/2025 | 160 | 6H.8475.../2420203 | VOC - Electrical Problems Customer Name -Anupam Singh Customer Number -7355543180 Mode- SR Generated through CDI calling. | Task Start | HOTEL AVINASH | S.S. Enterprises - Sonbhadra | 97 | Check & found low def level, low coolant in recovery tank & Service due | Closed | Sudhir Awasthi | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
34 | North | 211723739 | 17/02/2025 |  | DV8.8501.C4../2420232 | Wiring harness issue | Task Start | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - Jammu | 0.5(LR) | Visit the site fitted the wiring harness , Dg not assamble proper | Open | Ved Prakash Gupta | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
40 | North | 211721288 | 15/02/2025 | 58.5 | T4.8941.../2422378 | CONTROLLER ISSUE | Closed | DG MANSION LLP | SAAN Royal Power Solutions Private Limited - Zirakpur | 2.1 | Replace the controller KG 640 C | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
42 | North | 211719752 | 15/02/2025 | 62.5 | T4.8941.../2420100 | Voltage Fluctuation | Closed | Dwarika Auto Engg. Works | SAAN Royal Power Solutions Private Limited - Rohtak | 85 | DG tripped on load with over current alarm due to over-load (More than 90 amp) so same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
47 | North | 211716653 | 14/02/2025 | 125.4 | 4H.8041.../2420107 | Leakage Issue | Closed | SNV Overseas | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 162.56 | Fuel leakage found at Leak-off pipe so change the washer & tightened all the joints,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
48 | North | 211713103 | 13/02/2025 | 125.4 | 4H.8042.C4../2420803 | LOAD RELATED PROBLEM | Task Start | SS Electro Works Pvt Ltd | SAAN Royal Power Solutions Private Limited - Sonipat | LR | DG Not running on load,GOEM team taken load analysis of DG & Mains,decision pending from GOEM Side | Open | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
2 | East | 211728977 | 18/02/2025 | 20 | GP3.8601.../2421194 | Tripping Issue And Black Smoke issue Call By Customer Name :- AMAR KUMAR Mobile No :-7004929877 | Task Start | AMAR KUMAR | HACS Engineering and Tech Private Limited - Deoghar | 60 | DG not starting and showing under speed alarm so SE started to check the fuel line for air lock issue so loosen the banjo bolt, there found jelly like so removed the fuel level gauge and found the strainer was blocked by that fluid after cleaning issue resolved | CLOSED | Prabhakar Kumar | Fuel sample required | [8 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
9 | East | 211724863 | 17/02/2025 | 20 | GP3.8601.../2421689 | Genset Trip | Closed | S.K.S. PROJECTS | Revenus Industries Pvt. Ltd. - Midnapore | 5 | SE check the engine lube oil, coolant level, fuel level, all external checkup, found that starting problem Because High fuel alarm show, fuel sensor wiring connection issue, so fuel sensor wiring properly connected, then start the engine is running condition ok, | CLOSED | Prosanjit saha | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
8 | North | 211741780 | 21/02/2025 | 20 | GP3.8601.../2420464 | Amber Lamp Alarm Call By Customer Name :- Mobile No :- | Closed | Red Rose Convent School | Espiem Engines & Machines (P) Limited - Aligarh | 99 | Found Under speed alarm then check fuel line found ok then reset the alarm after trial on load near about 30 min. found no any issue | Closed | Sudhir Awasthi | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
11 | East | 211717445 | 14/02/2025 | 7.5 | D3.8305.../2400088 | Electrical Problems | Task Start | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - BHUBANESWAR | 14 | Exciter rotor defective,need to Exciter rotor repair | OPEN | Ujjwal Das | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
6 | West | 211727126 | 17/02/2025 | 30 | 3H.8902.../2420699 | Starting issue Call By Customer Name :- Nayar Mobile No :- 9702042518 | Closed | PERFECT FABRICATORS | Transcreek Engineers Pvt. Ltd. - Mumbai | 371 | RL2 Main relay switch point not working so fuel pump did not get the supply. changed relay board. | Closed | Jagdeep saini | [9 empty] | Fuel Pump | 8 | 6 | 5 | 240 | High
9 | South | 211730810 | 18/02/2025 | 250 | F6.8841.../2420413 | Genset Trip | Open | KRISHNA LAMICOAT PVT LTD | Surya Power Services - Peenya, Bangalore | 48 | 1761/16 Def level low | Open | Mr. Anil Kumar H G | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
12 | South | 211730424 | 18/02/2025 | 320 | F6.8802.../2420188 | Automatically switching off Call by : Customer Name :Ramesh Contact :9591989437 | Closed | Diamond Display Solutions Pvt Ltd | Surya Power Services - Kalyan Nagar | 8.5 | 157,14- Engine Fuel 1 Injector Metering Rail 1 Pressure-Special Instruction controller showing ecu protect alarm then connect the ikonnect tool and checked checked the alarm rail pressure low in injector 1 so once removed the connector and refitted the connector properly then cleared the DTC | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
15 | South | 211729855 | 18/02/2025 | 0 | GP3.8601.../2520076 | ERROR PROBLEM | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the site noticed the wiring harness furiel no B3 and C3 conneter loosed , correct the wiring harness after check the communication working ok | Task Start | Mr. NandhaGopal | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
10 | West | 211710017 | 12/02/2025 | 20 | GP3.1021.../2420202 | INSTANCE ID:-100748740 SITE ID:- I-GJ-PVJT-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG MAINS CONTACTOR FAULTY NAME:- NAVEEN NUMBER:- 9510756803 | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Baroda | 385 | Mains contactor coil found burn so replaced the mains contactor. Setting in controller- Mains over voltage:265V & Mains under voltage trip:100V. | Closed | Amit sandlya | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
18 | West | 211702403 | 10/02/2025 | 35 | 3H.8902.../2422058 | FLICKERING ISSUE | Task Start | Flora Furniture Square | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati | 11 | Observed flickering issue in polycab make 9 watt LED bulb. So replace the AVR with TAVR 27 & AVR tuning prosess carried out. Flickering decreased but not Stop. Then new 5 nos Wipro make 10 watt LED bulb fitted at load site. But issue is same. | Open | Jagdeep Saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
19 | West | 211709812 | 12/02/2025 | 20 | GP3.1021.../2420185 | VOC -Under Voltage Issue Customer Name -Sopan Customer Number -9049618317 Mode- SR Generated through CDI calling. | Open | Reliance Jio Infocomm Limited | Dhanashree Technocrats Pvt. Ltd. - Malegaon |  | Under volatge alarm procom controller sent to programe upgradation to new delhi. | Open | Jagdeep Saini | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
4 | West | 211728702 | 18/02/2025 | 5.5 | CC1.1013.../2400034 | Engine not taken load | Closed | Hotel Grace Lodging and Boarding | Transcreek Engineers Pvt. Ltd. - Ambernath | 23 | DG was not taking load.Spark arrestor found chocked. | Closed | Jagdeep saini | [9 empty] | Load | 8 | 6 | 5 | 240 | High
56 | South | 211745918 | 22/02/2025 | 200 | 6H.8435.../2420212 | Phase Problem Call by : Customer Name :NAVEEN Contact :6381216513 | Open | EXTERRO R & D PRIVATE LIMITED | Net Work Diesels - Potheri | 15 | DG panel to load panel out going cable phase sequence problem ender change the phase sequence, Started and tested the engine on load found DG set running | completed | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
10 | North | 211741708 | 21/02/2025 | 320 | F6.8802.../2420019 | Warning alarm showing on panel ECU | Closed | CIPL. | Vidyut Engineers - Noida | 225 | ECU Malfunctioning alarm after flashing the file then issue resolve | Closed | Kapil Solanki | ECU fault check | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
18 | North | 211747656 | 22/02/2025 | 58.5 | T4.8941.../2421954 | Electrical Problems | Closed | SUBHASH CHAND GENERATOR HOUSE | Paluck Technologies Ltd. - Ghaziabad | 248 | found d.c alternator not working charging fail alarm show and check d.c alternator found wire breck and connection fit done | Closed | Kapil Solanki | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
19 | East | 211746632 | 22/02/2025 | 58.5 | T4.8941.../2421680 | Automation Issue | Closed | PRASANT AUTO | Revenus Industries Pvt. Ltd. - Nandakumar | 31 | No Issue in DG, Customer side unbalance load | CLOSED | Prosanjit saha | [9 empty] | Load | 8 | 6 | 5 | 240 | High
22 | East | 211746632 | 22/02/2025 | 58.5 | T4.8941.../2421680 | Automation Issue | Closed | PRASANT AUTO | Revenus Industries Pvt. Ltd. - Nandakumar | 31 | No Issue in DG, Customer side unbalance load | CLOSED | Prosanjit saha | [9 empty] | Load | 8 | 6 | 5 | 240 | High
25 | East | 211738754 | 20/02/2025 | 250 | F6.8841.../2420214 | Starting/Stopping Issue | Closed | ORIENTAL COMPRESSOR ACCESSORIES PVT. LTD. | Revenus Industries Pvt. Ltd. - South Kolkata | 38 | DEF Level was low after that top up the def level,Issue resolved. | CLOSED | Prosanjit saha | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
26 | East | 211738547 | 20/02/2025 | 250 | F6.8841.../2420112 | Starting/Stopping Issue | Closed | Shalimar Hatcheries Ltd. | Revenus Industries Pvt. Ltd. - Barasat | 310 | DEF Level was low after that top up the def level,Issue resolved. | CLOSED | Prosanjit saha | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
1 | South | 211738310 | 20/02/2025 | 125.4 | 4H.8042.C4../2520067 | Line Rejection | Task Start | BMH Care Hospital Limited | G-Care Diesels Private Limited - Ernakulam | LR | Charge fail alarm topup. So found wiring harness issue.Wiring connected to the wrong port. After corrected found ok. Photo attached. | Closed | Mr. Sanjaimon S | Plant issue | [8 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
2 | South | 211737910 | 20/02/2025 | 125.4 | 4H.8042.C4../2420147 | Starting/Stopping Issue | Closed | Diocesan Charitable Trust | Electro Controls - Palakkad | 37 | 2802/4, 1761/16,920/5,2802/3 code topup. Adblue topup,then start the engine but found delay in start. So checked fuel line found NRV stuck. So clean the NRV. | Closed | Mr. Sanjaimon S | Buzzer relay logic check | [8 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
4 | South | 211737022 | 20/02/2025 | 125.4 | 4H.8042.C4../2420645 | ECU Issue | Open | Sigma MRI Scan center | Powerlinks Infra Tech Pvt Ltd - Nizamabad |  | ECU EDO Placed Awating for parts | Open | Mr. MD Saleem | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
12 | South | 211738442 | 20/02/2025 | 30 | 3H.8902.../2422160 | Starting/Stopping Issue | Task Start | Shrinidhi Engineers | Surya Power Services - Bangalore | 7.3 | 2791/18,2791/6 error code clear the DTC.Flash the ECU | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
13 | South | 211737997 | 20/02/2025 | 35 | 3H.8902.../2422231 | ESN NOT STARTING - RAMANJI | Completed | MS. Power Systems | Surya Power Services - Bangalore | LR | Found load side lights blinking because of interrupt neutral supply from connector due to faulty so replaced with new connector and resolved the issue. | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
14 | South | 211737799 | 20/02/2025 | 40 | 3H.8951.../2421760 | Alternate issue Call By KGD Name :- Jamuna Mobile No :- 9036094197 | Closed | ZIGMA TECHNOLOGIES | Surya Power Services - Billekahalli | 0.48 | Load side customer end change over problem, | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
15 | South | 211737005 | 20/02/2025 | 40 | 3H.8951.../2420336 | Oil leakage problem Call by : Customer Name :Naresh Contact : 9666109898 | Closed | Sangam Milk Producer Company Ltd...... | Powerlinks Infra Tech Pvt Ltd - Nalgonda | 19 | As per customer complaint during our visit the site check the all parameters observed fuel filter o ring is damaged so removed the fuel filter replaced the new fuel filter found ok after started the engine taken load trail running found ok and oil servicing also done | Closed | Mr. MD Saleem | [9 empty] | Load | 8 | 6 | 5 | 240 | High
19 | South | 211740084 | 20/02/2025 | 15 | GP3.8501.../2422178 | Shut Down Alaram Issue Call By customer Name Bhasakar Sir Mobile Number - 9742280609 | Open | M/s. SRI MARUTHI ENTERPRISES | Surya Power Services - Peenya, Bangalore | 9 | Customer side overload issue, Y phase is over current 34 amps take load then DG stop. | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
34 | South | 211735920 | 19/02/2025 | 58.5 | T4.8941.../2421891 | Red lamp alarm issue Call By Customer Name :-Vinaygan . Mobile No :-6385235499 | Closed | SAM INDIA BUILT WELL PVT LTD | Bharath Diesel Sales and Service - Karappakkam | 788 | 2791/0, 5838/1,2 error code topup. Se flash the ECU now working ok | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
36 | South | 211737010 | 20/02/2025 | 250 | F6.8841.../2320041 | Alaram issue | Closed | ST. Marys Hospital | Bharath Diesel Sales and Service - Salem | 118 | 5461/0 error code topup. Flash the ECU | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
43 | South | 211748813 | 23/02/2025 | 20 | GP3.8601.../2420186 | Starting Problem Call by : Customer Name : Shyam krishna Contact : 9989944336 | Task Start | Syam Krishna Kovelamudi | Ultimate Power Source - Nellore | 30 | Under speed Alarm. So checked fuel line found air lock issue. So remove airlock now issue resolve | Closed | Mr. NandhaGopal | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
13 | East | 211735069 | 19/02/2025 | 15 | GP3.8501.../2420002 | Genset Trip | Task Start | Laxman Choudhary. | Globalline India Services Private Limited - Darbhanga | 300 | SE visited and found emergency switch alarm so checked for loose connection properly found no as such loose coneection but cross check all connector like ECU connector, harness connector, canopy lamp and emergency switch screw after fitting all after cleainh issue resolved. | OPEN | Prabhakar Kumar | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
10 | East | 211738069 | 20/02/2025 | 15 | GP3.8501.../2420963 | Red Lamp Alaram Issue Call By Customer Name :- RANJIT HORO Mobile No :- 9110083717 | Task Start | ANAND KERIYA | HACS Engineering and Tech Private Limited - Ranchi | 9 | SE visited and found emergeny stop switch alarm so checked and found switch was pressed and after releasing it then also same issue after tightening emergency switch and reconnected ECU connector then Checked started DG ormally | CLOSED | Prabhakar Kumar | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
7 | East | 211741603 | 21/02/2025 | 125.4 | 4H.8042.C4../2420442 | Multiple alarm issue | Closed | M. P. Agarwal Pvt Ltd | Almas Engineers - Sivsagar | 486 | SE visited and found low DEF level alarm so topup and cleared code, cleared but on connecting Ikonnect found DEF level fluctuating(80-99%) so checked DEF tank connector voltage found (12,2.5,2.5,0)V which was ok so checked the resistance found 120ohm after that removed the DEF level and cleaned it by hot water and also removed the ECU connector and reconected after clening the pins after that found OK. | CLOSED | Ujjwal Das | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
6 | East | 211741679 | 21/02/2025 | 125.4 | 4H.8041.../2420938 | Urea issue Call By Customer Name :-Anil kumar . Mobile No :- 9534376666 | Closed | Shantidoot Infra Services Pvt. LTd. | HACS Engineering and Tech Private Limited - Ranchi | 286.3 | 516166 code ECU alarm and Low def level alarm found so after top adblue and clearing all DTC issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
23 | North | 211745063 | 22/02/2025 | 125.4 | 4H.8042.C4../2420781 | Emergency alarm issue Call by customer Name - Deepak Jaiswal No - 9935365222 | Closed | DEV YASH PROJECTS INFRASTRUCTURE PRIVATE LIMITED | R K Engineers - Meerut | 209 | Found Emergency 2B wire was loose so, tightness the same then issue resolve & Oil level & Def level top | Closed | Sudhir Awasthi | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
25 | North | 211742401 | 21/02/2025 | 320 | F6.8802.../2420044 | ECU warning alarm showing on panel | Closed | CIPL. Corporate Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 196 | ECU Malfunctioning Alarm & Low def level After top the def then clear the DTC then issue resolve | Closed | Kapil Solanki | ECU fault | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
28 | North | 211746065 | 22/02/2025 | 40 | 3H.8951.../2420351 | Starting issue Call by customer Name - Nitish Sharma No - 8894952913 | Open | D. R. V. S. Realestate Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Karnal | 2 | DG voltage fluctuation and check the main alternator and found that avr card fuse burnt so changed the new fuse then start the DG ...dg are working properly | Closed | Ved Prakash Gupta | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
32 | North | 211745127 | 22/02/2025 | 10 | GP3.8301.../2420250 | air lock | Open | Mahadev Enterprises. . | SAAN Royal Power Solutions Private Limited - Hisar | 39 | Starting issue due to Air locking in Fuel line , Fuel level found very low so top-up the same & educated customer to keep fuel minimum 20 % as per KOEL recommonded | Closed | Ved Prakash Gupta | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
36 | North | 211742624 | 21/02/2025 | 30 | 3H.8902.../2420081 | Starting/Stopping Issue | Closed | Nav Nirman Contruction Company | SAAN Royal Power Solutions Private Limited - Panipat | 47 | Starting issue with Under speed alarm , checked fuel line found air locked,release the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
37 | North | 211742501 | 21/02/2025 | 25 | GP3.8702.../2420046 | Starting Issue Call By Customer Name :Sunil . Mobile No :-7876130331 | Closed | Sharda Cotton Factory | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 34 | control panel wire check found the Controller on off switch no switch wire no 2B7 loose then the wire tight starting problem solved dg running (Update Pending) | Open | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
43 | North | 211741256 | 21/02/2025 | 125.4 | 4H.8042.C4../2420553 | voltage fluctuation Call by customer Name - Asgar Ali No - 9991098626 | Closed | RISHI LASER LTD. | SAAN Royal Power Solutions Private Limited - Sonipat | 5.51 | Voltage was going up and down, found that the phase was reversed (R-Y Phaseinterchanged) so corrected the phase, after that started the DG and trial on load, issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
11 | North | 211741424 | 21/02/2025 | 160 | 6H.8475.../2320002 | Emergency Stop Alarm Call By Customer Name :- Harish .. Mobile No :-9720331726 | Closed | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 93 | found Emergency stop Alarm show in Ems Display Due to Emergency switch wire is Loose After that We Re tight the Emergency switch wire | Closed | Kapil Solanki | [9 empty] | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
44 | North | 211741037 | 21/02/2025 | 250 | F6.8841.../2420020 | High Voltage Issue Call By Customer Name :- Monu Kumar Mobile No :-7088209582 | Closed | MANGLA APPARELS INDIA PVT LTD | SAAN Royal Power Solutions Private Limited - Sonipat | 112 | customer needs 396 voltage for his load as on load side, PCC used to burn on high voltage , set the voltage from 421 to 396, after that started the DG, working ok | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
7 | West | 211733736 | 19/02/2025 | 125.4 | 4H.8041.../2420315 | ECU Faulty issue call by customer Name:Kamlesh Kumar Number:7470909670 | Closed | JMS Mining Pvt Limited | Shree Engineering Service - Shahdol | 171 | Synchronization problem. Engine RPM is decreasing with respect to biasing voltage but not increasing, so calibrated ECU and enabled the sync setting, took trail of the DG found to be ok. | Closed | Vijay patil | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
13 | West | 211741071 | 21/02/2025 | 200 | 6H.8435.../2420054 | Abnormal sound issue Call by customer Name - Nilesh Kumar No - 7285053039 | Task Start | Advance Dental Export | Unique Techno Services Pvt Ltd. - Surat | 44 | There was an abnormal sound coming from the engine. So found that the charging alternator bolt was broken, replaced it. | Closed | Amit sandlya | Campaign check | [8 empty] | Alternator | 7 | 5 | 6 | 210 | High
15 | West | 211745190 | 22/02/2025 | 58.5 | T4.8941.../2423251 | Inspection/Maintenance | Closed | HOTEL SHILPA | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 10 | code 2791/18 Calibrated the ECU. | Closed | Jagdeep Saini | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
16 | West | 211741519 | 21/02/2025 | 35 | 3H.8902.../2421823 | Leakage Issue | Closed | SRI SAI AGRIGATE PROCESSORS | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 18 | Down side coolant drain cok found open . | Closed | Jagdeep Saini | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
18 | West | 211742485 | 21/02/2025 | 200 | 6H.8435.../2420228 | Electrical Problems | Closed | Zenith Concrete | Transcreek Engineers Pvt. Ltd. - Panvel | 69 | Error code 2802/4, 4225/1, 4225/1, Battery voltage found low due to charging alternator connectiuon 2B1 male female connector found loose so connect it properly. | Closed | Jagdeep Saini | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
1 | East | 211746068 | 22/02/2025 | 125.4 | 4H.8041.../2420393 | Starting/Stopping Issue | Task Start | Value Proc Solutions | Green Powerline - Dhemaji | 758 | SE visited and found 516166 code related to the ECU fault so cleared and flashed the ECU issue resolved. | OPEN | Ujjwal Das | ECU fault check | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
2 | East | 211745993 | 22/02/2025 | 25 | GP3.8702.../2421948 | Coolant leakage issue Call by customer Name - Vinod Kumar No - 8789971926 | Task Start | Kallu Lallu Babu | Globalline India Services Private Limited - Patna | 2 | Found Coolant seepage at byepass hose due so retighten clamp issue resolved | OPEN | Prabhakar Kumar | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
6 | West | 211737355 | 20/02/2025 | 125.4 | 4H.8041.../2420408 | Synchronization Issue Call Sevice Dealer Name :- Gokul Number:- 9098617551 | Closed | JMS Mining Pvt Limited | Shree Engineering Service - Shahdol | 149 | Synchronization problem. Engine RPM is decreasing with respect to biasing voltage but not increasing, so calibrated ECU and enabled the sync setting, took trail of the DG found to be ok. | Closed | Vijay patil | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
3 | North | 211685367 | 05/02/2025 | 57 | T4.8941.../2320247 | Over load issue Call By Customer Name :-Ram Gopal Panchal Mobile No :- 9410049917 | Task Start | Jyoti Moulds & Dies | Vidyut Engineers - Noida | 141.6 | Check the DG found over load alarm, Customer use the 80% above load Engineer Educate the Customer please maintain the load & below give the 80% | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
8 | East | 211755998 | 25/02/2025 | 30 | 3H.8902.../2422270 | Starting Issue Email By KGD Name:-Prajna Malik | Closed | Perennial Technologies Pvt. Ltd. | Gangpur Sales and Services - Jharsuguda | 247 | Customer was running DG at 10% load due to which EGR valve jammed this time EGR valve has been cleaned with diesel and refitted it and if will happen it will be on paid basis and educated the customer not to run DG under 50% load | CLOSED | Ujjwal Das | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
2 | South | 211684998 | 05/02/2025 | 25 | GP3.8702.../2421079 | voltage issue | Task Start | Sanjay J | Prasad Power Engineers - Davangere | LR | Flickering issue. Currently no full load available at customer side so avr which is suppose to be replace for checking is on hold | Tast Start | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
10 | South | 211678617 | 03/02/2025 | 35 | 3H.8902.../2422070 | Starting Problem Call by : Customer Name :Kalaivani Contact :9789410866 | Task Start | HOTEL VEERAS | Bharath Diesel Sales and Service - Karappakkam | 6 | Checked in normal.at same time abnormal noise for main alternator disc so disconnected the safety cover and checked the coupling disc is broken.so informed to alternator vendor must be change the main alternator coupling disc. and informed to the customer don't start the dg . | Task Start | Mr. NandhaGopal | Alternator issue | [8 empty] | Alternator | 7 | 5 | 6 | 210 | High
52 | South | 211655047 | 29/01/2025 | 400 | DV8.8542.C4../2420031 | Emergency Stop Alarm Issue Call By Customer Name :- Mahesh Mobile No :-8792438283 | Closed | Seshaasai Business Forms Pvt Ltd | Surya Power Services - Peenya, Bangalore | 25.15 | 516166/0 checked the dg emergency stop showing and error code from the engine controller and released the emergency stop showing connected the Ikonnect and reset the code finally started the engine observed on running without load condition and with load condition found working is satisfactory. | Closed | Mr. Anil Kumar H G | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
28 | South | 211676924 | 02/02/2025 | 20 | GP3.8601.../2421060 | Under voltage issue Call By Customer Name- Krishna Mobile No- 9346950589 | Open | P.Nagaraju | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 4.28 | Visited the site.as per customer complaint found observed the engine tripping due to 3 phase under voltage showing in the controller.crank the engine observed the output voltage is showing '0'volts due to diodes faulty. | Task Start | Mr. MD Saleem | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
12 | South | 211682324 | 04/02/2025 | 25 | GP3.8702.../2420375 | Fuel Leakage Call by Customer Name - Anil No - 6281873788 | Completed | PDR PROJECTS PRIVATE LIMITED | Sri Manjunath Technical Services - Ongole | 405 | Fuel leakage from filter O ring cut so change the filter. | Closed | Mr. MD Saleem | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
1 | North | 211683327 | 04/02/2025 | 320 | F6.8802.../2320079 | Starting Issue Call By Customer Name :- Jitendra kumar Mobile No:-8700684235 | Task Start | Yogesh Engineering Works | Paluck Technologies Ltd. - Faridabad | 195 | Low def level, required to be top-up | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
72 | South | 211647458 | 27/01/2025 | 82.5 | 5H.8901.../2420469 | Fuel indicator problem Call by : Customer Name : Hari kumar Contact : 6301409720 | Closed | Wilsons Farm | Ultimate Power Source - Tirupati | 90 | Fuel sensor failure. So replace the new fuel sensor. Now working ok | Closed | Mr. NandhaGopal | [9 empty] | Fuel Sensor | 7 | 6 | 5 | 210 | High
44 | North | 211674070 | 01/02/2025 | 30 | 3H.8902.../2420608 | Starting/Stopping Issue | Closed | AASTHA ENTERPRISES | SAAN Royal Power Solutions Private Limited - Rohtak | 126 | Customer complaint as DG Starts in morning in 3rd or 4th crank,on site,check fuel line & tightened all the Fuel pipe joints,asked customer to share video if that occurred again | Closed | Ved Prakash Gupta | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
9 | East | 211666294 | 31/01/2025 | 0 | 3H.8902.../2421094 | ENGINE HUNTING | Task Start | ELMECH ENGINEERS | Revenus Industries Pvt. Ltd. - Howrah | 1 | DG was hunting (rpm 1487-1505) and some abnormal sound was audible at alterntor end , Opened the alternator bracaket cover and start the engine, for 4-5 time engine rpm was also normal after that put a 50% load on it then engine running properly and rpm was normal but after the 2 hrs again hunting started suspected rpm is fluctuating due to alternator end abnormal sound need to replace ar recouple alternator, | OPEN | Prosanjit saha | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
3 | West | 211679003 | 03/02/2025 | 40 | 3H.8951.../2421166 | Starting/Stopping Issue | Task Start | Patel Poultry farm | Natraj Power Tech - Ratlam | 1 | 2791/18- Calibrated the ECU. | Closed | Vijay Patil | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
25 | North | 211667082 | 31/01/2025 | 160 | 6H.8475.../2320027 | Display Issue Call By Customer Name :- Amar Upadhyay Mobile No :-9560932926 | Closed | KANU KITCHEN KULTURE PVT LTD | Vidyut Engineers - New Delhi | 53 | Controller display before alarm proper work after any alarm show not all value | UNDER MONITORING | Kapil Solanki | KRM check | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
14 | South | 211641920 | 25/01/2025 | 320 | F6.8802.../2420228 | Load issue problem Call by : KGD Name : PANDIYARAJAN Contact :7010704256 Customer name : VISHNU mobile number : 9944457535 | Closed | SABARI WOOD AND PLYWOODS | Bharath Diesel Sales and Service - Karur | 9 | Customer side jerk load issue PF - .6, Advised to customer should be used only 80% load only to avoid future major breakdown,(customer side boiler motor 60 HP 2 NOS ,40 HP 1Motor not recommended for the above motors | Closed | Mr. NandhaGopal | [9 empty] | Motor | 9 | 6 | 7 | 378 | High
46 | South | 211656275 | 29/01/2025 | 30 | 3H.8902.../2420853 | Starting/Stopping Issue | Closed | K. G. D. Unikorn | Surya Power Services - Bommasandra, Bangalore | 10 | 157/14 error code shown in display so checked the rail pressure sensor voltage also checked fuel line found ok so clear the DTC. Under observation. | Closed | Mr. Anil Kumar H G | [9 empty] | Rail Pressure Sensor | 9 | 7 | 6 | 378 | High
71 | South | 211647996 | 27/01/2025 | 58.5 | T4.8941.../2423148 | Starting/Stopping Issue | Closed | COCHIN HYPER MARKET | G-Care Diesels Private Limited - Ernakulam | 1.4 | Found showing emergency stop alarm hence checked the emergency button found normal. checked and reset the alarm found again same issue so checked and found loose connection (2G,2A5,1CA 1H connections) hence checked and retighted and put cables tie. | Closed | Mr. Sanjaimon S | [9 empty] | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
10 | South | 211642137 | 25/01/2025 | 35 | 3H.8902.../2422075 | Other-MIL LAMP ON ALARM | Closed | Sri Mahalakshmi Marriage Hall | Bharath Diesel Sales and Service - Neyveli | 1.12 | 2791/18 flash the ECU | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
16 | North | 211683029 | 04/02/2025 | 125.4 | 4H.8041.../2420182 | Sound/Vibration Issue | Completed | Sunil Generators | OVN Industries Private Limited - New Delhi |  | Customer want to Def | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
4 | North | 211682646 | 04/02/2025 | 15 | GP3.8501.../2420905 | Starting/Stopping Issue | Closed | RIYASHAT GAURI | Espiem Engines & Machines (P) Limited - Agra | 54 | Customer side load issue over load Controller show the over current alarm, Suggest to the customer for load | Closed | Sudhir Awasthi | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
11 | South | 211683417 | 04/02/2025 | 125.4 | 4H.8042.C4../2420417 | Ad Blue Leakage Call By - Customer Name-Thimmappa Number -9945155152 | Task Start | Hotel Thimmappa | Prasad Power Engineers - Mangalore | 5 | Ad blue leakage in the header return pipe ,found that return pipe is not locking properly so put the new pipe now no leakage,and all so found that diesel cap is not setting properly put new cap that all so not locking and found that diesel cap neck had manufacturing defect | Completed | Mr. Anil Kumar H G | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
27 | North | 211665789 | 31/01/2025 | 125.4 | 4H.8041.../2420041 | Fuel Dash issue Call by Customer Name - Asim No - 9999229786 | Closed | Godrej Properties Ltd. | Paluck Technologies Ltd. - Faridabad | 1787 | Fuel level not showing in the controller When check & found Connector was removed refitted the same & check in controller showing properly | Closed | Kapil Solanki | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
12 | South | 211678482 | 03/02/2025 | 15 | GP3.8501.../2420368 | Electrical Problems | Task Start | Sam Issac | Electro Controls - Mavalikara | 29 | 2791/14, 2802/4 error code. Attended the site and checked the dg. Found the EGR issue. Remove the EGR valve check the valve and cleaned it. Then refitted the EGR valve and start. Presently the customer complaint is not found. Dg is all found ok. | Closed | Mr. Sanjaimon S | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
51 | South | 211655485 | 29/01/2025 | 25 | GP3.8702.../2421768 | Red lamp alram problem Call by : Customer Name : Kumar Contact : 9844613407 | Closed | LIONS BLOOD CENTER JEEVADHARA | Surya Power Services - Mysuru | 4 | 2791/18,5838/1 check the egr voltage is found ok and fitted with proper position in egr valve clip and clear the alarm in I Konnect tool and check the all external condition is found ok start and run the engine all working parameters condition is satisfied. | Closed | Mr. Anil Kumar H G | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
27 | South | 211661088 | 30/01/2025 | 15 | GP3.8501.../2421701 | Starting Problem & Smoking p[roblem Call by : Customer Name :Deepa Contact :9597691481 | Closed | SENTHILS PETRO | Madurai Electro Controls - Theni | 80 | Checked the engine starting issue.disel line problem.disel tank to dc motor connecting disel hose bend.so disel supply not properly.removed the hose and adjusted.refitted the hose properly.after start the engine running normal.no starting issue.checked oil level ok.checked air cleaner element ok. | Closed | Mr. NandhaGopal | [9 empty] | Motor | 9 | 6 | 7 | 378 | High
9 | North | 211662329 | 30/01/2025 |  | GP3.8301.../2420620 | CHARGING PROBLEM | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | LR | Found Sweep stuck alarm check the rod found no, any issue but now DG not start Change the ECU not to be resolve | open | Sudhir Awasthi | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
9 | West | 211633607 | 23/01/2025 | 625 | DV0.8501.C4../2420058 | Fuel Leakage issue Call By service dealer Name :- Kamlesh Mobile No :- 7567488849 | Task Start | Transworld Logistics Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Baroda | 15 | Fuel leakage from feed pump replaced and issue solved | Closed | Amit shandilya | Failed part | [8 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
9 | South | 211678988 | 03/02/2025 | 125.4 | 4H.8041.../2420199 | Fuel Level Problem Call by : Customer Name :Sudhi Contact :8943649197 | Closed | POWERMECH DIESELS | G-Care Diesels Private Limited - Ernakulam | 20 | Attended the site checked problem. error codes 3031/14 and 1761/16 alarms in the controller shows adblue temperature is high and low adblue level. checked adblue level and is 100 percentage and temperature is 31degree. Checked QLT sensor of the adblue tank. clips checked . a general inspection forbthe dg is carried out. since the temperature and level is corrected we flashed the ecu to the latest version. | Closed | Mr. Sanjaimon S | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
22 | South | 211677648 | 03/02/2025 | 30 | 3H.8902.../2420998 | Leakage Issue | Closed | P. Naryanan | G-Care Diesels Private Limited - Calicut | 135 | Check the site and fuel leakage found in fuel pipe tightened now ok | Closed | Mr. Sanjaimon S | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
23 | South | 211661578 | 30/01/2025 | 250 | F6.8841.../2420102 | ECU Protect | Task Start | PYARELAL FOAMS PVT LTD | Electro Controls - Palakkad | 12.8 | 3031/14,3364/8 Ecu protect alarm some quantity of def removed and cleaned quality sensor cleared alarm using I connect tool started the engine and was satisfied with the performance. | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
33 | North | 211673131 | 01/02/2025 | 125.4 | 4H.8041.../2420745 | Starting/Stopping Issue | Closed | JAIN GENERATOR HIRING CO.. | OVN Industries Private Limited - New Delhi | 1510 | Maintenance due alarm reset the alarm & Air lock in fuel line so, remove the air | Closed | Kapil Solanki | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
16 | North | 211678030 | 03/02/2025 | 125.4 | 4H.8041.../2320088 | Tripping Isssue Call By Customer Name :- Ghopal Kishan Mobile No:-9650991118 | Closed | Shramdeep Appartments | Vidyut Engineers - Noida | 172 | Check the Dg found Under frequency alarm reset the alarm after trial on load found no any issue | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
47 | North | 211673185 | 01/02/2025 | 10 | GP3.8301.../2420086 | Error code issue | Closed | Axis Bank Ltd | Industrial Power Solutions - LUDHIANA | 67 | Y-Phase Voltage drop(215V) on load so settled voltage on AVR Card ,DG running fine after correctoin | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
34 | North | 211666979 | 31/01/2025 | 20 | GP3.8601.../2420252 | Leakage Issue | Closed | Raheja Textiles | Industrial Power Solutions - LUDHIANA | 74 | Fuel Leakage found due to overfilling of fuel so reduce the same & emergency Stop activated so release the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
29 | North | 211678658 | 03/02/2025 | 125.4 | 4H.8042.C4../2420692 | Starting/Stopping Issue | Task Start | Bharat Tech and Engineering | Suraj Moters Stores - Leh | 95 | Customer complaint as black smoke issue , on site;oil level found above H-Mark & 1st no. cylinder head,one cross head dislocated from its position & a broken valve at the stem | Open | Ved Prakash Gupta | Detail to be check | [8 empty] | Cylinder Head | 9 | 4 | 6 | 216 | High
30 | South | 211676859 | 02/02/2025 | 160 | 6H.8475.../2420197 | Starting/Stopping Issue | Task Start | MAGIC FRAMES CINEMAS | G-Care Diesels Private Limited - Malappuram | 186 | Founded Charging alternator adjusting Lacha Brocken and Founded (516166/0, 516160/0) Error codes.Connected I connect Tool and Cleared Error codes and Flashed ECU. Now Engine running performance ok. | Task Start | Mr. Sanjaimon S | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
18 | South | 211677796 | 03/02/2025 | 125.4 | 4H.8041.../2320068 | Display problem Call by : Customer Name :Sudhi Contact :8943649197 | Task Start | POWERMECH DIESELS | G-Care Diesels Private Limited - Ernakulam | 33.1 | Attended the site .Checked problem Adblue level is not showing in the controller.A general inspection is carried out . So Kg640C controller is flashed with the new file. Observed two alarms alblue level low alarm and but adblue is full in the tank and are cleared with the I Konnect tool. Then started the dg and tested . dg is running normally but adblue high temp flt alarm showing. So checked adblue condition and is ok. Tool is again connected and ecu flashed to the latest version.Then checked and found no alarms . Started again and tested . Now no errors or issues .Dg is running normally. | Closed | Mr. Sanjaimon S | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
50 | South | 211655726 | 29/01/2025 | 45 | 3H.8951.../2421421 | ALARM ISSUE | Closed | Raini Industries India Private Limited | Net Work Diesels - Chennai | LR | DURING OBSERVATION,FOUND ALARM ISSUE 5538/1 AND 2791/18.CHECKED ALL WIRING HARNESS,BATTERY CONNECTION,ECU WIRING HARNESS.REMOVED THE EGR VALUE CONNECTOR.BUT ISSUE IS NOT RESOLVED.HENCE FLASHED THE ECU WITH THE HELP OF NEW CALIBRATION FILE.ISSUE RESOLVED. | Closed | Mr. NandhaGopal | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
16 | North | 211676831 | 02/02/2025 | 20 | GP3.8601.../2420547 | Starting issue Call by customer Name: SR Singh Number: 7678373367 | Open | TRINITY CALCIUM | Pratap Diesels Pvt. Ltd. - Alwar | 290 | Check in the sump found metal particles, then check & found oil pump gear was damage so, replace the pump, Now abnormal sound from the Engine | open | Gourav Sharma | [9 empty] | Oil Pump | 8 | 6 | 5 | 240 | High
17 | North | 211677916 | 03/02/2025 | 320 | F6.8802.../2420127 | Starting/Stopping Issue | Task Start | Vikas Polyplast Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 17.3 | found intake manifold gaskets suspected so change the gaskets and fill adblue in urea tank. After that take load trial on site, in first trial 130 kw load given to the DG. 2nd trial 145kw load given to the DG and DG trip on this load. 3rd trail same load given to the DG and that time DG also trip and alarm showing under voltage and frequency. DG is under rating customer already know. | open | Gourav Sharma | [9 empty] | Load | 8 | 6 | 5 | 240 | High
6 | East | 211663200 | 30/01/2025 | 125.4 | 4H.8042.C4../2420841 | Low Fuel Level Call By Customer Name :- Rajib Das Mobile No :-8638291760 | Closed | National Highways Infra Projects Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 30 | Low fuel level alarm was on display so checked the mechanical fuel level which was above 50% so checked the resistance of the sensor found 118 Ohm which was OK then check voltage at its connector which was 7-8 V so on checking found 25 no. wire was loose at controller jack 25 no. pin after tightening issue resolved. | CLOSED | Ujjwal Das | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
6 | South | 211684352 | 05/02/2025 | 58.5 | T4.8941.../2421869 | Starting/Stopping Issue | Task Start | SAI YASODHA PROPERTIES | Laxmi Diesels - Visakhapatnam | 1 | Visited the site along with Sunbeam Ramesh sir and checked The DG set found painting was burned due to heat near Exhaust manifold and Explained customer it is coming from Kirloskar plant only and it is tested in Kirloskar plantso there is no Old spares used in our DG set. | Closed | Mr. MD Saleem | [9 empty] | Exhaust Manifold | 7 | 6 | 5 | 210 | High
15 | South | 211678008 | 03/02/2025 | 30 | 3H.8902.../2420853 | Starting Issue Call By Customer Name :- Sharma Mobile No :-9258686715 | Task Start | K. G. D. Unikorn | Surya Power Services - Bommasandra, Bangalore | 11 | Visit the site check the engine not starting due to Under speed alarm and fail to stop alarm so check and found controller backside 4no wire loose so tighten the same now dg working ok. | Closed | Mr. Anil Kumar H G | GOEM issue | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
2 | North | 211666029 | 31/01/2025 | 125.4 | 4H.8042.C4../2420013 | Electrical Problems | Closed | BABA AMARNATH ENTERPRISES | Pratap Diesels Pvt. Ltd. - Alwar | 427.12 | ECU fault alarm & Low def level top up the def & clear the fault by i-konnect tool | Closed | Gourav Sharma | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
12 | West | 211636306 | 23/01/2025 | 400 | DV8.8542.C4../2420069 | CONTROLLER ISSUE | Task Start | Toll India Logistics Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Ankleshwar | 13 | display not working need to replce the Controller. | Closed | Amit shandilya | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
44 | South | 211673370 | 01/02/2025 | 125.4 | 4H.8041.../2320068 | Starting/Stopping Issue | Closed | POWERMECH DIESELS | G-Care Diesels Private Limited - Ernakulam | 33 | Checked controller panel. Found 102 no ferrul connection in interface card is loosen. Tighten the connection. And rest controller. | Closed | Mr. Sanjaimon S | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
5 | South | 211665702 | 31/01/2025 | 25 | GP3.8702.../2421498 | Air Compression Issue. Call by customer. Name:- Sethu G ... Mobile No.:-9777766024 | Closed | Mythri Motors | G-Care Diesels Private Limited - Muvattupuzha | 11 | Attended the site checked dg.found unbalanced load 20A,8A,1A .advice the customer to balance the load.checked air compressor found phase reverse alarm on compressor controller advice the customer to rectify it.need dg inspection after rectify electrical issues. | Closed | Mr. Sanjaimon S | KRM check | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
26 | North | 211665616 | 31/01/2025 | 125.4 | 4H.8042.C4../2420273 | Low Urea Level Issue Call By Customer Name - Pavan Number - 7678692190 | Closed | CHAUHAN DIESEL SALES & SERVICE | Vidyut Engineers - Noida | 37.5 | Low def level topup the def | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
40 | North | 211661665 | 30/01/2025 | 500 | F6.8843.C4../2420001 & 24200001 | Fuel Tank Issue & Adblue Level Issue Call By Service Dealer Name - Sukhvinder Singh Number - 9991740559 | Closed | M. P. Institute of Medical Research | SAAN Royal Power Solutions Private Limited - Karnal | 109 | Fuel Level showing on controller 400% but DEF Connector continuity found ok;Flash the controller with latest version , DG is running fine on Load with all parameter showing correct on controller | Closed | Ved Prakash Gupta | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
61 | South | 211651596 | 28/01/2025 | 20 | GP3.8601.../2421083 | Starting/Stopping Issue | Closed | Jyothi hospital | Laxmi Diesels - Srikakulam | 12 | Checked the dg found that dg not started due to kg645 controller showing high fuel level alarm so open the fuel float and clean and fitment the same fuel float then started the dg running found ok | Closed | Mr. MD Saleem | KRM check | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
67 | South | 211650768 | 28/01/2025 | 15 | GP3.8501.../2421822 | Fuel Leakage Problem Call by : Customer Name :Sumesh Sir Contact :9496557111 | Closed | MOONSTAR PETROLEUM | G-Care Diesels Private Limited - Muvattupuzha | 4.36 | Checked and found fuel leaking through the high pressure pipe connecting to the fuel injector. Tighten the nut and leak arrested. Then started ad checked for half an hour. Now found no leakages. Photo | Closed | Mr. Sanjaimon S | [9 empty] | Injector | 9 | 8 | 5 | 360 | High
48 | South | 211673049 | 01/02/2025 | 0 | GP3.8702.../2421960 | EGR CONNECTOR BROKEN | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected the generator and found EGR valve assembly connector found damaged during the transit time,so removed the damaged EGR valve assembly and replaced new EGR valve assembly. | Closed | Mr. NandhaGopal | [9 empty] | EGR | 9 | 7 | 5 | 315 | High
11 | WEST | 211664238 | 31/01/2025 | 30 | 3H.8902.../2422024 | Display Issue Call By Customer Name :- Gopal Mobile No :- 9221070922 | Closed | SHREE MANGLAM BUILDCON (I) PVT LTD | Unique Techno Services Pvt Ltd. - Baroda | 8.9 | Emergency alarm so refieted the connector and 2791/18- calibrated the ECU. | closed | Amit sandlya | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
10 | WEST | 211665153 | 31/01/2025 | 625 | DV2.8552.C4../2320005 | Leakage Issue | Task Start | ADANI RENEWABLE ENERGY FIFTY SEVEN LIMITED | Unique Techno Services Pvt Ltd. - Gandhidham | 2017 | Fuel leakage from leak off pipe so today engineer will visit with pipe. | closed | Amit sandlya | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
7 | North | 211678677 | 03/02/2025 | 57 | T4.8941.../2420096 | VOC -BRUSHLESS ALTERNATOR - LOW VOLTAGE Cstomer Name -Mahesh Singh Customer Number-9452111389 Mode- SR Generated through CDI calling. | Task Start | Jey Tee Power Plus Pvt Ltd | OVN Industries Private Limited - New Delhi | 65.4 | Engineer visit the site check & found When customer gives the load RPM drop approx 1400 & DG not taking the load load 20KW | open | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
37 | North | 211666062 | 31/01/2025 | 58.5 | T4.8941.../2421469 | Leakage Issue | Closed | VP. Broadband Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 7.5 | Fuel leakage found from water separator , open the sensor from that & check the condition of O-Ring,found ok,clean the sensor & re-fitted the same ,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Fuel Leakage | 10 | 8 | 7 | 560 | High
66 | South | 211651374 | 28/01/2025 | 58.5 | T4.8941.../2421002 | AMF panel problem Call by : Customer Name : Basav raj Contact : 9902325554 | Closed | Kamadhenu Cutting Tools Pvt. Ltd. | Surya Power Services - Peenya, Bangalore | 64 | Checked DG set controller KG 645 found mains sensing program disable so engine not start | Closed | Mr. Anil Kumar H G | [9 empty] | Controller | 7 | 6 | 5 | 210 | High
6 | North | 211678730 | 03/02/2025 | 200 | 6H.8435.../2320011 | Preventive Maintenance Call By Customer Name :- Avinash . Mobile No :- 8750913517 | Closed | Permeshwar Creations Private Limited. | Vidyut Engineers - Noida | 1126 | Low def level recommended for def | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
39 | North | 211662518 | 30/01/2025 | 30 | 3H.8902.../2420071 | Oil Leakage Issue Call By Customer Name ;- Saksham Gulati No :- 9812451496 | Closed | Vishnu Carpets | SAAN Royal Power Solutions Private Limited - Panipat | 175.8 | Oil throwing from exhaust site(Slightly) due to DG running at very low Load(5-12 Amp),same educated to customer to run DG on minimum 25% | Closed | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
20 | North | 211676893 | 02/02/2025 | 250 | F6.8841.../2320021 | ECU shut down Alarm Call By Customer Name :- Nasim ... Mobile No :-8178330262 | Closed | ASJK. corporate Service Pvt. Ltd. | Vidyut Engineers - Noida | 538.81 | Low def level topup the def above 50% & Educate the customer about def & Def tank cap | Closed | Kapil Solanki | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
50 | South | 211672922 | 01/02/2025 | 82.5 | 5H.8901.../2420419 | Genset Trip | Closed | MR FREEZE ZONE | G-Care Diesels Private Limited - Calicut | 40 | Found fist starting time 0.5,8,0.9,then cut machine for 30 minutes and trail running done found sudden load amps ,20,amps load is 21,29,22,kw is 3.1,5.1,3.2, voltage is 415,410, 415 advised customer to balance the load and take more trail reading in different condition and not the reading.problem under observation | Closed | Mr. Sanjaimon S | [9 empty] | Load | 8 | 6 | 5 | 240 | High
5 | WEST | 211665253 | 31/01/2025 | 160 | 6H.8475.../2420199 | Tripping issue Call By Customer Name ;- Vinesh .. No :- 9925610485 | Closed | V.S.SHAH & CO. | Unique Techno Services Pvt Ltd. - Baroda | 214 | Low DEF level. |  | Amit sandlya | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
7 | East | 211678028 | 03/02/2025 | 20 | GP3.8601.../2420741 | Automation Issue Call By Customer Name :- Surykant .. Mobile No :- 9153922722 | Task Start | AAROHI HOSPITALITY | Globalline India Services Private Limited - Purnia | 56 | Emergency stop alarm - its was showing frequently many time this complaint was raised by customer to SE checked for loose connection it resolved but after that again same issue so provide direct supply to emergency switch to resolve the issue | CLOSED | Prabhakar Kumar | [9 empty] | Emergency Stop Alarm | 10 | 8 | 7 | 560 | High
25 | North | 211664351 | 31/01/2025 | 57 | T4.8941.../2420096 | Starting/Stopping Issue | Closed | Jey Tee Power Plus Pvt Ltd | OVN Industries Private Limited - New Delhi | 64.2 | Jerk load on the DG, Educate the Customer | Closed | Kapil Solanki | [9 empty] | Load | 8 | 6 | 5 | 240 | High
5 | South | 211680594 | 04/02/2025 | 200 | 6H.8435.../2420188 | COOLANT LEAKAGE | Completed | Rajana Raju. | Laxmi Diesels - Visakhapatnam | 9 | Checked the engine thoroughly found coolant leakage and balance Tank getting empty for every time while DG starting and stoppingstarted the engine with out load and found coolant leakage near bypass Hose due clamp loose Retighted and found ok load trial not taken due no load customer asking come tomorrow for load trial that is on 5 or 6 February | Closed | Mr. MD Saleem | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
18 | North | 211675124 | 01/02/2025 | 20 | GP3.8601.../2420279 | Loading issue Call by customer Name - Brijesh Kumar Number - 6392429266 | Closed | VIPUL KAUSTUB AGRO PRIVATE LIMITED | Excel Diesel Private Limited - Faizabad | 476 | Overload & Unbalance load Suggest to the customer for Balance the load | Closed | Sudhir Awasthi | [9 empty] | Load | 8 | 6 | 5 | 240 | High
41 | South | 211658540 | 29/01/2025 | 20 | GP3.8601.../2420497 | Starting Problem Call by : Customer Name : Raj kumar Contact : 8608924888 | Completed | Meras Plugins Pvt. Ltd. | Net Work Diesels - Chennai | 56 | ENGINE NOT STARTING DUE TO AIR LOCK IN FUEL LINE SO REMOVED THE AIR LOCK IN FUEL PUMP STARTED THE ENGINE WITH IN 30 SECONDS ONLY DG RUNNING AGAIN ENGINE TRIP (INTERMEDIATE) SO NEEDS TO BE FLASH THE ECU UNIT. Fuel filter is in bad condition as customer not done A checked. | Closed | Mr. NandhaGopal | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
36 | South | 211659543 | 30/01/2025 | 20 | GP3.8601.../2420354 | Genset Trip | Task Start | Badriya Juma Masjid Kuppetti | Prasad Power Engineers - Puttur | 201 | Engine tripping due low charg alternator voltage check the charging alternator failure then flat charging alternator fitment and check the other parameters found ok then started the engine found ok | Task Start | Mr. Anil Kumar H G | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
26 | South | 211677560 | 03/02/2025 | 15 | GP3.8501.../2421401 | Starting issue Call by customer Name: AJOMON JOSEPH . Number: 9400181789 | Task Start | AJOMON JOSEPH | Electro Controls - Thodupuzha | 11.9 | Found emergency stop switch deactivate, checked wiring harness ok. DG take trail run ok good. | Task Start | Mr. Sanjaimon S | [9 empty] | Wiring Harness | 7 | 6 | 5 | 210 | High
45 | South | 211673138 | 01/02/2025 | 30 | 3H.8902.../2422192 | AMF Panel Problem Call by : Customer Name :SURESH Contact :9972634148 | Closed | K JAYAMMA CIVIL CONTRACTOR | Surya Power Services - Peenya, Bangalore | 9 | 2791/18, 5838/1 error code flash the ECU | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
13 | North | 211678121 | 03/02/2025 | 58.5 | T4.8941.../2420950 | Starting issue Call by customer Name: Jitendra Number: 9810870765 | Task Start | K. T. Power Sales and Services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 7 | Controller display not proper working, after start the Dg Controller display blank- | open | Kapil Solanki | Contrast check | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
23 | North | 211673277 | 01/02/2025 | 30 | 3H.8902.../2420319 | Starting/Stopping Issue | Closed | The Heavens Shakes | Pratap Diesels Pvt. Ltd. - Alwar | 39 | Check & found Low coolant in Recovery box & Distribution XDBK connection loose tightness to be all then issue resolve | Closed | Gourav Sharma | [9 empty] | Coolant | 8 | 7 | 6 | 336 | High
14 | West | 211626943 | 21/01/2025 | 500 | DV8.8501.C4../2420002 | Starting Issue Call By Service Dealer Name :- ABID Mobile No :7558590241- | Closed | M/s Silverio Developers Pvt. Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 69 | Cumminication error from ECU/DCU, issue not resolved. Visit again yesterday and found DCU2 not getting power supply from interface box so loop the wire from DCU2 switch point to 5 pin teco connector and found T4 and T6 sensor conn. Interchanged correct the same and dosing module found faulty so engg. will visit today for D.M. replacement. | Closed | Jagdeep Saini | ECU fault | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
46 | South | 211673130 | 01/02/2025 | 30 | 3H.8902.../2422106 | AMF Panel Problem Call by : Customer Name :SURESH Contact :9972634148 | Closed | K JAYAMMA CIVIL CONTRACTOR | Surya Power Services - Peenya, Bangalore | 8.9 | 2791/18, 5838/1 error code flash the ECU | Closed | Mr. Anil Kumar H G | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
4 | South | 211665806 | 31/01/2025 | 250 | F6.8841.../2420434 | Starting/Stopping Issue | Closed | Gopalakrishna Kusuma Memorial Hospital | Laxmi Diesels - Srikakulam | 8 | Electrical panel Board inside Fuse Burn(+ve).And New Fuse fietment Dg running condition Load trial 20 minutes and all systems are found okk | Closed | Mr. MD Saleem | [9 empty] | Load | 8 | 6 | 5 | 240 | High
25 | South | 211677564 | 03/02/2025 | 125.4 | 4H.8041.../2420398 | Starting Issue Call By Customer Name - Sant Kumar Number - 7899956153 | Task Start | T. NARENDRA BHAT | Prasad Power Engineers - Shimoga | 13 | 520528/31 shown in display. Also found SCR pipe melt. So replaced the Pipe & for error code flash the ECU. | Closed | Mr. Anil Kumar H G | GOEM issue | [8 empty] | ECU | 10 | 9 | 7 | 630 | High
2 | WEST | 211665253 | 31/01/2025 | 160 | 6H.8475.../2420199 | Tripping issue Call By Customer Name ;- Vinesh .. No :- 9925610485 | Closed | V.S.SHAH & CO. | Unique Techno Services Pvt Ltd. - Baroda | 214 | v belt loose so tight the belt. DEF Level low so top up DEF | closed | Amit sandlya | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
22 | North | 211673533 | 01/02/2025 | 58.5 | T4.8941.../2420850 | Electrical Problems | Closed | Munna Smriti Sansthan. | Espiem Engines & Machines (P) Limited - Etawah | 103 | Air lock in fuel line remove the air then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Fuel Line | 9 | 7 | 6 | 378 | High
37 | North | 211665705 | 31/01/2025 | 58.5 | T4.8941.../2423329 | Power Supply Issue Call By Customer Name - Niraj .. Number - 7876907355 | Closed | SANT AUTO | Megatron Engineers - Amb | 3 | Voltage drop on load from 415V to 384 V ,found neutral link common plate screw missing so fitted properly after customer arrange the screw,Voltage found ok on load (Update Pending) | open | Ved Prakash Gupta | [9 empty] | Load | 8 | 6 | 5 | 240 | High
10 | East | 211678675 | 03/02/2025 | 160 | 6H.8475.../2420162 | V Belt found loose & Preventive Maintenance Email By - GOEM Name - Arup Kr. Ray | Task Start | Ms Ankur Enterprise | Hibreed Engineering Pvt. Ltd. - Nagaon | 196 | V belt found loose because eyebolt of the charging alternator found broken so replaced the eye bolt issue resolved (after replacing found no vibration or misalignment of the pulley issue raised may be eye bolt quality or the extra tightening of the belt) | CLOSED | Ujjwal Das | [9 empty] | Alternator | 7 | 5 | 6 | 210 | High
2 | South | 211666536 | 31/01/2025 | 58.5 | T4.8941.../2420593 | Over load issue Call by customer Name: Pawan Number: 8088277307 | Closed | ADISHAKTI CARS PVT LTD | Prasad Power Engineers - Davangere | 137 | Customer using Over load. Customer side issue. | Closed | Mr. Anil Kumar H G | [9 empty] | Load | 8 | 6 | 5 | 240 | High
68 | South | 211650753 | 28/01/2025 | 5.5 | CC1.1013.../2400430 | Voltage PrCall by : Dealer Name :Govindan Contact : 9790033065 oblem | Closed | ICICI Bank | Bharath Diesel Sales and Service - Pattanur | 10 | Control panel EB contractor auxiliary and auto sansing wiring problem so auto not work contactor auxiliary and auto sansing wire change proper wiring connect after dg auto start stop auto power changeover working ok DG started and tested on load DG performance is normal | Closed | Mr. NandhaGopal | [9 empty] | Load | 8 | 6 | 5 | 240 | High
7 | South | 211680554 | 04/02/2025 | 30 | 3H.8902.../2420241 | low fuel level | Task Start | Rohans Madhuram House | Laxmi Diesels - Visakhapatnam | 43 | Fuel available at 70% in tank mechanical float working good check resistance 130ohms but controller showed OPEN CIRCUIT and also KRM SHOWING OPEN CIRCUIT but no error codes any DG running ok need ikonnect tool | Closed | Mr. MD Saleem | GOEM issue/one pager | [8 empty] | Controller | 7 | 6 | 5 | 210 | High
9 | North | 211681336 | 04/02/2025 | 320 | F6.8802.../2420060 | Emergency switch faulty | Open | Rudra Construction | Gen Powers - Nabha,Patiala | 282 | Emergency switch element was defective so, replace with same then issue resolve | Closed | Ved Prakash Gupta | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
3 | South | 211681160 | 04/02/2025 | 250 | F6.8841.../2420399 | Ad blue level variation | Task Start | St. AUGUSTINES FORANE CHURCH | Electro Controls - Kottayam | 110 | Attended the site check the engine, found that issue Ad blue level variation on display shown in 100%, check the def tank for Ad blue level (actual 50% in physical) ,and remove the QLT sensor and check ,some tightness for the Ad blue level needle ,then clean and check for working ,then fit and tight then connect the in connections, clear the error codes and Start the engine, it's working normally ,engine good condition | Closed | Mr. Sanjaimon S | [9 empty] | DEF | 8 | 7 | 5 | 280 | High
1 | West | 211630784 | 22/01/2025 | 750 | DV2.8501.C4../2420057 | Voltage Fluctuation | Completed | Nyati Hotels & Resorts Pvt. Ltd. | Dynapulse | 24 | Genset was synced properly but genset was hunting during biasing. Voltage fluctuation was 15 RPM at 2.5V speed biasing. Checked voltage at terminals 615 and 620 and found same voltage on both sides at ECU number 6 chamber connector. Replaced ECU with float ECU but problem is same." | OPEN | Jagdeep Saini | [9 empty] | ECU | 10 | 9 | 7 | 630 | High
1 | South | 211681484 | 04/02/2025 | 15 | GP3.8501.../2420910 | Starting/Stopping Issue | Task Start | Dodla Dairy Limited | Bharath Diesel Sales and Service - Dharmapuri | 68.5 | Attend the site start the DG is Crank only.Amper alarm on display.check fuel level 50 Percentage.chrck efficient Fuel pump is not functioning.pump input is 12.5volt.Direct check to the efficient Fuel pump.Not functioning pump. Tommorow SE will replace the pump. | Tast Start | Mr. NandhaGopal | [9 empty] | Fuel Pump | 8 | 6 | 5 | 240 | High
29 | South | 211716413 | 14/02/2025 | 58.5 | T4.8941.../2422751 | Canopy lamp failure | Closed | D K Lodge | Electro Controls-Tirupur | 5.46 | Checked and found canopy lamp wiring line, Dc voltage, wiring connector checked ok. Lamp internal failure.so, New one replased,lamp working Normal.start the Engine found Normally | Closed | Mr. Sanjaimon S | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
21 | South | 211717106 | 14/02/2025 | 30 | 3H.8902.../2420029 | Starting Problem Call by : Customer Name : Narayana Contact : 9908544730 | Task Start | St. Joseph Degree College | Ultimate Power Source - Kurnool | 129 | Under Speed alarm. Fuel is less then 30% so Air lock issue remove the airlock no DG working ok. | Closed | Mr. NandhaGopal | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
26 | South | 211716661 | 14/02/2025 | 320 | F6.8802.../2420090 | coolant leakage | Completed | The Name of Nord Angilia Education Infrastructure Pvt. Ltd. | Laxmi Diesels - Visakhapatnam | 107.59 | Attended the site and checked the engine and found the problem is coolant leak found the radiator bottom hose pipe and retired the house clamp and checked all system and started the engine and checked all leaks and found the engine running performance is normal | Closed | Mr. MD Saleem | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
54 | South | 211746324 | 22/02/2025 | 58.5 | T4.8941.../2421041 | Inspection/Maintenance | Task Start | Shaik Adam Basha. | Ultimate Power Source - Ananthapuramu | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
16 | North | 211717074 | 14/02/2025 | 15 | GP3.8501.../2420049 | Starting Issue Call By Customer Name :-Mr. Ashok Galoth . Mobile No :-9730101552 | Closed | Ashok Galoth. | Paluck Technologies Ltd. - Ghaziabad | 73 | Found Battery voltage low, battery charger connection done but supply off from customer end, Educate the Customer for same | Closed | Kapil Solanki | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
6 | North | 211717878 | 14/02/2025 | 58.5 | T4.8941.../2423285 | Abnormal sound issue | Closed | Bharat Associates Pvt.Ltd. | Espiem Engines & Machines (P) Limited - KANPUR | 20 | Abnormal sound from the Canopy doorlock bolt was loose so, tightness the same | Closed | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
14 | East | 211718842 | 14/02/2025 | 40 | 3H.8951.../2421571 | Automation issue Called by customer Name : EC FARM Number : 8327779009 | Cancelled | SHYAM POWER SOLUTION | Gangpur Sales and Services - Bhubaneswar | 46 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
14 | North | 211676872 | 02/02/2025 | 82.5 | 5H.8901.../2420649 | Starting Issue Call By Customer Name :-Brijesh Mishra Mobile No :-7990841596 | Task Start | KALYAN JEWELLERS INDIA LTD | S. R Engines Sales And Service - LUCKNOW | 6.27 | Battery terminal loose tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
18 | South | 211734602 | 19/02/2025 | 30 | 3H.8902.../2421382 | DG not starting | Open | ATC Telecom Infrastructure Private Limited | Ultimate Power Source - Kurnool |  | No issue. SR to be Cancelled | Open | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | North | 211678793 | 03/02/2025 | 125.4 | 4H.8041.../2420197 | Mobil Consumption Issue & Hunting Issue. Call By Customer. Name:-Lalit Tyagi Mobile No.:-9810138700 | Open | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad |  | Cancelled- Customer Approvel not received | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
21 | South | 211738516 | 20/02/2025 | 15 | GP3.8501.../2421099 | Starting Problem Call by : Customer Name :Somasuthiram Contact :8438114639 | Open | The Karur Vysya Bank Limited | Electro Controls - Nagercoil | 40 | Air lock issue.air lock released.engine running condition ok.Intimate to the customer maintain the fuel level. | Closed | Mr. Sanjaimon S | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
23 | South | 211737937 | 20/02/2025 | 25 | GP3.8702.../2420715 | Starting/Stopping Issue | Closed | ATC Telecom Infrastructure Private Limited | Ultimate Power Source - Vellore | 18 | Visit about the genset for engine not starting problem check the engine for air lock problem after release the air lock is ok checked the all parameters working condition is normal started the engine running condition is normal | Closed | Mr. NandhaGopal | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
42 | North | 211719585 | 15/02/2025 | 15 | GP3.8501.../2421195 | Battery Charger | Completed | M/S VISHAL SHAMIYANA HOUSE | S. R Engines Sales And Service - Gorakhpur | 17 | found battery charger and AVR card, mains dg fuse block burnt due to mains supply High voltage so replace the AVR card and both fuse block then start dg set and check now dg set working ok but battery charger required to replace all work on paid basis | Open | Sudhir Awasthi | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
41 | North | 211719668 | 15/02/2025 | 58.5 | T4.8941.../2421281 | Di seal Leakage Issue Call By Customer Name :-Apruv . Mobile No :- 9910350990 | Closed | Manoj Gupta | Vidyut Engineers - Noida | 26 | Found no any diesel leakage, Diesel overflow KRM unit not update | Closed | Kapil Solanki | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
25 | South | 211736859 | 20/02/2025 | 25 | GP3.8702.../2421572 | MCB Lamp Alarm Issue Call by customer. Name:- Kartik Mobile No.:- 7899308318 | Closed | Charan kumar | Surya Power Services - Kalyan Nagar | 10 | 5838/1 error code topup. Clear the DTC. | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
29 | South | 211735044 | 19/02/2025 | 20 | GP3.8601.../2420675 | Starting Problem Call by : Customer Name : Karthik Contact : 9885598353 | Closed | S. Satyanarayana Murthy | Ultimate Power Source - Nellore | 33 | Oil filter loose tighten the connection found ok. Engine starting ok. | Closed | Mr. NandhaGopal | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
35 | North | 211720166 | 15/02/2025 | 750 | DV2.8501.C4../2420029 | Wire Burn Issue Call By Customer Name - Sonu Number - 6390495480 | Closed | ABNC PROPERTY MANAGEMENT PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 49 | Found no any in issue in Dg but found only Battery terminal loose | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
30 | South | 211734971 | 19/02/2025 | 15 | GP3.8501.../2421008 | Starting Problem Call by : Customer Name : Ganesh Contact : 9443450494 | Open | KAVIN ESTATE | Bharath Diesel Sales and Service - Palani | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
31 | South | 211734068 | 19/02/2025 | 15 | GP3.8501.../2421374 | Red Lamp Alarm issue Call By Customer Name :- Umesh Mobile No :- 9742391076 | Cancelled | Hindustan Pencills PVT LTD | KALA Care Global LLP - Hubli | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
32 | South | 211733667 | 19/02/2025 | 25 | GP3.8702.../2420754 | DG ISSUE | Task Start | ATC Telecom Infrastructure Private Limited | Surya Power Services - Mysuru | 27 | Visit the site check the ac voltage is low and remove the altarnator in side wire is loose Connection then reconnected the altarnator wire found ok | Closed | Mr. Anil Kumar H G | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
29 | North | 211720872 | 15/02/2025 | 30 | 3H.8902.../2320082 | Starting/Stopping Issue | Task Start | EDS Construction Private Limited | Vidyut Engineers - New Delhi | 1242 | Found air lock in fuel line remove the air & Battery terminal loose tightness & clean the terminal | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
35 | South | 211737210 | 20/02/2025 | 250 | F6.8842.C4../2420022 | Abnormal sound problem Call by : Customer Name : Girish Contact : 9948977010 | Task Start | Adishwar Auto Diagnostics Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 108 | 1761/16,516166/0,3031/14 topup. Clear the DTC | Closed | Mr. MD Saleem | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
38 | South | 211749729 | 24/02/2025 | 58.5 | T4.8941.../2422043 | Starting/Stopping Issue | Task Start | Nahla Polyclinic | G-Care Diesels Private Limited - Calicut | 9 | Attend the site and customer complaint about wrong fuel sensing.customer filling 120 ltr diesel in fuel tank but controller showing only 20% fuel in fuel tank.then removed the sensor and clean.refitted by changing its position (because the fuel flot touching in the fuel tank inside plate) now issue solved | Closed | Mr. Sanjaimon S | [9 empty] | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
20 | North | 211716664 | 14/02/2025 | 57 | T4.8941.../2420002 | Leakage Issue | Closed | Hotel Surabhi. | Deep Jyoti Electricals and Services - Shahjahanpur | 2.5 | Found radiator hose clamp loose tightness the same then issue resolve(CC done on 21/08/2024) | Closed | Sudhir Awasthi | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
14 | North | 211717088 | 14/02/2025 | 125.4 | 4H.8041.../2420204 | Starting Issue Call By Customer Name :-Rajkumar . Mobile No :- 9873308474 | Task Start | KESHAV GENERATORS PVT LTD | Paluck Technologies Ltd. - Gurgaon | 348 | Canopy door lock alighnment correct | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
44 | South | 211748772 | 23/02/2025 | 320 | F6.8802.../2420270 | Display Issue Call By Customer Name : Madan Kumar No :7904530162 | Open | Dr. M. Mani Elango M. S. | Ultimate Power Source - Vellore | 778 | Battery voltage is very low check the battery voltage and top up the battery distilled water. Battery charger input line not connected by customer | Closed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
12 | North | 211717118 | 14/02/2025 | 57 | T4.8941.../2420016 | Door Lock Issue Call By Customer Name :-Rajkumar . Mobile No :- 9873308474 | Task Start | KESHAV GENERATORS PVT LTD | Paluck Technologies Ltd. - Gurgaon | 213 | Canopy door lock alighnment correct | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
11 | North | 211717224 | 14/02/2025 | 125.4 | 4H.8041.../2320189 | Def tank temp | Closed | Rohit Industries | Paluck Technologies Ltd. - Ghaziabad | 161 | Def level low, Customer fill the DEF but Alarm not clear so, When Engineer visit the site & clear the DTC | Closed | Kapil Solanki | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
45 | South | 211748139 | 22/02/2025 | 125.4 | 4H.8042.C4../2420295 | Genset Trip | Task Start | Sri Vishnu Ready Mix Concrete | Ultimate Power Source - Nellore |  | Checked in KRM found 6095/0, 516166./0 error code. SE visit pending | Task Start | Mr. NandhaGopal | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
46 | South | 211748083 | 22/02/2025 | 15 | GP3.8501.../2421574 | automatically switched off Call by : Customer Name :Anvi Power Contact :9900035484 | Task Start | Shanthamurthi Shri Shanishwara Swami And Shri Kannikaparameshwari Devasthana Trust | Prasad Power Engineers - Udupi | 9.4 | Dg Tripping due to Emergency Wire Loose Connection the Thigth the wire and Start The dg Check The all Parameters Ok dg Running properly | Closed | Mr. Anil Kumar H G | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
15 | North | 211678023 | 03/02/2025 | 15 | GP3.8501.../2420603 | Red Lamp On Alarm issue Call by customer Name: Pappu Number: 9672595828 | Task Start | Vinayak Technologies | Pratap Diesels Pvt. Ltd. - Sri Ganganagar | 110.4 | Check Event log found-Under speed, Emergency switch activated, Engine Speed Sensor Erratic After that check- MPU found 12V AC, Emergency switch connection found ok, then check Battery condition ok after that check fuel found ok, but some times problem show in the DG | open | Gourav Sharma | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
2 | North | 211718627 | 14/02/2025 | 750 | DV2.8501.C4../2420177 | DG Issue | Task Start | Vodafone | R K Engineers - Meerut |  | Cancelled-SR open by mistake | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | North | 211663211 | 30/01/2025 | 125.4 | 4H.8041.../2420138 | Starting issue and preventive maintanance Called by customer Name : Shruti singh Number : Shruti singh | Cancelled | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur |  | Under Cancellation- Problem solve without visit | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | North | 211685396 | 05/02/2025 | 5.5 | CC1.1013.../2400107 | Starting Issue Email by KGD Name - Sanjeev Jain | Open | ELECTRO EQUIPMENTS | Pratap Diesels Pvt. Ltd. - Bhilwara |  | Cancelled- Problem solve in PM visit | Cancelled | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
62 | South | 211745189 | 22/02/2025 | 5.5 | CC1.1013.../2400391 | Starting/Stopping Issue | Closed | Vishwasamdra Engineering Pvt. Ltd. AP. | Laxmi Diesels - Srikakulam | 124 | dg not started due to battery positive wire damaged so replaced the new one then started the dg running found ok | Closed | Mr. MD Saleem | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
70 | South | 211649195 | 27/01/2025 | 25 | GP3.8702.../2421365 | Starting/Stopping Issue | Task Start | MOHSIN KHAN | Powerlinks Infra Tech Pvt Ltd - Madinaguda | Cancelled | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
78 | South | 211693058 | 07/02/2025 | 45 | 3H.8951.../2420798 | Starting Problem Call by : Customer Name : RAGHU Contact :7013939726 | Closed | Bekem Infra Projects Pvt. Ltd. | Ultimate Power Source - Ananthapuramu | 151 | The problem is battery terminals loose connection to tight the terminals problem solved then starts the engine running condition found ok then check all parameters condition found ok | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
75 | South | 211693662 | 07/02/2025 | 25 | GP3.8702.../2421866 | Starting Issue Call By Customer Name :- Dr Subhash Bohra .. Number:- 9902167435 | Task Start | Aura Care Hospital | Prasad Power Engineers - Shimoga | 23 | visited the site observed the Oil lekage through header assamble removed the header observed oring missing and alterneter cooling fan leaves was broken due to below housing campling bolt was drop | Task Start | Mr. Anil Kumar H G | GOEM issue | [8 empty] | Cooling Fan | 7 | 6 | 4 | 168 | Moderate
11 | North | 211750289 | 24/02/2025 | 25 | GP3.8702.../2420910 | Genset Trip | Closed | Girija Shankar Mehrotra & Sons | Deep Jyoti Electricals and Services - Shahjahanpur | 535 | Found radiator was chocked condition so cleaning the radiator | Closed | Sudhir Awasthi | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
69 | South | 211695357 | 08/02/2025 | 160 | 6H.8475.../2420211 | Leakage Issue | Closed | HOTEL GRAND PALACE | Bharath Diesel Sales and Service - Salem | 283 | Visit the site check the engine fuel tank, fuel suction pump hose side fuel leakage so re tightness the fuel hose clip and arest the fuel leakage done. | Closed | Mr. NandhaGopal | [9 empty] | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
13 | North | 211748938 | 23/02/2025 | 160 | 6H.8475.../2420025 | Tripping issue Call By Customer Name :- Sonu ... Mobile No :- 9058614379 | Closed | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 2565 | 1761/15 Def high level alarm remove the def & clear the DTC then issue resolve | Closed | Kapil Solanki | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
14 | North | 211748696 | 23/02/2025 | 250 | DV8.9840.../2420006 | Starting Issue Call By Customer Name :Yuvraj Mathur No :9811346072 | Cancelled | The Ekta Vihar C/o. Operative Group Housing Society Ltd. | Vidyut Engineers - New Delhi |  | Under Cancellation-Problem solve in tele discussion | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
66 | South | 211695566 | 08/02/2025 | 58.5 | T4.8941.../2422729 | KRM Problem Call by : Customer Name :racheesh Contact :9947514840 | Closed | Phonetech Education. | G-Care Diesels Private Limited - Kannur | 9 | Inspected above the DG set. Checking the KRM unit, Checked voltage and resistance. Connecting the all connections . After start and checked koel app. | Closed | Mr. Sanjaimon S | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
40 | North | 211664421 | 31/01/2025 | 125.4 | 4H.8041.../2420164 | Starting/Stopping Issue | Closed | Peace Unlimited Hospitalities | SAAN Royal Power Solutions Private Limited - Rohtak | 221 | Starting Issue due to Battery Voltage found low ; Battery Charger was disconnected from mains supply so connected the same,Issue resolved after charging | Closed | Ved Prakash Gupta | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
16 | North | 211748959 | 23/02/2025 | 20 | GP3.8601.../2421337 | Power Supply Issue Call By Customer Name :- Ajay Joshi Mobile No :-9915501972 | Cancelled | Ajay Joshi | Dynamic Engineering Services - Jalandhar | 4.93 | Under Cancellation-Work comes out of Scope | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
62 | South | 211696658 | 08/02/2025 | 2.8 | AP1.7003.../2400008 | Starting Issue. Call By Service Dealer Name:-Vishwas.. Mobile No.:-9035054801 | Closed | SK PATIL | Prasad Power Engineers - Hassan | 16 | Visited the site checked the engine found that problem is battery is weak condition then charged the battery and refitted battery terminal is loose connection is tightened check the all parameters ok start the engine running condition is good | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
42 | North | 211661505 | 30/01/2025 | 82.5 | 5H.8901.../2420722 | Cooleant Leakage Issue. Call By Customer Name - Deepak No - 9350958638 | Closed | GOYAL SONS ZAVERI PVT LTD | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 91 | Coolant leakage from Radiator bypass hose due to clamp found loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
69 | South | 211649757 | 27/01/2025 | 58.5 | T4.8941.../2422735 | Fuel Sensor Problem Call by : Customer Name : vasu Contact : 9566021604 | Closed | Prime Fitness Studio Private Limited | Bharath Diesel Sales and Service - Kanchipuram | 8.55 | Visited the site noticed that fuel level sensor problem and Replace new fuel level sensor and dg running found ok all parameter found ok | Closed | Mr. NandhaGopal | [9 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
20 | North | 211748149 | 22/02/2025 | 250 | F6.8842.C4../2420013 | NCD lamp alarm | Cancelled | Arihant Machinery Store | SAAN Royal Power Solutions Private Limited - Sonipat | 224.49 | Under Cancellation-Commercial Pending from Customer end | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
35 | North | 211666771 | 31/01/2025 | 82.5 | 5H.8901.../2320017 | KRM Issue Email By Customer Name:-varun | Closed | Sikka Precision Technologies | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 412.2 | Fuel Level was not showing in KRM app & running hour showing wrong value ; same updated by KRM Team,Issue resolved | Closed | Ved Prakash Gupta | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
54 | South | 211699077 | 10/02/2025 | 25 | GP3.8702.../2421337 | ERROR CODE ISSUE | Closed | Shraeyyes Packers | Bharath Diesel Sales and Service - Chennai | LR | Self Starter pinnion gear not working properly so replace the starter motor. | Closed | Mr. NandhaGopal | [9 empty] | Starter Motor | 7 | 4 | 5 | 140 | Moderate
51 | South | 211699246 | 10/02/2025 | 160 | 6H.8475.../2420155 | ABNORMAL SOUND | Closed | Polydime India Packaging Pvt. Ltd. | Electro Controls - Pollachi | 945 | started the engine found radiator belt loosed condition so stopped the engine then found belt groove is good condition then retighted the belt then started the engine running performance is normal found engine sound is normal | Closed | Mr. NandhaGopal | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
49 | South | 211699357 | 10/02/2025 | 30 | 3H.8902.../2420590 | Starting/Stopping Issue | Closed | Mr. Naveen. | Surya Power Services - Billekahalli | 14 | Retighted all wiring connection ,checked all sensor connection,check oil , coolant level,fuel level, battery connection,start the dg running ok,auto and manual mode working fine. | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
47 | South | 211699504 | 10/02/2025 | 20 | GP3.8601.../2420438 | Starting Issue Call By Customer Name :- Prasana Kumar Mobile No:-9686505525 | Closed | JnanaJyoti Convent. | Prasad Power Engineers - Chithradurga | 60 | Visit the site and start the dg was tripping observed Communication failure alarm then check all wring found 2A 1 fuse problem hence so replace the fuse and start the dg ranning condition ok and check the oil and check the battery voltage and check the coolant and all ok | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
6 | West | 211741839 | 21/02/2025 | 35 | 3H.8902.../2422398 | Starting Issue Email By - KGD Name -Surekha Auti | Cancelled | Bhegade Petroleum | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | cancelled | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
8 | West | 211747952 | 22/02/2025 | 0 | F6.8802.../2420230 | HEADER ASSEMBLY REQUIERD | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi | LR | A new oil cooler header assembly was installed as this engine's header was installed on another engine. | Closed | Amit Sandlya | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
10 | West | 211738229 | 20/02/2025 | 25 | GP3.8702.../2421870 | R phase under voltage | Closed | YASHODHARA UROLOGY MULTI SPECILITY HOSPITAL | KALA Care Global LLP - Latur | 8 | Alarm R phase low volatge , found loose connection of CT on the terminal so tightened the connection properly. | Closed | Jagdeep Saini | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
39 | South | 211703405 | 10/02/2025 | 58.5 | T4.8941.../2421460 | Power Supply Issue & Starting Issue Call By Customer Name :- Kiran Prabhu Mobile No :- 9986167777 | Closed | Mr.Prashanth Narra | Surya Power Services - Bangalore | 8.21 | Engine not started due to loose connection in llop switch wire solved the problem | Closed | Mr. Anil Kumar H G | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
65 | South | 211651425 | 28/01/2025 | 25 | GP3.8702.../2421818 | Abnormal sound &Black smoke problem & Vibration problem Call by : Customer Name : Anjaneyulu Contact : 7993412868 | Task Start | Chaitra builders | Surya Power Services - Bangalore | 11 | Visited the site and customer given complaint abnormal sound and heavy smoke But I was checked the engine thoroughly and heat the sound is normal and smoke within limits. tested with load & without load. But customer not agreed regarding sound so kindly request to koel team support for further investigation. | Closed | Mr. Anil Kumar H G | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
17 | West | 211733483 | 19/02/2025 | 500 | DV8.8501.C4../2420184 | Door lock issue Call by customer Name:Bharat . Number:8275116992 | Open | DHL Supply Chain India Pvt Ltd | Transcreek Engineers Pvt. Ltd. - Bhiwandi |  | cancelled | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
33 | South | 211705909 | 11/02/2025 | 40 | 3H.8951.../2320111 | Batter charger instalation | Completed | BHARTI AIRTEL LIMITED | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 8.42 | Check the battery voltage is low so ENg not starting so arrange the new battery charger instalation and thiting found ok. Check the all parmetars ok. Waiting 5H ok. Started the ENG running coundistion ok. | Completed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
32 | South | 211705915 | 11/02/2025 | 15 | GP3.8501.../2420487 | Voltage Problem & Low Battery problem Call by : Customer Name :Sahad Contact :9486589786 | Closed | Syed Johara Beevi | Bharath Diesel Sales and Service - Karaikal | 67 | Engine not starting problem customer site yesterday to attend the problem battery cells weakness so as per ASM approval for battery replaced the new battery fixed battery serial no 17412127H40406 | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
63 | South | 211651566 | 28/01/2025 | 250 | F6.8841.../2420099 | Leakage Issue | Closed | M/s. Ravi Nursing Home | Sri Manjunath Technical Services - Narasaraopet | 27 | Coolant leakage from hose pipe so retight the radiator hose clamp is ok and dg started is ok and load trail done is ok and dg performance is ok | Closed | Mr. MD Saleem | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
23 | South | 211708559 | 12/02/2025 | 320 | F6.8802.../2420105 | Starting Problem Call by : Customer Name : Dilip Contact : 9603780177 | Closed | BVRIT HYDERABAD College of Engineering for Women | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 52 | Inspection the dg set then checked the lube oil level and radiator coolent ok All fuel pipes ok then checked All fuel pipes ok .but copper washer failure then replace the new one then start the dg set running condition ok no lekeges found | Closed | Mr. NandhaGopal | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
10 | East | 211675381 | 01/02/2025 | 30 | 3H.8902.../2420140 | Starting issue Called by customer Name : Abhishek Number : 9579206584 | Open | Balram Children Hospital. | HACS Engineering and Tech Private Limited - Ranchi | 143 | SR will cancelled- as on telephonic communication issue resolve emergency switch was pressed. | OPEN | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
53 | South | 211699111 | 10/02/2025 | 160 | 6H.8475.../2420191 | Starting/Stopping Issue | Closed | Clayworks Spaces Technologies Private Limited | Surya Power Services - Billekahalli | 20 | Atteand ,Check The Battery Charger Output Cable disconnected Battery voltage Low Dg Not Started,The Site Check The Engine Oil Check The Battery water Check The V Belt Check The Coolent Check The Leakage Check The Electricl Connection | Closed | Mr. Anil Kumar H G | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
22 | North | 211661409 | 30/01/2025 | 750 | DV2.8501.C4../2320048 | Door lock issue Call by customer Name: Chauhan Number: 9720313166 | Closed | Jai Mata DI. Generator Service | Vidyut Engineers - Noida | 52.44 | Canopy door lock adjust | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
82 | South | 211691901 | 07/02/2025 | 5.5 | CC1.1013.../2400294 | Starting/Stopping Issue | Task Start | TRIPTHI SALES CORPORATION | G-Care Diesels Private Limited - Kannur | 5 | Check engine and battery charger,found charger fuse and main dc postive fuse blown condition, check charger and found charger is short circuited, replaced battery charger with new one, connect it and checked , found working normal' | Closed | Mr. Sanjaimon S | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
33 | North | 211677596 | 03/02/2025 | 125.4 | 4H.8041.../2420889 | Electrical Problems | Open | M. S. R. Associates | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Under Cancellation-wrongly Open | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
8 | South | 211713090 | 13/02/2025 | 160 | 6H.8475.../2420196 | RADIATOR FAN DAMAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected the dg noticed the radiator fan leaf one damage, change the new radiator fan replaced from geom stock , after start the dg check the all safety working done | Task Start | Mr. NandhaGopal | Details required | [8 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
5 | South | 211713675 | 13/02/2025 | 58.5 | T4.8941.../2420362 | KRM ISSUE | Task Start | Venkat Sai. | Laxmi Diesels - Visakhapatnam | 16 | KRM NOT WORKING then check wiring is OK and signals ok Antena is outside ok then call to KRM team there activated now is working properly showing parameters ok | Closed | Mr. MD Saleem | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
4 | South | 211713685 | 13/02/2025 | 125.4 | 4H.8041.../2420852 | Starting Issue. Call By Customer. Name:- Jagdish Mobile No.:-9480699678 | Open | K. V. G. Bank. | KALA Care Global LLP - Hubli | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | South | 211715048 | 13/02/2025 | 125.4 | 4H.8042.C4../2420317 | Starting Problem Call by : Customer Name :Sivakrishna Siva Vasireddy Contact :7997290150 | Task Start | KMV Projects Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda | Cancelled | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
67 | South | 211742757 | 21/02/2025 | 58.5 | T4.8941.../2420598 | Automatic not working Properly. | Task Start | ZEOMEGA INFOTECH PVT LTD | Surya Power Services - Billekahalli | 21 | Problem found water pump belt removed from water pump and dianamo and crank pully. Refixed to belt and checked all bolt nut connection tightness checked. | Closed | Mr. Anil Kumar H G | Need to check | [8 empty] | Water Pump | 7 | 6 | 4 | 168 | Moderate
68 | South | 211742622 | 21/02/2025 | 40 | 3H.8951.../2420116 | Starting/Stopping Issue | Closed | Rudraash Diagnostic Labs Pvt. Ltd. | Bharath Diesel Sales and Service - Tiruchirappalli | 45 | Checked found starting problem due to metering valve flt - open alaram created. clear the DTC | Closed | Mr. NandhaGopal | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
69 | South | 211742504 | 21/02/2025 | 40 | 3H.8951.../2421518 | Starting Problem Call by : Customer Name :Ifchekar Contact : 9008999822 | Closed | M/s. Embassy Services Pvt. Ltd. | Surya Power Services - Kalyan Nagar | 5 | satating issue as the battery terminal loose connection | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
11 | East | 211698974 | 10/02/2025 | 45 | 3H.8951.../2520085 | Door Lock Issue And emergency Stop Alarm Issue Call By KGD Name ;Sheetal Gupta no :6299024030 | Task Start | Jai Prakash Kesari. . | HACS Engineering and Tech Private Limited - Hazaribagh | 64 | SR opened by mistake- is under cancellation | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | North | 211665604 | 31/01/2025 | 20 | GP3.8601.../2420107 | Maintenance Due Alarm Call By Customer Name :- M B Shibu Mobile No :-9369653183 | Open | DEEPAK TRAPATHI | SAM Engineering corporation - Varanasi Cantt. |  | Under Cancellation- Problem solve without visit | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | East | 211706081 | 11/02/2025 | 30 | 3H.8902.../2420729 | DG Issue | Open | Axis Bank Ltd | HACS Engineering and Tech Private Limited - Deoghar |  | Cancelled- on telephonic communication issue resolved. | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
1 | North | 211666358 | 31/01/2025 | 45 | 3H.8951.../2421380 | Oil Leakage issue Call By Customer Name :- Ompal Mobile No :-8512050074 | Closed | VICTOR POWER SOLUTION | Pratap Diesels Pvt. Ltd. - JAIPUR | 34.4 | Coolant leakage from radiator hose clamp loose tightness the same | Closed | Gourav Sharma | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
15 | North | 211712621 | 13/02/2025 | 125.4 | 4H.8041.../2420609 | Emergency Stop Alarm Issue Call By Customer Name :- Vivek Mobile No :-9026737976 | Closed | H.S. Construction Pvt Ltd | Deep Jyoti Electricals and Services - Bareilly | 4.24 | Engineer visit on site check & found Controller OFF check battery voltage found 2&3 voltage then check with another battery found No Any issue | Closed | Sudhir Awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
14 | North | 211712780 | 13/02/2025 | 125.4 | 4H.8042.C4../2420462 | Battery issue and Preventive Maintenance Call by Customer Name :-Kachan mishra NO :-8130780192 | Closed | IMPACTQA SERVICES [P] LTD | Vidyut Engineers - Noida | 6.32 | Battery low Charger connection not done (CC done on -(20-january-2025) | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
79 | South | 211740384 | 20/02/2025 | 160 | 6H.8475.../2420208 | AD blue problem Call by : Customer Name : RajuReddy Contact : 9985044305 | Open | Navtej Infrastructure Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Karimnagar |  | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | North | 211747233 | 22/02/2025 | 40 | 3H.8951.../2420463 | INSTANCE ID:-100774140 SITE ID :- 538780 CALL BY CUSTOMER :- DG ISSUE :- DESPLAY ISSUE NAME :-RAJKUMAR . MOB NUMBER :-9821437773 | Task Start | ATC Telecom Infrastructure Private Limited | OVN Industries Private Limited - New Delhi | 1.2 | Control panel wiring burn so, check the connection found Override switch wire wrongly connection then correct the connection After trying to start but Battery discharge recommeded for batttery charging-(CC done on 23/08/2024) | open | Kapil Solanki | Detail mail | [8 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
80 | South | 211740384 | 20/02/2025 | 160 | 6H.8475.../2420208 | AD blue problem Call by : Customer Name : RajuReddy Contact : 9985044305 | Open | Navtej Infrastructure Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Karimnagar |  | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | North | 211713647 | 13/02/2025 | 125.4 | 4H.8041.../2420778 | Tripping Issue Call By Customer Name :- Vikrant Mobile No:-9639100451 | Completed | Shree Ram Industries. | Deep Jyoti Electricals and Services - Moradabad | 821 | Supply module not working so, replace the supply module then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
3 | East | 211750501 | 24/02/2025 | 15 | GP3.8501.../2421456 | Starting/Stopping Issue | Task Start | RAMAN KUMAR TIWARI | Globalline India Services Private Limited - Purnia |  | SR under cancellation- Customer only required service | OPEN | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
6 | East | 211748779 | 23/02/2025 | 320 | F6.8802.../2420154 | ECU Amber Alarm Issue Call By Customer Name :Satendr Singh No :9933195111 | Open | HARI CONSTRUCTION & ASSOCIATES PVT lTD | Globalline India Services Private Limited - Begusarai | 48 | SR cancellation mail snd to hepdesk.- DEF low and Customer require service. | OPEN | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
100 | South | 211699029 | 10/02/2025 | 58.5 | T4.8941.../2421057 | Electrical Problems | Open | Rato Dratsang | Prasad Power Engineers - Sirsi | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
99 | South | 211705324 | 11/02/2025 | 30 | 3H.8902.../2420593 | Starting Problem Call by : Customer Name :karthik Contact :7760919113 | Cancelled | My City Builders and Developers Pvt. Ltd. | Surya Power Services - Mysuru | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
97 | South | 211692829 | 07/02/2025 | 400 | DV8.8542.C4../2420109 | Starting Issue Call By Customer Name :- Shubam Mobile No :-8127655901 | Open | Ravi Infrabuild Projects Pvt. Ltd. | Vijayshree Diesel Sales and Service - Bijapur | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
96 | South | 211687179 | 06/02/2025 | 125.4 | 4H.8041.../2420991 | Lock issue | Open | Ashraya Hospital. | G-Care Diesels Private Limited - Calicut | Cancelled | Cancelled | Cancelled | Mr. Sanjaimon S | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
95 | South | 211689013 | 06/02/2025 | 20 | GP3.8601.../2421277 | Starting Problem & Battery Problem Call by : Customer Name :Raamasubrahmaniyan Contact :8072156825 | Closed | Aarraa Homes | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 3 | checked the battery voltage goes 11 voltage in auto mode, So checked battery charger found eb supply not given, so battery voltage drained. so we given temporary line to battery charge, now battery charging, engine is running condition, informed to the customer, when battery charging 12 Voltage above start the engine to say customer end. | Closed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
93 | South | 211689158 | 06/02/2025 | 58.5 | T4.8941.../2421886 | Starting/Stopping Issue | Closed | Sri santeeswara baba institute of higher studies educational society | Laxmi Diesels - Visakhapatnam | 1 | Visited the site check the engine battery was discharged removed the battery and recharged battery and started the engine running condition are ok satisfied | Closed | Mr. MD Saleem | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
9 | East | 211744425 | 21/02/2025 | 82.5 | 5H.8901.../2420067 | Starting issue Called by customer Name : yusuf Number : 8989161747 | Task Start | Jharkhand Machinery | HACS Engineering and Tech Private Limited - Jamshedpur | 21 | DG not starting due to low battery voltage so given the static charger supply after charging issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
31 | North | 211678045 | 03/02/2025 | 500 | F6.8843.C4../2420001 & 24200001 | Starting Issue Call By Customer Name - Bhagat Singh Number - 9416317467 | Task Start | M. P. Institute of Medical Research | SAAN Royal Power Solutions Private Limited - Karnal | 95 | AVR not giving output & engine tripping with Fuel level sensor alarm ; trace the wire & check the continuity & resistance of fuel guage connector;interchange the guage & found there is no such issue found in guage | Open | Ved Prakash Gupta | [9 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
73 | South | 211647340 | 27/01/2025 | 25 | GP3.8702.../2421013 | Starting issue Call By Customer Name : Vishnu ... No:9986710043 | Closed | Punith Reddy P.S | Surya Power Services - Bangalore | 15.5 | Battery voltage low due to customer not given EB supply | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
4 | East | 211733261 | 19/02/2025 | 30 | 3H.8902.../2420802 | Starting Issue Call By Customer Name :-Pintu Mobile No:-6299403595 | Task Start | Sanjay Kumar.... | Globalline India Services Private Limited - Arrah | 85 | canopy door lock issue, So SE aligned the locking latch | CLOSED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | North | 211747952 | 22/02/2025 | 0 | F6.8802.../2420230 | HEADER ASSEMBLY REQUIERD | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi | LR | A new oil cooler header assembly was installed as this engine's header was installed on another engine. | open | Sudhir Awasthi | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
9 | North | 211713327 | 13/02/2025 | 125.4 | 4H.8041.../2320090 | Starting Issue Call By Customer Name - Rajesh Kumar Number - 7042659373 | Under Monitoring | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi | 3098 | Service done & Radiator cleaning & DEF line Tank to DM Clean with hot water after that (Under load trial) | Under Monitoring | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
2 | North | 211679825 | 03/02/2025 | 15 | GP3.8501.../2421667 | Trip_Genset_Low_Voltage | Open | Open | Rajdhani Diesels and Electricals - Jodhpur |  | Cancelled-double sr open | Cancelled | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
31 | WEST | 211720326 | 15/02/2025 | 40 | 3H.8951.../2421190 | dg set not start in auto | Closed | Technocraft Engineering. . | KALA Care Global LLP - Babhleshwar | 45 | loose connection in AMF panel so tight the wire. | closed | Jagdeep Saini | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
9 | South | 211737007 | 20/02/2025 | 5.5 | CC1.1013.../2400268 | Starting Issue Call By Customer Name :- Vidhyadhar Sahu Mobile No :-8984710946 | Cancelled | BHRAMMAVEER GOLD | KALA Care Global LLP - Belagavi | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
10 | South | 211730560 | 18/02/2025 | 5.5 | CC1.1013.../2400268 | Inspection/Maintenance | Open | BHRAMMAVEER GOLD | KALA Care Global LLP - Belagavi | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | South | 211665161 | 31/01/2025 | 58.5 | T4.8941.../2423007 | Starting/Stopping Issue | Closed | Asian Paints Limited | Laxmi Diesels - Rajahmundry | 24 | visited the site as per following compliant. changed genset condition. found diesel leakage from Banjo bolt so replaced with new copper watcher removed air lock. started the genset running condition is ok. | Closed | Mr. MD Saleem | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
8 | South | 211730921 | 18/02/2025 | 20 | GP3.8601.../2420832 | Alarm issue | Closed | M/s. Amrutha Bakery. | Surya Power Services - Kalyan Nagar | 92.5 | As per the customer complaint check the engine properly. Problem found in emergency Stop connection 1 is damaged. Battery positive cable terminal lux So remove the Lux and replaced it.check the all parameters of engine found ok | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
7 | WEST | 211734639 | 19/02/2025 | 58.5 | T4.8941.../2421410 | Air Look Issue Call By Customer Name :- Mobile No :- | Open | P. N. Gadgil Jewellers Limited. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | cancelled | Closed | [10 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | South | 211731332 | 18/02/2025 | 58.5 | T4.8941.../2422795 | Oil leakage issue Called by customer Name : Ramisetty mery Kavitha Number : 9663727272 | Open | Ramisetty mery Kavitha | Surya Power Services - Bangalore | 3 | Carried out visit the site observed on oil leakage in drain plug, thighten the drain plung found ok check the oil level coolent level v belt hose fuel pipe ems battery air cleaner found ok observed on dg running condition foundbok | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
4 | South | 211731369 | 18/02/2025 | 15 | GP3.8501.../2420843 | Trip_Genset_Low_Voltage | Task Start | Abode Real Estate Developers P. Ltd. | Madhu Engineering Sales & Service - TIRUVALLUR | 203 | Visited the site inspected the engine, check the problem engine tripe, so check the even log and check the load condition, engine over load and single phase over load ,so advice the customer to be explained the problem, check the engine oil level, check the radiator coolant level, check the v belt tension check the battery distilled water, starting the engine test found ok | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
12 | West | 211728784 | 18/02/2025 | 40 | 3H.8951.../2420902 | DG set isnâ€™t Starting in auto - | Cancelled | ICICI Bank Limited | Transcreek Engineers Pvt. Ltd. - Vasai |  | cancelled | Closed | Jagdeep saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
10 | WEST | 211737200 | 20/02/2025 | 58.5 | T4.8941.../2422857 | Air locking issue | Task Start | ARCHANA JAISWAL | Unique Techno Services Pvt Ltd. - Ahmedabad | 8 | DG only start after hand priming of the fuel. Took the bucket trail DG was not started. No any leakage found in fuel system. After one time start opened the fuel filter and found about half fuel in fuel filter. So today engineer will visit at the site with all copper washer and one NRV(For fitted in suction line). | Closed | [10 empty] | NRV | 6 | 5 | 4 | 120 | Moderate
8 | South | 211664237 | 31/01/2025 | 30 | 3H.8902.../2420111 | Starting/Stopping Issue | Closed | Dr. Danish George. | G-Care Diesels Private Limited - Ernakulam | 18 | Attended the site, checked engine parameters found normal. Under speed alarm in controller and DM2 fault code also observed (637/2). Fault code cleared with ikonnect, then started DG and running found normal. checked cam sensor, found ok. No loose connection observed on sensor connector and ECU connector. No error code observed during load test. Battery voltage and water level found ok. Controller connections checked ok | Closed | Mr. Sanjaimon S | [9 empty] | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
12 | WEST | 211735888 | 19/02/2025 | 625 | DV0.8501.C4../2420129 | Starting and Battery Charging issue Call By Customer Name :-Rahul Mobile No :-9770917387 | Closed | MALPANI PARKS INDORE PRIVATE LIMITED | Natraj Power Tech - Indore | 23 | Engine not starting due to low battery voltage. So checked and found battery charger mains supply wire loose so tightened the same. | Closed | [10 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
9 | South | 211678673 | 03/02/2025 | 58.5 | T4.8941.../2422043 | Starting/Stopping Issue | Task Start | Nahla Polyclinic | G-Care Diesels Private Limited - Calicut | 8 | Attend the site and check the general condition and find out the complaint is coolant leakage from radiator hose clip and hose. Then retight the all radiator hose clips, top-up the radiator coolant and start the engine working found | Closed | Mr. Sanjaimon S | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
1 | West | 211709169 | 12/02/2025 | 5.5 | CC1.1013.../2400113 | Battery Charge Issue Call By Customer Name :- Balram Mobile No :-9508252219 | Closed | Rajlaxmi Dev Build India Pvt. Ltd. | Natraj Power Tech - Bhopal | 566.11 | Engineer visited the site and checked and found DG starting issue due to low battery voltage. So need to be replace the charger. | OPEN | Vijay Patil | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
7 | East | 211727384 | 17/02/2025 | 200 | 6H.8435.../2420108 | Sound/Vibration Issue | Closed | M/s. Innovative Construction | Gangpur Sales and Services - Cuttack | 52 | SE found abnormal sound due to belt loose. Then tight the belt after that Start the engine sound was normal | CLOSED | Ujjwal Das | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
4 | East | 211726235 | 17/02/2025 | 15 | GP3.8501.../2421464 | Lub Oil Throw | Open | M.S Interprices | Globalline India Services Private Limited - Biharsharif | 179 | Line rejection(commisisiong not done yet)- AS per complaint SE visited site and at silencer found lube oil, so removed turbo and found no lube oil at exhaust manifold and so it's indicate that the lube oil at silencer is due to the turbo exhaust side o ring damage and as per KRM data customer's load is 2-3 amp and it's an single phase DG, so turbo will be send for reparing. | OPEN | Prabhakar Kumar | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
19 | WEST | 211710266 |  | 750 | DV2.8501.C4../2420147 | STARTING ISSUE | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | CAN parameter not showing so replaced the DCU 1. | Closed | [10 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
3 | North | 211742686 | 21/02/2025 | 82.5 | 5H.8901.../2420379 | Starting Issue Call By Customer Name :- BRIJ VERMA Mobile No :- 9559819888 | Open | Jr. Steel Rooftech Infrastructure | S. R Engines Sales And Service - LUCKNOW | 613 | Check & found Oil not available in Sump then check the radiator found oil in radiator then check oil cooler found punchure then check gasket found ok: Now, call for the OIL cooler replaced | open | Sudhir Awasthi | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
16 | South | 211677915 | 03/02/2025 | 15 | GP3.8501.../2421340 | Starting/Stopping Issue | Task Start | H M B S Textiles Private Limited | G-Care Diesels Private Limited - Malappuram | 64 | LLOP Switch wire loose Connection tighten the wire and started the DG found runnging ok. | Closed | Mr. Sanjaimon S | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
9 | NORTH | 211729101 | 18/02/2025 | 58.5 | T4.8941.../2422167 | TRANSIT DAMAGE | Cancelled | Axis Bank Ltd | Paluck Technologies Ltd. - Ghaziabad |  | Under Cancellation | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
11 | NORTH | 211728725 | 18/02/2025 | 125.4 | 4H.8041.../2421031 | Starting Issue Call By Customer Name :- Pankaj Sir Mobile No :-8527068558 | Task Start | NAMITA SABHARWAL | Vidyut Engineers - Noida | 62 | Battery voltage low, battery charger supply wire was break so, connect the wire then charge the battery then issue resolve | Closed | Kapil Solanki | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
16 | North | 211747845 | 22/02/2025 | 125.4 | 4H.8041.../2320086 | Oil leakage issue and abnormal sound issue Called by customer Name ; ShivJi Number ; 8800312571 | Task Start | Total Construction | Paluck Technologies Ltd. - Gurgaon | 2683 | Found battery terminal Coonection loose so, tightness the same & Educate the customer | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
15 | NORTH | 211728601 | 18/02/2025 | 500 | DV8.8501.C4../2420020 | Starting Issue Call By Customer Name :- Ajay Mobile No :-9958214785 | Task Start | ESQUIRE TECH.. | Vidyut Engineers - New Delhi | 76 | Found battery voltage low, Battery charger connection removed from customer end, Engineer educate customer to many times | Closed | Kapil Solanki | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
17 | NORTH | 211727876 | 17/02/2025 | 40 | 3H.8951.../2420281 | troubleshooting activites Eamil By Customer Name :-Prashant | Task Start | Vedanta Jyoti Eye Hospital | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | KRM issue Engineer visit today | open | Sudhir Awasthi | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
19 | NORTH | 211727453 | 17/02/2025 | 57 | T4.8941.../2320075 | Door lock issue | Closed | Khandelwal Namkeen & Snacks Pvt.Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 155 | found 1 no door not close of pannel side and canopy lamp not working. | Closed | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | WEST | 211731104 | 18/02/2025 | 25 | GP3.8702.../2420527 | Fuel Leakage from DG,Please Visit -512224 | Cancelled | ICICI Bank Limited | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | cancelled | Closed | [10 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
23 | NORTH | 211726027 | 17/02/2025 | 320 | F6.8802.../2420046 | Tripping issue Called by customer Name VIVEK Number ; 8920770585 | Task Start | COUNTYESTATE DEVELOPERS LLP | Paluck Technologies Ltd. - Gurgaon |  | Under Cancellation | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
9 | North | 211741731 | 21/02/2025 | 57 | T4.8941.../2320227 | Auto Panel Issue Call By Customer Name- Mithilesh Number-9910563347 | Task Start | Komal Co Operative Group Housing Society | Paluck Technologies Ltd. - Faridabad |  | Cancelled-Mains voltage issue | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
19 | South | 211677750 | 03/02/2025 | 25 | GP3.8702.../2420902 | Display Problem Call by : Customer Name :Mahendran Contact :9345882754 | Task Start | Kovai Akshaya Social Club | Electro Controls - Coimbatore | 17 | DG battery voltage very low voltage so engine battery removed and spare battery fitting start the engine working found ok | Closed | Mr. Sanjaimon S | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
32 | North | 211728697 | 18/02/2025 | 30 | 3H.8902.../2320025 | Abnormal Sound Issue Call By Customer Name :- Bhupendra Singh Mobile No :-9354306513 | Closed | Gabsons Engineers & Consultants | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 194.06 | Abnormal sound found due to bolt found loose of Silencer support with canopy,Tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | East | 211664220 | 31/01/2025 | 25 | GP3.8702.../2420144 | Battery Issue Call By Customer Name :-Ananya .. Mobile No :- 7903846934 | Closed | Basant Bahar Sweets | Globalline India Services Private Limited - Biharsharif | 273 | DG was not cranking properly so checked battery voltage found 12.3V and its cranking voltage was 10.2V so tighten the battery terminal clamp and all panel and controller connection then cranked DG started normally. | CLOSED | Prabhakar Kumar | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
36 | North | 211723433 | 17/02/2025 | 82.5 | 5H.8901.../2320017 | KRM Issue Email by Customer Name - Varun sikka | Closed | Sikka Precision Technologies | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 413 | KRM was not working so connected to KRM team ;re-Slotted the Sim card & run the DG on Load ; all parameter showing correctly | Closed | Ved Prakash Gupta | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
37 | North | 211722690 | 16/02/2025 | 58.5 | T4.8941.../2420917 | Alarm Issue Call By Customer Name - Prashant . Number - 8239294506 | Open | Durga Food | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Under Cancellation-Appointment Issue | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
24 | NORTH | 211726017 | 17/02/2025 |  | 3H.8902.../2520063 | STARTING ISSUE | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Found Water pump not working, Engine tempreture high so replace the same DG run ok | Closed | Gourav Sharma | [9 empty] | Water Pump | 7 | 6 | 4 | 168 | Moderate
13 | South | 211730310 | 18/02/2025 | 10 | GP3.8301.../2420365 | Shutdown alarm issue Call By Customer Name :ADESH . No :8610233236 | Task Start | Budans 7 Cafe. | Madhu Engineering Sales & Service - Teynampet,Chennai | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | WEST | 211737246 | 20/02/2025 | 25 | GP3.8702.../2420527 | fule leakage from dg 512224 | Task Start | ICICI Bank Limited | Dhanashree Technocrats Pvt. Ltd. - Nasik | 43 | oil leakage from oil filter header body so need to replace oil filter header | Closed | [10 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
16 | South | 211733958 | 19/02/2025 | 25 | GP3.8702.../2420252 | Electrical Problems | Task Start | Progen Power Engineers | Surya Power Services - Peenya, Bangalore | 2 | Electrical problems due to main phase rivers from E B side. So solved the problem by changing it. Checked the engine oil and coolant. Checked the battery and distilled water. Finally other general checkup was done. Started the D G set and found ok | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
18 | North | 211732944 | 19/02/2025 | 58.5 | T4.8941.../2422654 | Starting Issue Call By Customer Name - Number - 9511507498 | Task Start | Monu Tripathi | Pratap Diesels Pvt. Ltd. - Bhilwara | 91 | Found battery voltage low, alarm but check in multermeter found ok then check wiring connection found 2A wire was loose so, tightness the same then start the DG | Closed | Gourav Sharma | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
19 | North | 211732931 | 19/02/2025 | 125.4 | 4H.8042.C4../2420669 | Maintenance Due alarm issue Call By Customer Name :- Shrikant Kumar Mobile No :-8210295791 | Open | ARIHANT CONTRACTORS PRIVATE LIMITED | S.S. Enterprises - Allahabad |  | Under Cancellation | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
23 | North | 211731109 | 18/02/2025 | 58.5 | T4.8941.../2422467 | Canopy Door Problem Call by : Customer Name :Anuraj Contact :9787109408 | Closed | nabadurga pesticides pvt ltd | Paluck Technologies Ltd. - Faridabad | 4 | Canopy door lock adjust, if problem again repeat then replace the lock | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
24 | North | 211731094 | 18/02/2025 | 58.5 | T4.8941.../2420570 | STARTING ISSUE | Closed | NIRMAN E-STORE LLP | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 3451 | Found radiator was chocked condition so, educate the customer for radiator cleaning | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
29 | North | 211730229 | 18/02/2025 | 125.4 | 4H.8041.../2420222 | Starting Issue Call By Customer Name :- Avinash . Mobile No :-9540023080 | Closed | SHIVALIK ENGG.WORKS | Paluck Technologies Ltd. - Faridabad | 426 | Found Battery voltage low, connect the charger | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
30 | North | 211730161 | 18/02/2025 | 125.4 | 4H.8041.../2420024 | Starting Issue Call By Customer Name :- Sumit Kumar Mobile No :- 7742911970 | Closed | Ophthalmic Technology | Pratap Diesels Pvt. Ltd. - Bhiwadi | 83 | Battery voltage low, Charger connection done from customer end | Closed | Gourav Sharma | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
13 | WEST | 211660616 | 30/01/2025 | 30 | 3H.8902.../2421203 | Starting/Stopping Issue | Open | VENTURE STEELS PVT LTD | Unique Techno Services Pvt Ltd. - Surendranagar | 1.26 | Engine starting issue. Battery voltage 10.8V and battery charger was disconnect from customer side. | closed | Amit sandlya | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
40 | North | 211716867 | 14/02/2025 | 125.4 | 4H.8041.../2420774 | Sound/Vibration Issue | Closed | I. B. School | SAAN Royal Power Solutions Private Limited - Rohtak | 72 | Check the DG throughout but no any such issue found as abnormal sound,so same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
44 | North | 211714806 | 13/02/2025 | 58.5 | T4.8941.../2422284 | Door look Issue Call By Customer Name :- Mr. babloo Mr. babloo Mobile No :- 9896907109 | Closed | SIDHARTHA OVERSEAS | SAAN Royal Power Solutions Private Limited - Panipat | 25.26 | Canopy door lock catcher found faulty so adjusted same with help ofhinge & issue resolved | Closed | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
12 | East | 211734604 | 19/02/2025 | 15 | GP3.8501.../2421616 | Starting/Stopping Issue | Task Start | Shyam Sundar Chakraborty | Revenus Industries Pvt. Ltd. - Bankura | 6.5 | SE found emergency switch alarm so tighten all connection related the emergency switch but not resolved so he provided direct negative connection from battery,Issue resolved. | CLOSED | Prosanjit saha | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
6 | WEST | 211664219 | 31/01/2025 | 500 | DV0.9030.../2300001 | engine not workimg | Task Start | Cedar Decor Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Vadagam | 75 | Low DEF level Engine was not cranking so checked the interfacebox and found that the 25Amp fuse of starter motor power supply line was burn so replaced it with 30Amp fuse. Goel Power Engineers, |  | Amit sandlya | [9 empty] | Starter Motor | 7 | 4 | 5 | 140 | Moderate
8 | East | 211732119 | 18/02/2025 | 58.5 | T4.8941.../2420535 | Starting issue Call By Customer Name :- Rajkumar Jha Mobile No :-9988368785 | Task Start | Adi Sports India Pvt. Ltd. | Globalline India Services Private Limited - Patna | 36 | DG not starting due to battery discharge so SE check static charger connetion, where provided but the battery charger was not getting on so on further checking found battery charger mains supply connector jack was defective so replaced the jack issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
7 | East | 211732668 | 19/02/2025 | 250 | F6.8841.../2420383 | Canopy door issue Call By Customer Name Umesh No : 9431049058 | Task Start | Mithila Earthing Solutions | Globalline India Services Private Limited - Patna | 8.6 | canopy door lock issue, So SE aligned the locking latch, Customer is not satisfied by these solutions | CLOSED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
6 | East | 211732937 | 19/02/2025 | 25 | GP3.8702.../2421906 | Diesel Leakage Issue Call By Customer Name :- Ashish Mishra Mobile No :- 9770074460 | Task Start | SHREE KHATU INFRAPROJECTS | HACS Engineering and Tech Private Limited - Deoghar | 90 | SE visited and checked Diesel leakage found diesel at the canopy base but that was not due to leakage. It was because filling mistake it drop on the base and the DG is on trolley so it is not stationay it moves so due to the vibration diesel over flow from the diesel tank. | CLOSED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
42 | North | 211715038 | 13/02/2025 | 15 | GP3.8501.../2421245 | Starting Issue Call By Customer Name :- Pravin Mobile No:-9660540744 | Cancelled | BHARAT GENERAL STORE | Suraj Motor Store - Jammu |  | Under Cancellation-no response from customer | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | NORTH | 211729374 | 18/02/2025 | 15 | GP3.8501.../2320030 | Starting and KRM issues | Task Start | Jain Children Hospital | Pratap Diesels Pvt. Ltd. - Bhiwadi | 39 | KRM not working Check & found Network not found Set up the the KRM | Closed | Gourav Sharma | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
11 | North | 211738197 | 20/02/2025 | 625 | DV0.8501.C4../2420158 | Trip_Genset_Low_Voltage | Open | Radikale Engineering Pvt. Ltd.. | Paluck Technologies Ltd. - Faridabad |  | Under Cancellation | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
8 | North | 211733757 | 19/02/2025 | 125.4 | 4H.8041.../2420124 | Starting/Stopping Issue | Cancelled | Venus CGHS. Ltd. | OVN Industries Private Limited - New Delhi |  | Under Cancellation | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
17 | South | 211733374 | 19/02/2025 | 15 | GP3.8501.../2421044 | Oil Leakage Problem Call by : Customer Name :Umesh Contact :9686566017 | Task Start | Samyak Tiles & Granites | Prasad Power Engineers - Haveri | 33 | Checked found oil leakage from gear cover gasket side oil leakage due to gear cover bold tighte not proper tight. so re tight the gear casing cover tight then oil leakage is arrested.Then thermoset bye pass hose t bolt side coolant water leakage so tight and correct the issue is solved. Then checked Coolant water level is lower so top up coolant.oil level checked ok, then 1 hrs trail done engine oil leakage check ok, DEF level leakage checked ok, diesel leakage checked ok | Closed | Mr. Anil Kumar H G | Qa communication | [8 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
18 | South | 211733294 | 19/02/2025 | 25 | GP3.8702.../2420859 | Starting Problem Call by : Customer Name : Anji Contact : 9043850803 | Task Start | BHARANI NURSING HOME | Ultimate Power Source - Kadappa | 14 | Found that battery issue due to fuse was burnt . So replaced the old fuse with new one . Now DG running condition found ok | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
3 | WEST | 211738584 | 20/02/2025 | 400 | DV8.8542.C4../2420047 | Genset Trip | Open | Sahyadri Hospitals Ltd. | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | given for cancellation | Closed | [10 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
20 | South | 211732785 | 19/02/2025 | 5.5 | CC1.1013.../2400502 | Starting Problem Call by : Customer Name :Prathap Reddy Contact : 6301459473 | Closed | Ameva Enterprises | Laxmi Diesels - Vizianagaram | 21 | As per the complaint, I attended the site and checked the engine. I found the battery was discharged, so I removed it and sent it to the battery servicing center for charging. After charging, I reinstalled the battery, started the DG, and the engine condition was good | Closed | Mr. MD Saleem | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
8 | West | 211723867 | 17/02/2025 | 400 | DV8.8542.C4../2420145 | Genset Trip | Closed | Y.N Dhanani | Unique Techno Services Pvt Ltd. - Surat | 228 | This DG is at RMC site. Engineer went to site for genset tripping problem. He found that radiator and CAC was choked externally, so he was educated to customer. | Closed | Amit sandlya | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
28 | North | 211735614 | 19/02/2025 | 7.5 | D3.8305.../2400147 | Oil leakage issue Call By Customer Name :- Ambuj.. Mobile No :- 9103646957 | Task Start | Phooltas Transrail Limited | Suraj Motor Store - Jammu |  | Air Locking issue in KCC ; same rectified on telephonic Discussion | Cancelled | Ved Prakash Gupta | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
14 | North | 211733085 | 19/02/2025 | 40 | 3H.8951.../2420246 | Starting/Stopping Issue | Open | PUNJABI DHABA | Rajdhani Diesels and Electricals - Jodhpur | 4 | Battery voltage low, Charger connection done | Closed | Gourav Sharma | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
27 | North | 211735656 | 19/02/2025 | 40 | 3H.8951.../2420947 | Inspection/Maintenance | Cancelled | General Electric & Machinery Corporation | Industrial Power Solutions - LUDHIANA | 69.93 | Under Cancellation-Service Due | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
15 | West | 211731907 | 18/02/2025 | 35 | 3H.8902.../2421823 | Starting Issue Email By KGD Name:-Ranajn Kowale | Task Start | SRI SAI AGRIGATE PROCESSORS | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 17 | radiator coolant drain plug coolant leakage because Radiator drain cok open | Closed | Jagdeep Saini | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
17 | West | 211673604 | 01/02/2025 | 10 | GP3.8301.../2320008 | ENGINE CHECK | Task Start | Sai Construction Company | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC |  | cancelled | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
23 | North | 211737717 | 20/02/2025 | 20 | GP3.8601.../2420942 | Starting issue and preventive maintenance Call By Customer Name :- Sunil Kumar Mobile No:-7009342528 | Cancelled | PRINCIPAL, DIET BARKANDI | Industrial Power Solutions - LUDHIANA | 5.88 | Under Cancellation-Service Due | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
22 | North | 211737794 | 20/02/2025 | 40 | 3H.8951.../2420948 | Automation Issue Call By Customer Name :- Manish Sir Mobile No :- 9814091000 | Cancelled | Jalan Colors | Industrial Power Solutions - LUDHIANA | 50.65 | Under Cancellation-Service Due | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
21 | North | 211738006 | 20/02/2025 | 20 | GP3.8601.../2420034 | Inspection/Maintenance | Open | Mata Mohandai Oswal Public Senior Secondary School | Industrial Power Solutions - LUDHIANA | 137.31 | Under Cancellation-Service Due | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | North | 211733739 | 19/02/2025 | 750 | DV2.8501.C4../2420173 | INSTANCE ID:-100789729 SITE ID:- INUW080079 CALL BY CUSTOMER// DG ISSUE:- DG DOOR ISSUE NAME:- KARAN NUMBER:- 7906702750 | Task Start | Vodafone | R K Engineers - Meerut | 121 | Canopy door lock defective so, replace the same | Closed | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
26 | North | 211737202 | 20/02/2025 | 40 | 3H.8951.../2420538 | Starting/Stopping Issue | Open | Axis Bank Ltd | SAAN Royal Power Solutions Private Limited - Zirakpur | 14.95 | Under Cancellation-Customer not followed warranty Policy | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
1 | North | 211679894 | 03/02/2025 | 320 | F6.8802.../2320024 | Emergency stop alarm issue Call By Customer Name :-Mahesh Chand Mobile No :- 9354228807 | Open | KLK. Venture Pvt. Ltd. | Vidyut Engineers - Noida |  | Cancelled-Problem solve in tele. discussion | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
21 | North | 211745178 | 22/02/2025 | 15 | GP3.8501.../2420049 | Electrical Problems | Closed | Ashok Galoth. | Paluck Technologies Ltd. - Ghaziabad | 74 | Check & found battery charger not charge the battery because during checking the voltage found 415v supply from customer end, then correct the connection after that issue resolve | Closed | Kapil Solanki | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
24 | North | 211745062 | 22/02/2025 | 15 | GP3.8501.../2420685 | Oil Seal Leakage Issue Call By Customer Name:-Mohit Singh No:-9950101111 | Cancelled | Bhagwati Indian Oil | Pratap Diesels Pvt. Ltd. - Sikar |  | Under Cancellation-postponed visit | Cancelled | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
6 | South | 211724892 | 17/02/2025 | 25 | GP3.8702.../2520201 | Oil Presure Alarm | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | East | 211741746 | 21/02/2025 | 20 | GP3.8601.../2421201 | Amber Lamp ON Alarm Issue Call By Customer Name :- Dheeraj Kumar Mobile No :- 9122320667 | Closed | Raava Keshri C/O Rishi Kumar | HACS Engineering and Tech Private Limited - Ranchi | 23.8 | Battery not charging issue due to charging alterator fuse(50A) found defectived so replaced and issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
3 | South | 211725319 | 17/02/2025 | 20 | GP3.8601.../2420470 | Starting/Stopping Issue | Task Start | M. Chinna Swamy | Surya Power Services - Bangalore | 32 | Found canopy emergency switch connector issue so corrected and resolved the issue. | Closed | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
1 | South | 211725885 | 17/02/2025 | 320 | F6.8802.../2420087 | Oil Leakage Problem Call by : Customer Name : Rosayya Contact : 9701496632 | Open | MAANGALYA SHOPPING MALL PRIVATE LIMITED | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 40 | Oil leakage from oil cooler side | Task Start | Mr. MD Saleem | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
9 | East | 211738357 | 20/02/2025 | 25 | GP3.8702.../2420833 | Starting Issue Call By Customer Name :- NITIN JI NITIN JI Mobile No :- 7903102566 | Task Start | Nidhivan Restaurant | HACS Engineering and Tech Private Limited - Dhanbad | 273.5 | DG shutdown showing under voltage Alarm due to the loose connection of voltage sensing wiring at MCB after tightening issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
16 | NORTH | 211722617 | 16/02/2025 | 58.5 | T4.8941.../2421839 | Starting Issue Call By Customer Name :- Rajendra Kumar Mobile No :8954665692 | Closed | ADESH GUPTA ENTERPRISES | Deep Jyoti Electricals and Services - Bareilly | 24 | R phase fuse was faulty replace the same then chaging the battery then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
13 | NORTH | 211722702 | 16/02/2025 | 57 | T4.8941.../2420160 | Tripping Issue Call By Customer Name :- Hariram Mobile No :-8368858087 | Task Start | Avtar Electric & Generator Works | Vidyut Engineers - Noida | 275 | DG set found error code show on EMS 633/3 check fuel filter, fuel filter chowk so fuel filter change and check fuel tank, fuel tank dirty advised to the customer for fuel tank clean | open | Kapil Solanki | [9 empty] | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
12 | NORTH | 211722754 | 16/02/2025 | 125.4 | 4H.8042.C4../2420472 | Automation & Battery Under Voltage Issue Call By Customer Name :- Narendar Singh No :- 7669931331 | Task Start | M P Singh | Vidyut Engineers - Noida | 4.8 | found the dg set starting issue problem dg set battery Crank voltage 5 volt engine not start and dg set battery charger proper charging working ok but dg set battery problem dg set battery new replace | Closed | Kapil Solanki | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
6 | NORTH | 211723940 | 17/02/2025 | 82.5 | 5H.8901.../2420422 | Low coolant issue call by customer Name:MAHESH MAURYA Number: 9452111389 | Task Start | SHAKTI PACKERS INDIA PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | 8.3 | Coolant leakage from radiator hose clamp loose tightness the same | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
18 | East | 211746621 | 22/02/2025 | 250 | F6.8841.../2420311 | Electrical Problems | Closed | Bharat Singhal | Revenus Industries Pvt. Ltd. - Howrah | 14 | Customer Pressed the emergency switch after that released the switch and there was a loose connection somewhere all the connections are tightening the same,Issue resolved | CLOSED | Prosanjit saha | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
24 | North | 211668190 | 31/01/2025 | 320 | F6.8802.../2420073 | Door Lock Issue Coolant Leakage Issue & Coolant Lid Issue Call By Customer Name :- Rishi Pal Mobile No :- 7838955880 | Open | A.G. Pipes Pvt. LTD. | Paluck Technologies Ltd. - Faridabad |  | Cancelled | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
21 | East | 211746621 | 22/02/2025 | 250 | F6.8841.../2420311 | Electrical Problems | Closed | Bharat Singhal | Revenus Industries Pvt. Ltd. - Howrah | 14 | Customer Pressed the emergency switch after that released the switch and there was a loose connection somewhere all the connections are tightening the same,Issue resolved | CLOSED | Prosanjit saha | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
37 | WEST | 211720054 | 15/02/2025 | 200 | 6H.8438.C4../2420025 | KRM activation | Open | Faith Automation System & Tooling Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | cancelled | closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
36 | WEST | 211721402 | 15/02/2025 | 58.5 | T4.8941.../2423069 | Power Supply Issue. Call By Customer. Name:-Pradeep shetty Mobile No.-8830094704 | Open | Plumeria Luxury Banquet | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | cancelled | closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
32 | WEST | 211701644 | 10/02/2025 | 125.4 | 4H.8042.C4../2420030 | FUEL SENSOR FAULTY Email by KGD Name - Surekha Auti | Closed | Divya Associates | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 53 | Fuel level sensor did not shows the proper value so replace the sensor. | closed | Jagdeep Saini | [9 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
62 | South | 211651589 | 28/01/2025 | 58.5 | T4.8941.../2421934 | Leakage Issue | Closed | PRADEEPRAJ INFRA PRIVATE LIMITED | Sri Manjunath Technical Services - Ongole | 5.55 | Coolant leakage from the radiator hose so retight the hose and arrest the leakage of coolent is ok and dg started is ok and load trail done is ok | Closed | Mr. MD Saleem | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
29 | WEST | 211719878 | 15/02/2025 | 30 | 3H.8902.../2320122 | Automation Issue Call By Customer Name :- Lavelesh Parashar Mobile No :- 9860317912 | Open | Orbit Techsol W. Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune |  | cancelled | closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | WEST | 211713803 | 13/02/2025 | 5.5 | CC1.1013.../2400117 | Battery Charging issue Call by Service Dealer Name :-Prasad NO :-750723336 | Completed | Mr. Navneet Kumar.. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 32 | Rectifier in battery charger found faulty so battery was not charged, change the rectifier issue solved. | closed | Jagdeep Saini | Photo required | [8 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
51 | South | 211672872 | 01/02/2025 | 160 | 6H.8475.../2420111 | Sound/Vibration Issue | Task Start | KVR AUTOMALL PRIVATE LIMITED | G-Care Diesels Private Limited - Kannur | 850 | Abnormal sound, fan belt loose condition, then tight the fan belt, Engine working found ok | Task Start | Mr. Sanjaimon S | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
9 | WEST | 211685506 |  | 750 | DV2.8501.C4../2420057 | Engine hunting problem | Completed | Nyati Hotels & Resorts Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 30 | Engine hunting due to potential meter was connected with battery, so remove the connection from battery and done the GAIN setting ON SYNCHRONISE CONTROLLER, now there is no fluctuation in bias voltage so engine is running satisfactory in sync. | closed | Jagdeep Saini | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
6 | South | 211735075 | 19/02/2025 | 200 | 6H.8435.../2420059 | Tripping issue Call By Customer Name :- Anil ... Mobile No :-9164459147 | Task Start | Amrutha Constrcution Pvt. Ltd. | Vijayshree Diesel Sales and Service - Hospet | 42 | 520528/31 error code . Clear the DTC | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
12 | WEST | 211719513 | 15/02/2025 | 200 | 6H.8435.../2420035 | Tripping Issue & Coolant Issue Call By Customer Name - Virendra Kumar Number - 9725270303 | Closed | Ashish Brass Components Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Jamnagar | 54.11 | The coolant level in the reservoir tank was above the maximum level, causing coolant to overflow from the tank, thereby maintained the level of coolant in the tank. DEF was leaking from the supply module to the dosing module pipe, so it was replaced. | closed | Amit Shandilya | [9 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
14 | WEST | 211718553 | 14/02/2025 | 625 | DV0.8501.C4../2420095 | Heavy blow by observed, and frequency drop at 100 % load | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi | LR | An abnormal sound was noted in the engine, accompanied by heavy blow-by. The tappet cover was removed, and the valve bridge position was checked and found to be Ok. The oil filter was then opened, and oil was extracted. Upon inspection, metal particles were found in the oil. | closed | Amit Shandilya | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
7 | South | 211724793 | 17/02/2025 | 30 | 3H.8902.../2420295 | Low Battery Problem Call by : Customer Name :Vignesh Contact :9566334962 | Task Start | N. Vignesh. | Bharath Diesel Sales and Service - Thiruvannamalai | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
16 | WEST | 211716919 | 14/02/2025 | 40 | 3H.8951.../2420311 | Starting Issue Call By Customer Name - VINU Number - 9824448355 | Closed | Nutan Public School | Unique Techno Services Pvt Ltd. - Surat | 85 | Engine starting issue due to loose battery +Ve connection. | closed | Amit Shandilya | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
20 | WEST | 211709807 | 12/02/2025 | 500 | DV0.8552.C4../2420004 | ECU malfunctioning | Closed | Oetiker India Pvt Ltd | Transcreek Engineers Pvt. Ltd. - Panvel | 68 | 523518/ 7, 522120/7, 523524/7, 522122 /7 check all the connection found ok , connect ikonnect and clear DTC . | closed | Jagdeep Saini | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
19 | North | 211674413 | 01/02/2025 | 10 | GP3.8301.../2420407 | Starting Issue Email By - KGD Name - Vnu Mehta | Open | Ultratech Cement Ltd | BSES (I) Pvt. Ltd. - Dungarpur |  | Cancelled-SR open by mistake | Cancelled | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
22 | WEST | 211698900 | 10/02/2025 | 500 | DV8.8501.C4../2420419 | Starting/Stopping Issue | Closed | MEYER ORGANICS PVT. LTD. | Transcreek Engineers Pvt. Ltd. - Thane | 17 | error code 523582/ 9 , connect ikonnect and clear DTC. | closed | Jagdeep Saini | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
27 | East | 211737553 | 20/02/2025 | 15 | GP3.8501.../2421288 | Electrical Problems | Closed | R M GOLD | Revenus Industries Pvt. Ltd. - Nadia | 8.3 | DG shutdown showing under voltage Alarm due to the loose connection of voltage sensing wiring at MCB after tightening issue resolved. | CLOSED | Prosanjit saha | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
27 | WEST | 211709643 | 12/02/2025 | 30 | 3H.8902.../2421623 | Power Supplay Issue Call by Customer Name :-Bhavesh Keshrwani NO :-7999487242 | Closed | BHAVESH KESHARWANI | Shree Engineering Service - Bilaspur | 2 | loose connection in AMF panel so tight the wire. | closed | Jagdeep Saini | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
21 | North | 211673714 | 01/02/2025 | 125.4 | 4H.8041.../2420953 | Electrical Problems | Closed | AADITRIZ TRADERS | S. R Engines Sales And Service - Gorakhpur | 2 | Battery voltage low, Charger connection not done from customer end Supply not available, DG not start last 2 months | Closed | Sudhir Awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
19 | WEST | 211723575 | 17/02/2025 | 25 | GP3.8702.../2421571 | DG Battery Issue,Display required - 511177 | Task Start | ICICI Bank Limited | Transcreek Engineers Pvt. Ltd. - Panvel |  | cancelled | closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
29 | North | 211661634 | 30/01/2025 | 125.4 | 4H.8041.../2420218 | Maintenance Due Alarm Call By Customer Name :- Sachidanand Mobile No :-7042323811 | Cancelled | SGV. Super Security Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | Under cancellation-Problem solve in PM visit | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
30 | North | 211676890 | 02/02/2025 | 58.5 | T4.8941.../2420767 | Low oil issue Call by customer Name: RAHUL JI Number: 8588890193 | Open | Ankur Auto Sales Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad |  | Under cancellation-Customer aprrovel not received | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
39 | South | 211674111 | 01/02/2025 | 30 | 3H.8902.../2422076 | Starting/Stopping Issue | Closed | Axis Bank Ltd | G-Care Diesels Private Limited - Ernakulam | 2 | Checked dg staring issue noticed that dc fuse damage,Replaced dc fuse and dc fuse holder wire connections tighted properly and all fuses checked ok.checked engine oil and coolant level ok.Then dg started and tested starting and stopping issue rectified | Closed | Mr. Sanjaimon S | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
41 | North | 211661449 | 30/01/2025 | 40 | 3H.8951.../2420069 | Sound/Vibration Issue | Closed | Dr. Rahul Mittal Memorial Hospital. | SAAN Royal Power Solutions Private Limited - Panipat | 35.46 | Abnormal sound due to Air Cleaner bolt found loose so tightened the same | Closed | Ved Prakash Gupta | GOEM issue | [8 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
1 | South | 211729805 | 18/02/2025 | 57 | T4.8941.../2420547 | Starting/Stopping Issue | Task Start | Sairam Marbles and Tiles. | Laxmi Diesels - Visakhapatnam | 85 | EB Supply not given to Battery Charger so battery discharge | Closed | Mr. MD Saleem | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
31 | North | 211745342 | 22/02/2025 | 625 | DV0.8501.C4../2420079 | Display Issue And Load Issue Call By Customer Name :- Devendra Saini Mobile No :-8053353744 | Open | HPL. Electric & Power Ltd. | SAAN Royal Power Solutions Private Limited - Sonipat |  | Under Cancellation-Service Due | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
3 | South | 211729543 | 18/02/2025 | 200 | F6.8871.../2420012 | ECU Amber problem & Alarm problem Call by : Customer Name :Moorthi Contact :9941508250 | Task Start | A. K. Finishing Technologies | Madhu Engineering Sales & Service -Poonamallee,Chennai | 18 | 516166/0 FC found in Event log. Clear the DTC issue resoolve | Task Start | Mr. NandhaGopal | ECU | [8 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
29 | North | 211746030 | 22/02/2025 | 250 | F6.8841.../2420072 | Tripping Issue Call By Customer Name :-Gautam Mobile No :-7052442465 | Open | A. P. Concast | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Under Cancellation-No issue in DG | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
42 | North | 211661359 | 30/01/2025 | 10 | GP3.8301.../2420086 | DG set issue | Cancelled | Axis Bank Ltd | Industrial Power Solutions - LUDHIANA |  | Under Cancellation-No Issue found | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | East | 211717848 | 14/02/2025 | 40 | 3H.8951.../2420738 | Diesel not showing | Closed | JYOTISHMAN HARDWARE & GRILL | Hibreed Engineering Pvt. Ltd. - Nagaon | 511 | SE visited and found fuel level was fluctuating 30-65% frequently so he checked the fuel level sensor resistance found 100 ohm according to mechanical gauge it was ok (50-55%) so he checked for loose connection as such loose connection was not found but SE tighten all connetion related fuel gauge and also tighten all electrical connection in control panel then checked found OK not fluctuation found. | CLOSED | Ujjwal Das | [9 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
10 | South | 211727789 | 17/02/2025 | 5.5 | CC1.1013.../2400502 | Starting Problem Call by : KGD Name : k.V Prathap reddy Sir Contact : 9866435678 KGD NAME :Uma | Task Start | Ameva Enterprises | Laxmi Diesels - Vizianagaram | Cancelled | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
12 | South | 211727676 | 17/02/2025 | 82.5 | 5H.8901.../2420361 | Door lock problem Call by : KGD Name : Kameswara Rao Contact : 9949790703 Dealer name :- Uma | Task Start | Karri Kameswara Rao | Laxmi Diesels - Visakhapatnam | 4 | Replaced new Door lock with new one Under Warranty and Fitted Canopy rain guard Started the engine found engine running satisfactory with proper load | Closed | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
13 | South | 211727618 | 17/02/2025 | 125.4 | 4H.8042.C4../2421090 | Starting/Stopping Issue | Closed | Presidency | G-Care Diesels Private Limited - Kannur | 4 | Found fuel level low showing in controller, 516166/0 FC After removed fuel level sensor and cleaned and refitting found alarm clear condition. | Closed | Mr. Sanjaimon S | ECU fault | [8 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
15 | South | 211727342 | 17/02/2025 | 82.5 | 5H.8901.../2420268 | Starting issue Called by customer Name ; Sandesh Number : 8660863608 | Closed | Goyal & Co. | Surya Power Services - Bommasandra, Bangalore | 12 | 516166/0 FC & air lock issue after removing the air lock , clear the alram. Engine running fine | Closed | Mr. Anil Kumar H G | ECU | [8 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
16 | South | 211726440 | 17/02/2025 | 58.5 | T4.8941.../2421041 | Help | Open | Shaik Adam Basha. | Ultimate Power Source - Ananthapuramu | Cancelled | SR to be Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
1 | NORTH | 211729948 | 18/02/2025 | 250 | F6.8841.../2320012 | Genset Trip | Task Start | VAISHNO INDUSTRIES PVT LTD | Paluck Technologies Ltd. - Faridabad | 478 | Radiator fully chocked & Service due So, quatation send to the customer | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
2 | NORTH | 211729916 | 18/02/2025 | 30 | 3H.8902.../2420414 | Starting/Stopping Issue | Task Start | Tanu Engineering Products Private Limited.** | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2517 | Radiator fully chocked same Educate the customer for radiator cleaning | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
11 | South | 211727784 | 17/02/2025 | 15 | GP3.8501.../2421925 | Starting Problem Call by : Customer Name :New Jyothi Prakash Contact :7760429106 | Task Start | M/S.New Jyothi Prakash Bakery | Prasad Power Engineers - Chithradurga | 8 | Dg alarm Amber Lamp on notification show low fuel level on display. Additionaly check oil pressure switch and oil pressure switch wire loose connection so tight oil pressure switch connection and start the dg running ok check with load running condition found satisfactory | Closed | Mr. Anil Kumar H G | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
22 | North | 211745140 | 22/02/2025 | 40 | 3H.8951.../2420691 | Starting issue Call by customer Name - Deepak Fartyal No - 9639836606 | Cancelled | Mr. Sanjeev Agarwal. | Deep Jyoti Electricals and Services - Haldwani |  | Under Cancellation-Problem solve in tele discussion | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | East | 211724172 | 17/02/2025 | 125.4 | 4H.8041.../2420357 | Starting issue callby customer Name:Suraja Kumar Number:9570537309 | Task Start | Pir Jee Textiles | Globalline India Services Private Limited - Patna | 40 | As per the complaint SE talked customer there was the low urea level and need to topup the urea, and SR will cancelled | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
29 | South | 211676907 | 02/02/2025 | 200 | 6H.8435.../2420049 | Abnormal sound issue Call By Customer Name - Purushotam .. Number - 9482160721 | Task Start | BIMBA HOSPITALITY LLP | Surya Power Services - Mysuru | 13 | Abnormal sound, fan belt loose condition, then tight the fan belt, Engine working found ok | Closed | Mr. Anil Kumar H G | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
32 | North | 211674100 | 01/02/2025 | 125.4 | 4H.8042.C4../2420999 | Genset Trip | Open | Power Control System | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Cancelled-Problem solve wiout visit | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
17 | South | 211721725 | 15/02/2025 | 125.4 | 4H.8042.C4../2420429 | amphere alarm issue Email By - KGD Name -S.K.POWER SYSTEMS | Cancelled | Saravana Builders | Bharath Diesel Sales and Service - Chengalpattu | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
18 | South | 211721688 | 15/02/2025 | 40 | 3H.8951.../2420593 | ERROR CODE | Open | Axis Bank Ltd | Powerlinks Infra Tech Pvt Ltd - Secunderabad | Cancelled | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
23 | South | 211720777 | 15/02/2025 | 250 | F6.8841.../2420128 | Starting issue Call By Customer Name : Govardhan . Mobile No : 7795661049 | Open | AKSHAYAKALPA FARMS AND FOODS PRIVATE LIMITED | Surya Power Services - Peenya, Bangalore | 227 | Customer complaint for engine oil service request | Closed | Mr. Anil Kumar H G | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
33 | South | 211719758 | 15/02/2025 | 250 | F6.8842.C4../2420022 | Starting/Stopping Issue | Closed | Adishwar Auto Diagnostics Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 56.7 | Visited the site.as per customer complaint observed the engine tripping due to low coolant level alarm showing in controller.observed the radiator coolant level is ok but alarm showing in controller due to nagitve sensing problem.so additionally given the nagitve sensing to the controller and check the all wiring connections tightened found ok.crank the engine given the load observed the engine running condition with load upto 2hours and DG running condition found satisfaction. | Closed | Mr. MD Saleem | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
42 | North | 211741363 | 21/02/2025 | 82.5 | 5H.8901.../2420543 | Cam Sensor fitted | Task Start | IEC ELECTRIC POWER LIMITED | Suraj Motor Store - kathua | 1 | cam sensor touch the cam tonweel so remove cam tonweel and check cam tonweel worng fitment and Cam tonweel double damge advise to IEC please remove the radiator | Closed | Ved Prakash Gupta | [9 empty] | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
1 | East | 211726235 | 17/02/2025 | 15 | GP3.8501.../2421464 | Lub Oil Throw | Open | M.S Interprices | Globalline India Services Private Limited - Biharsharif | 179 | Line rejection(commisisiong not done yet)- AS per complaint SE visited site and at silencer found lube oil, so removed turbo and found no lube oil at exhaust manifold and so it is suspected that the lube oil at silencer is due to the turbo exhaust side oil seal damage and as per KRM data customer's load is 2-3 amp and it's an single phase DG, so turbo will be send for reparing. | OPEN | Prabhakar Kumar | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
36 | South | 211719480 | 15/02/2025 | 30 | 3H.8902.../2421386 | Abnormal sound problem Call by : Customer Name : Bala krishna Contact : 6301344490 | Closed | Pushadapu Infra Ventures LLP | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 2 | No Abnormal Sound observed by SE. | Closed | Mr. MD Saleem | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
38 | South | 211718696 | 14/02/2025 | 58.5 | T4.8941.../2421346 | Starting/Stopping Issue | Task Start | Vittal Das | Prasad Power Engineers - Udupi | 73 | Due to battery discharge for Mains sensing issue,so float battery fitted,and Dg battery taken to workshop for recharge, otherwise Dg running normally | Task Start | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
39 | South | 211718424 | 14/02/2025 | 20 | GP3.8601.../2421173 | KRM not working | Closed | Anitha Chandrasekran | Madhu Engineering Sales & Service - Teynampet,Chennai | 6 | Visit obove the, site check the engine check the problem,krm dc supply wiring is loose condition so krm not working then fix krm wiring properly now no issues in krm | Closed | Mr. NandhaGopal | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
40 | South | 211718397 | 14/02/2025 | 0 | 4H.8042.C4../2520041 | COOLANT LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the dg noticed the coolant leak for oil cooler to dosing module supply adaptor fixing inner thread damage | Task Start | Mr. NandhaGopal | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
41 | South | 211718359 | 14/02/2025 | 82.5 | 5H.8901.../2420339 | Starting Problem Call by : Customer Name :Chinna Samy Contact :8122598396 | Closed | BHAGGYAM CONSTRUCTIONS | Net Work Diesels - Chennai | 19 | 14.02.25: FOUND ENGINE NOT STARTING DUE TO BATTERY CHARGER CIRCUIT WIRING CONNECTION IN LOOSE CONDITION.CORRECTED THE SAME PROPERLY.FOUND OK BATTERY IS CHARGING PROPERLY.15.02.2025:AFTER BATTERY FULLY RECHARGED,CHECKED ALL SYSTEM.FOUND OK.STARTED AND TESTED THE ENGINE.FOUND ENGINE RUNNING PERFORMANCE IS SATISFACTORY. | Closed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
41 | North | 211741599 | 21/02/2025 | 500 | DV8.8501.C4../2320093 | Abnormal sound issue | Closed | AV. Unicoaters Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 212 | Abnormal sound due to Air pressure leak near turbo , CAC Clamp found loose near same ,Tightened the clamp & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
40 | North | 211742272 | 21/02/2025 | 20 | GP3.8601.../2421115 | Starting/Stopping Issue | Cancelled | HILAL BAKERY.. | Suraj Motor Store - Srinagar |  | Under Cancellation-Rectified on call | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
37 | South | 211718709 | 14/02/2025 | 20 | GP3.8601.../2421335 | Maintenance Due Call by : Customer Name : Kumaravel Contact : 9385413153 | Closed | B.G.NAIDU SWEETS PRIVATE LIMITED | Bharath Diesel Sales and Service - Tiruchirappalli | 40 | Checked Found DG Panel to AMF Panel Auto Sensing Wires Faulty So Auto Start Signal Not Receiving to DG Control Panel so Engine Not Starting in Auto Mode, So DG Control Panel EB Power Available So KG645c Control Unit Mains Monitoring Enable then EB Power Fail DG Start in Auto Mode ok, Load on Checked ok, No Issue DG Side, EB Battery Charger Working is Good. | Closed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
17 | South | 211709466 | 12/02/2025 | 250 | F6.8841.../2420160 | Oil Leakage Issue Call By Customer Name - Ramesh .. Number - 9940373359 | Closed | BKN EDUCATIONAL AND CHARITABLE TRUST | Madhu Engineering Sales & Service - Teynampet,Chennai | 597 | So after checked thr turbo train hose clip re.tight checked the clip.tight checking ok. Checked the engine oil level low top up engine oil.checked the engine oil level checking ok. checked the radiator coolant level checking ok.after the start the engine running performance found ok.checked the engine sound & smoke normal checked the output voltage checking ok.checked the no leakage for turbo train hose side ok. | Closed | Mr. NandhaGopal | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
5 | East | 211733140 | 19/02/2025 | 15 | GP3.8501.../2320017 | Red lamp on alarm issue And Preventive Maintenance Call By Customer Name:- Nitesh Kumar Number:- 9939240973 | Task Start | Panjab National Bank. . | Globalline India Services Private Limited - Purnia | 331 | No issue in DG service required SR will cancellation | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
14 | North | 211680960 | 04/02/2025 | 30 | 3H.8902.../2320151 | VOC -Fule meter issue and leakage issue. Customer Name -Anuj Customer Number-9654837371 Mode- SR Generated through CDI calling. | Task Start | Saras Medical Services | OVN Industries Private Limited - New Delhi | 45 | Fuel level not showing proper & Battery voltage show in the controller 10V but check in Battery terminal by Multimeter show 12v Check & Found in Controller 1& 2 piont Negative drop So, now give the negative supply direct through battery then show the all correct value | open | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
9 | North | 211699280 | 10/02/2025 | 58.5 | T4.8941.../2423329 | Loading issue Call By Customer Name :- Rakesh Mobile No :- 7018324952 | Task Start | SANT AUTO | Megatron Engineers - Amb | 10 | Load issue due to loose connection found in Customer's AMF Pannel , no issue found in DG so same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
18 | South | 211685797 | 05/02/2025 | 5.5 | CC1.1013.../2400024 | Service | Task Start | HEGDAL CONSTRUCTIONS | Vijayshree Diesel Sales and Service - Bellary | 363 | visit the check the engine oil and filter is ok but service alarm is clear, after checked engine running condition is ok.. | Tast Start | Mr. Anil Kumar H G | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
6 | North | 211699569 | 10/02/2025 | 30 | 3H.8902.../2420675 | Automation issue Call by Customer Name - SANJAY SHARMA No - 8979097952 | Task Start | R. L. Sharma Filling Station. | Espiem Engines & Machines (P) Limited - Agra | 93 | Found battery terminal was loose so, tightness the same then start the DG issue resolve | Closed | Sudhir Awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
16 | South | 211755302 | 25/02/2025 | 15 | GP3.8501.../2422117 | Flickering | Closed | The Karur Vysya Bank Limited | Bharath Diesel Sales and Service - Tiruchirappalli | 2 | DG Change Over Side Neutral Link Closing Not Properly, So While DG Load on Lightings Flickering already Commission time Inform to Supplier But Not Resolve the Problem, Changeover Switch Neutral Link Bolt Missing and Loose Connection So New Bolt. Fixed and Tightened then Flickering Problem Rectified Load on Checked ok. | Closed | Mr. NandhaGopal | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
24 | North | 211759247 | 26/02/2025 | 20 | GP3.8601.../2420479 | Leakage Issue | Closed | Dr. Sanjeev Singh. | Deep Jyoti Electricals and Services - Shahjahanpur | 53 | Coolant leakage from radiator hose clamp loose bottom side | Closed | Sudhir Awasthi | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
22 | South | 211685467 | 05/02/2025 | 125.4 | 4H.8042.C4../2420366 | Low Level Alarm Issue Call By Customer Name :Jagadeesh Sir No :7411205717 | Task Start | AMP Rose Private Limited | Surya Power Services - Kalyan Nagar | 146 | As per the customer complaint check the engine properly. Problem found in adblue and internal fault code 520528/31, 1761/17.so using the I konnect tool and clear the All dtc. Check the all parameters of engine found ok | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
1 | North | 211701555 | 10/02/2025 | 57 | T4.8941.../2420149 | Leakage Issue | Task Start | Sanjay Arora | OVN Industries Private Limited - New Delhi | 12.23 | Found oil filter leakage & Coolant hose clamp loose tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
19 | South | 211754804 | 25/02/2025 | 58.5 | T4.8941.../2420012 | Starting/Stopping Issue | Closed | M/s. St. Benedicts Academy | Surya Power Services - Billekahalli | 19 | 100/3 error code. Checked the wiring found ok then clear the DTC. Now engine running ok | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
35 | South | 211659567 | 30/01/2025 | 125.4 | 4H.8041.../2420976 | Starting/Stopping Issue | Closed | Citrus Trail | Surya Power Services - Bommasandra, Bangalore | 82 | Visit the site checked the fuel tank fuel is full but gauge showing fuel 44% check the fuel gauge suppler gauge direction wrong fitted gauge needal lock to fuel tank change the gauge direction and check the level showing properly and started the engine running condition ok | Closed | Mr. Anil Kumar H G | KRM check | [8 empty] | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
15 | East | 211694303 | 07/02/2025 | 625 | DV0.8501.C4../2420150 | Door lock Issue Email By - KGD Name -Deshmukh | Closed | Blinkit. . | Revenus Industries Pvt. Ltd. - Hooghly | 5 | SE check properly engine then found canopy door is not closed properly so adjust lock clamp then fitted and check lock found now canopy lock is properly closed and open and lock properly.after that start engine and observe all parameters found engine runs normal. | CLOSED | Prosanjit saha | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
13 | South | 211755568 | 25/02/2025 | 40 | 3H.8951.../2420593 | Starting Problem Call by : Customer Name : Pranith Contact : 7700957641 | Open | Axis Bank Ltd | Powerlinks Infra Tech Pvt Ltd - Secunderabad | Cancelled | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
24 | South | 211685276 | 05/02/2025 | 25 | GP3.8702.../2420070 | Starting/Stopping Issue | Task Start | KOLATHAKKARA FUELS | G-Care Diesels Private Limited - Calicut | 354 | check the problem found exhaust bellow broken need replacement,and also radiator and tac fins blocked need fins cleaning | Closed | Mr. Sanjaimon S | Communication to AMe | [8 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
23 | South | 211754545 | 25/02/2025 | 200 | 6H.8435.../2420168 | Leakage Issue | Closed | Ayati Constructions & Estates LLP | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 26 | Minor leakage from radiator hose clip, found hose clip loose so retighten & clear the issue. | Closed | Mr. MD Saleem | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
18 | South | 211611495 | 16/01/2025 | 25 | GP3.8702.../2421365 | Black smoke problem Call by : Customer Name : Mohammad Contact : 9573676959 | Closed | MOHSIN KHAN | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 12.48 | No issue in DG .visit the site check the engine oil level and v belt and coolant level found ok after start the dg working ok, battery customer asking dg exhaust pipe extending required, | Closed | Mr. MD Saleem | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
20 | North | 211759912 | 26/02/2025 | 58.5 | T4.8941.../2422467 | VOC -CANOPY DOOR/LOCK PROBLEM Customer Name -Parveen Customer Number -7988639205 Mode- SR Generated through CDI calling. | Task Start | nabadurga pesticides pvt ltd | Paluck Technologies Ltd. - Faridabad | 11 | Canopy door lock issue not proper work so, need to be replace | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
11 | East | 211684917 | 05/02/2025 | 5.5 | CC1.1013.../2400016 | Starting Issue Call By Customer Name :- Shakti Kumar Mobile No:-6294815565 | Open | East Coast Railway Andhra Pradesh | HACS Engineering and Tech Private Limited - Deoghar |  | Service required so cancellation mail send to the helpdesk | OPEN | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | East | 211687370 | 06/02/2025 | 20 | GP3.8601.../2420789 | Starting/Stopping Issue | Task Start | M/S. SARS INTERIOR | Green Powerline - Tezpur | 63 | crank DG but not cranked properly so checked battery voltage found OK so tighten the battery terminal clamp found loose then crank The DG started normally | CLOSED | Ujjwal Das | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
20 | South | 211661961 | 30/01/2025 | 20 | GP3.8601.../2421529 | ENGINE NOT START | Task Start | Shobha | Prasad Power Engineers - Mangalore | LR | Visited the site, Observed battery under voltage. so removed battery and customer took Battery to recharge. Run the dg using float battery. Checked all parameters. all parameters are ok. dg running properly. No issue they open for claim | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
17 | North | 211760078 | 26/02/2025 | 62.5 | T4.8941.../2320179 | ALARM ISSUE | Closed | Yaduvanshi Generators Services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2701 | Found radiator was chocked so, cleaning required | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
8 | East | 211686500 | 05/02/2025 | 30 | 3H.8902.../2422023 | Automation Issue Email By - KGD Name - Arup Kr. Ray | Open | M/S F. DKHAR AUTOMOBILE SPARE PARTS | Hibreed Engineering Pvt. Ltd. - Guwahati |  | SR cancelled due to customer side issue. | OPEN | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | East | 211690602 | 06/02/2025 | 20 | GP3.8601.../2421228 | Starting Issue & KRM Issue. Call By KGD. Name:-Sahil Mobile No.:-7909030218 | Open | Shakuntala Mart | Globalline India Services Private Limited - Patna | 25 | DG was not cranking, so SE checked battery voltage found ok but then also not starting so checked the voltage at starter motor solenoid 3 no. wire found 0 voltage so on checking found relay not holding so checked the voltage at relay positive pin found 5-6V so retighten controller 3 no. jack wire and then started issue solved, after SE ensure allthe connection tightness in the pannel. | OPEN | Prabhakar Kumar | [9 empty] | Starter Motor | 7 | 4 | 5 | 140 | Moderate
6 | East | 211683846 | 05/02/2025 | 20 | GP3.8601.../2421238 | Starting Issue Email by KGD Name - sunrise power | Open | ROHIT KUMAR | Globalline India Services Private Limited - Darbhanga | 68 | SR cancelled service required | OPEN | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
22 | South | 211754594 | 25/02/2025 | 40 | 3H.8951.../2421518 | Starting Problem Call by : Customer Name : Ifchekar Contact : 9008999822 | Closed | M/s. Embassy Services Pvt. Ltd. | Surya Power Services - Kalyan Nagar | 6 | 2802/4 , 157/14 error code so checked the panel wiring then clear the DTC. Now issue resolved. | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
11 | North | 211698901 | 10/02/2025 | 82.5 | 5H.8901.../2420005 | Starting Issue Call By Customer Name - Paramveer Number - 9999576496 | Task Start | Smitha Surgicals India Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 330 | Battery voltage low, because charger not connected, connect the wire after that DG start with another battery issue resolve | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
17 | South | 211686803 | 05/02/2025 | 25 | GP3.8702.../2420163 | Starting/Stopping Issue | Completed | Vaneesa Infra Developerrs Private Limited. | Net Work Diesels - Sholinganallur | 60 | VISIT THE SITE TO ATTEND THE COMPLAINT OFF ENGINE NOT STARTING DURING INSPECTION CHECK THE ENGINE FOUND BATTERY WAS DISCHARGE CONDITION DUE TO CHECK THE BATTERY CHARGER WORKING NORMAL .AND BATTERY DISTILLED LEVEL FOUND OK .PROBLEM SUSPECT FROM BATTERY (BATTERY VOLTAGE 10.30) SO BATTERY NEEDS TO BE NECESSARY INSPECTION | Completed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
3 | North | 211682793 | 04/02/2025 | 250 | F6.8842.C4../2420015 | Starting issue | Closed | Satyam Packaging | Pratap Diesels Pvt. Ltd. - Bhiwadi | 52.28 | Battery voltage low, Charger not connected, connect the charger then start the battery charging | Closed | Gourav Sharma | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
5 | East | 211702199 | 10/02/2025 | 15 | GP3.8501.../2420272 | Loading Issue & Preventive Maintanance Call By Customer Name :- Ngatum Sir Mobile No :-8731087541 | Open | APEX STRUCTURE PVT LTD | Almas Engineers - Dibrugarh | 314 | Unbalance load from customer end wet PM required so SR is cancelled. | CANCELLED | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | East | 211698195 | 09/02/2025 | 20 | GP3.8604.../2420182 | INSTANCE ID:-100742009 SITE ID:-I-BR-GAYA-ENB-0041 CALL BY CUSTOMER\\ DG ISSUE :-DG PROBLEM NAME:-DEEPAK KUMAR NUMBER:-8340312768 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Gaya |  | SR Cancelled | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | East | 211748892 | 23/02/2025 | 20 | GP3.8604.../2420089 | INSTANCE ID:-100740918 SITE ID:- I-BR-DHKA-ENB-9025 DG ISSUE:-DG ALARM ISSUE NAME: DEEPRAJ NUMBER:-9229202768 | Cancelled | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Purnia |  | Cancelled SR no issue in DG | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | West | 211651092 | 28/01/2025 | 250 | F6.8841.../2420175 | ECU issue Call By Service Dealer Name - Vijay Choudhary Number - 7722039102 | Closed | SHREYA CONSTRUCTION | Dhanashree Technocrats Pvt. Ltd. - Jalgaon | 498 | Engg. Visited and checked supply voltage is not operating so visit again for supply module replacement. | OPEN | Jagdeep Saini | [9 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
12 | South | 211683356 | 04/02/2025 | 100 | 4H.8041.../2420734 | Leakage Issue | Closed | KNR CONSTRUCTIONS LTD | Sri Manjunath Technical Services - Ongole | 259 | DG running condition it was oil leakage problem due to oil filter o ring failure then replaced the oil filter checked the oil leakages no leakage | Closed | Mr. MD Saleem | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
11 | North | 211702138 | 10/02/2025 | 25 | GP3.8702.../2420946 | Starting/Stopping Issue | Closed | BHARAT CROP PROTECTION PVT LTD | SAAN Royal Power Solutions Private Limited - Hisar | 6 | Starting Issue due to battery voltage found low,Charger was not connected with mains supply so charge the same after mains connected & resolved the issue | Closed | Ved Prakash Gupta | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
47 | North | 211762980 | 27/02/2025 | 20 | GP3.8601.../2421256 | battery charger faulty | Task Start | SHRADHA COLLECTION | Pratap Diesels Pvt. Ltd. - Kota | LR | Found Battery charger faulty because when we give the 230v supply Charger not on | open | Gourav Sharma | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
42 | South | 211657257 | 29/01/2025 | 30 | 3H.8902.../2421171 | Starting issue Call By: Customer Name :Chikapayya No :8296608529 | Open | Chikkappaiah | Surya Power Services - Peenya, Bangalore | 35.14 | Asper customer complaint DG not starting. Visited the site observed battery got discharged. Battery needs to be recharge immediately. | Task Start | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
8 | North | 211703296 | 10/02/2025 | 20 | GP3.8601.../2320057 | Starting issue Call by customer Name - Harshdeep . Number - 7404979690 | Open | Sobhagia Sales Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Ambala | 92.68 | Under Cancellation-Service due | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
8 | South | 211642875 | 25/01/2025 | 58.5 | T4.8941.../2422766 | Oil leakage issue Call by : Customer Name : Sabari Contact : 9363640877 | Task Start | AGP Engineers | Electro Controls - Coimbatore | 1012.5 | removed radiator and accessories cleaning and Replaced gear end oil seal | Closed | Mr. Sanjaimon S | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
1 | North | 211705377 | 11/02/2025 | 500 | DV8.8501.C4../2320029 | Starting/Stopping Issue | Open | Sheen Agri Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar | 172.28 | Under Cancellation-No Issue in DG | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
11 | East | 211685147 | 05/02/2025 | 58.5 | T4.8941.../2420403 | Under Speed Alarm Call By Customer Name :- Ravi Kumar Mobile No :-9934852155 | Task Start | Ravi Soni | Globalline India Services Private Limited - Muzaffarpur | 149 | Proper update pending as per cordinator there was loose connection in control panel so SE tighten and issue resolved, SE is on leave not able to connect with him. | OPEN | Prabhakar Kumar | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
4 | South | 211758228 | 26/02/2025 | 40 | 3H.8951.../2420575 | Leakage Issue | Task Start | United Intigration | Prasad Power Engineers - Mangalore |  | Leakage from oil cooler side. | Task Start | Mr. Anil Kumar H G | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
9 | East | 211701374 | 10/02/2025 | 20 | GP3.8601.../2420651 | V belt issue | Task Start | Hill Billy | Green Powerline - Tezpur | 149 | There was an abnormal sound due to the V belt loose after tightening issue resolved | CLOSED | Ujjwal Das | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
8 | South | 211679419 | 03/02/2025 | 82.5 | 5H.8901.../2420039 | AMF panel problem Call by :Customer Name : Khaja Contact : 9154784695 | Closed | Baba Infra and Developers | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 2.48 | Attended the site for engine starting problem in auto mode of crank code (636/0) alarm and v belt adjusted and cam sensore check wirring adjusted fitted and start to be running ok | Closed | Mr. MD Saleem | [9 empty] | Cam Sensor | 5 | 4 | 5 | 100 | Moderate
40 | South | 211658564 | 29/01/2025 | 5.5 | CC1.1013.../2400021 | Smoking Problem Call by : Customer Name : VIVIAN TIES Contact :9400302821 | Closed | VIVIAN TIES | G-Care Diesels Private Limited - Kannur | 34 | Over load, advice customer to minimise the load connected CHECK ENGINE OIL LEVEL AND CONDITION, CHECK ALL ELECTRICAL CONNECTIONS AND OUTPUT VOLTAGE FOUND NORMAL, CHECK LOAD CONNECTED FOUND OVER LOAD,FRIDGE -3 NOSLED BOARD LIGHT- 1NOSEX FAN -2 NOSCEILING FAN -9 NOSLED TUBE-12 NOSLED FILAMENT BULB- 12 NOSLED 10 W BULB- 172 NOSINDUCTION COOKER -1 NOSELECTRIC KETTLE -1 NOSGRINDER -1 NOSGENSET RUNNING SMOOTHLY ON RECOMMENDED LOAD, GENSET WORKING NORMAL | Closed | Mr. Sanjaimon S | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
2 | East | 211699349 | 10/02/2025 | 5.5 | CC1.1013.../2400366 | Abnormal voice issue Call by Customer Name : Himanshu Barik No 7848976414 | Task Start | Creative Image | Gangpur Sales and Services - BHUBANESWAR | 69 | Engine RPM was not going above 1500 and shutdown due to Under Speed Alarm and on running condition there was an abnormal sound at some where cylinder so after overhauling of head found the Piston's compression ring was not installed properly | OPEN | Ujjwal Das | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
15 | South | 211641911 | 25/01/2025 | 15 | GP3.8501.../2421338 | LFL not working | Closed | Mr. Syed Aziz Babu Garu | Laxmi Diesels - Rajahmundry | LR | Inspected the site DG checked oil level, coolant level,v belt tension ok. Engine not starting previous visit LFL SENSOR not working, so replaced the same, checked and re tighted all electrical connection and fuel lines . Started the genset running condition is ok | Closed | Mr. MD Saleem | [9 empty] | Fuel Lines | 7 | 5 | 4 | 140 | Moderate
16 | South | 211641892 | 25/01/2025 | 10 | GP3.8301.../2420158 | Starting/Stopping Issue | Closed | ALICE MEDICAL CENTRE | G-Care Diesels Private Limited - Kannur | 50 | Attended the site as per customer call about starting trouble , checked the engine found that fuel level variation in controller . Remove the fuel level sensor and cleaned and refitted .then checked the fuel level and found stable. Then started the engine, found ok | Closed | Mr. Sanjaimon S | [9 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
20 | North | 211696863 | 08/02/2025 | 40 | 3H.8951.../2421389 | Starting/Stopping Issue | Closed | METFAB TECHNOLOGIES | SAAN Royal Power Solutions Private Limited - Zirakpur | 17 | DG Starting issue due to Relay burnt in customer's pannel due to which battery charger MCB down so corrected the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
7 | South | 211684348 | 05/02/2025 | 20 | GP3.8601.../2420141 | Display Showing "Maintenance Due " Call by : Customer Name :Mathew Varghese Contact :9539800961 | Open | MUNDAKAPADAM MANDIRAM HOSPITAL | Electro Controls - Kottayam | Cancelled | Cancelled | Cancelled | Mr. Sanjaimon S | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
12 | South | 211757852 | 26/02/2025 | 58.5 | T4.8941.../2420276 | Starting Problem Call by : Customer Name :Bala Contact :9443333424 | Task Start | S. Kannan | Bharath Diesel Sales and Service - NAMAKKAL | 113 | Inspected the engine battery not charging by battery charger.Battery voltage low (6V). Battery need to check.Battery removed and sent to testing.start with standby battery load on all parameters working ok.No leakage.Issue not solved | Task Start | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
17 | South | 211612184 | 16/01/2025 | 200 | 6H.8435.../2420257 | Starting/Stopping Issue | Closed | Utsav | Surya Power Services - Bommasandra, Bangalore | 8 | visit the site check the engine problem is fuel level sensor is not working properly due to fuel sensor height issue after replaced the new new fuel sensor height is 220mm fixed after clear the fuel sensor falt code check the engine all parameters after start the engine running coundtion ok | Closed | Mr. Anil Kumar H G | BoM need to check as per part number | [8 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
21 | South | 211661865 | 30/01/2025 | 30 | 3H.8902.../2421502 | coolant leakage problem Call by : Customer Name :Sankar Contact :9591049300 | Closed | JPS. Trading Co. | Surya Power Services - Chikkaballapur | 92 | Visited the site carried out the daily check up and Coolant leakage in radiator return hose side and tight the hose clamps and top up the coolant after started the engine no leakage running found normal. Ok | Closed | Mr. Anil Kumar H G | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
13 | South | 211683295 | 04/02/2025 | 35 | 3H.8902.../2421781 | ABNORMAL SOUND | Task Start | Sri Shiridi Sai Engineering | Laxmi Diesels - Visakhapatnam | Cancelled | Cancelled | Cancelled | Mr. MD Saleem | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | East | 211692471 | 07/02/2025 | 125.4 | 4H.8041.../2420525 | Black Smoke Issue & Stop speed Issue. Call By Customer. Name:-Gopal Sharma Mobile No.:-8011058372 | Task Start | Binod Karnani. | Hibreed Engineering Pvt. Ltd. - Jorhat | 150 | Fault code 516166 triggred so cleared DTC and also found lube oil level low topup the lube and and found no smoke as per the complain. | CLOSED | Ujjwal Das | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
73 | North | 211685155 | 05/02/2025 | 250 | F6.8842.C4../2420061 | LINE REJECTION | Closed | BHARATIYA JANATA PARTY | SAAN Royal Power Solutions Private Limited - Zirakpur | 2(LR) | Oil Leakage found from oil filter due to found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
39 | North | 211696754 | 08/02/2025 | 125.4 | 4H.8042.C4../2420734 | Trip_Genset_Low_Voltage | Cancelled | Hotel Subhadra | Espiem Engines & Machines (P) Limited - KANPUR |  | Under Cancellation- problem solve in telediscussion | Cancelled | Sudhir awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
10 | North | 211754067 | 25/02/2025 | 82.5 | 5H.8901.../2420392 | Coolent | Closed | KALYAN JEWELLERS.. | Megatron Engineers - Amritsar | 27 | Coolant leakage found on hose of Water Pump due to clamp found ;loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Water Pump | 7 | 6 | 4 | 168 | Moderate
21 | South | 211758641 | 26/02/2025 | 45 | 3H.8951.../2421276 | Starting/Stopping Issue | Task Start | M/s. Creative Green Inventions | Laxmi Diesels - Rajahmundry | 100 | Battery voltage low, Eb supply not given to battery Charger | Closed | Mr. MD Saleem | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
12 | North | 211753586 | 25/02/2025 | 320 | F6.8802.../2320050 | Coolant leakage issue | Closed | JAYCEE CASTALLOYS (P) LTD. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 265 | Coolant leakage found on top Radiator pipe (Thermo-stat to Radiator) due to clamp found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
33 | North | 211688687 | 06/02/2025 | 15 | GP3.8501.../2420482 | Fuel Leakage Issue Call By Customer Name :-Rajesh Kumar Mobile No :-9452749999 | Closed | Ratan Filling Station | Espiem Engines & Machines (P) Limited - Banda | 15 | Battery voltage low, Check with another battery found ok & Battery charger connection not done, now connect the charger connection then issue resolve | Closed | Sudhir awasthi | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
14 | East | 211673465 | 01/02/2025 | 30 | 3H.8902.../2420243 | Starting Issue Call By Customer Name :- MITESH AGRAWAL Mobile No :-7894071139 | Closed | Arati Agrawal. | Gangpur Sales and Services - Bolangir | 1201 | SE found engine not started due to air lock in fuel system,after that check the fuel line properly and air released in fuel line found water in fuel sensor O ring Damage replace the O ring issue resolved. | CLOSED | Ujjwal Das | [9 empty] | Water in Fuel Sensor | 7 | 5 | 4 | 140 | Moderate
16 | South | 211759003 | 26/02/2025 | 160 | 6H.8475.../2420314 | Sound/Vibration Issue | Closed | S. K. Heart Care Hospital. | Bharath Diesel Sales and Service - Tiruchirappalli | 46 | Abnormal sound due to V belt loose , so retight the belt problem solved. | Closed | Mr. NandhaGopal | [9 empty] | Abnormal Sound | 7 | 5 | 3 | 105 | Moderate
14 | South | 211759050 | 26/02/2025 | 25 | GP3.8702.../2421566 | Leakage Issue | Closed | B. Jothi | Bharath Diesel Sales and Service - Dharmapuri | 5 | Checked the DG now radiator bottom hose side coolant leakage so hose clip retightning then coolant leak arrested | Closed | Mr. NandhaGopal | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
12 | South | 211759894 | 26/02/2025 | 40 | 3H.8951.../2320046 | Starting Issue Call By Customer Name - Sence Kurian Number - 9446066944 | Closed | PAVITHRA GOLD | Madurai Electro Controls - Theni | 85 | BATTERY VOLTAGE CHECKED,BATTERY VOLTAGE LOW, BATTERY DISTILLED WATER LEVEL CHECKED, BATTERY CHARGER CABLE LOOSE CONNECTION TIGHT THE WIRE BATTERY CHARGER WORK CHARGE THE BATTERY NOW START THE GENSET RUNNING GOOD CONDITION, PERFORMANCE OK | Closed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
27 | North | 211691902 | 07/02/2025 | 160 | 6H.8475.../2320032 | Coolant Leakage Issue Call By Customer Name :- Nitin Sir Mobile No :- 9818270101 | Task Start | Nirupam Vatika Society | Vidyut Engineers - Noida | 143.18 | Found oil mix in Coolant because Gasket not found in Oil cooler that’s reason mixing of coolant & Oil | open | Kapil Solanki | [9 empty] | Oil Cooler | 7 | 5 | 4 | 140 | Moderate
40 | North | 211696358 | 08/02/2025 | 45 | 3H.8951.../2420715 | Starting issue Call By Customer Name :- Soni Mobile No :-9369942055 | Closed | Purnodaya Mahila Mahavidyalaya | SAM Engineering corporation - Varanasi Cantt. | 70 | DG starting problem and control panel wiring loose 2B3no of switch wiring loose and correct type kiya Oil check kiya coolent check kiya vbelt check kiya battery water | open | Sudhir awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
5 | East | 211674499 | 01/02/2025 | 400 | DV8.8542.C4../2420116 | Starting issue | Open | NORTH EAST FRONTIER RAILWAY | Hibreed Engineering Pvt. Ltd. - Guwahati | 0 | No issue in DG cancellation mail send to helpdesk | OPEN | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
23 | North | 211692701 | 07/02/2025 | 250 | F6.8841.../2320019 | Coolent leakage issue Call By Customer Name : -Ramesh No:-9911266168 | Task Start | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 509 | coolant leakege from water pump weep hole.when the dg is off drop off coolant comes outfrom the weep hole and after running the dg a lot of coolant drop from weep hole Educate the customer for not start the DG if you run the DG Its your responsible | open | Kapil Solanki | Failed part | [8 empty] | Water Pump | 7 | 6 | 4 | 168 | Moderate
21 | North | 211693242 | 07/02/2025 | 58.5 | T4.8941.../2420636 | Starting/Stopping Issue | Closed | SKS ISPAT & POWER LTD | OVN Industries Private Limited - New Delhi | 28.7 | Found battery terminal was loose tightness the same & low fuel level & Coolant low in Recovery bottle topup the both | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
7 | South | 211760589 | 26/02/2025 | 25 | GP3.8702.../2420368 | Starting Problem Call by : Customer Name : Ashath Contact : 7845790749 | Task Start | S. T. Courier | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 7.1 | Engine not starting issue and checked the battery low voltage due to eb not given so remove the battery and recharge the battery | Task Start | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
7 | East | 211673520 | 01/02/2025 | 58.5 | T4.8941.../2420951 | Starting/Stopping Issue | Open | B. A. C. Infratech Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 960 | Neutral link burn so replaced on paid basis and SR will be cancelled | OPEN | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
1 | North | 211688622 | 06/02/2025 | 15 | GP3.8501.../2420933 | Maintenance Due Alarm Call By Customer Name :- Vinod Mobile No :- 9793126690 | Open | Maa Radhika Automobiles | SAM Engineering corporation - Varanasi Cantt. |  | Cancelled- Problem solve in PM Visit | Cancelled | Sudhir awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | South | 211761166 | 27/02/2025 | 125.4 | 4H.8041.../2420708 | Starting Problem Call by : Customer Name :SHANKAR Contact :9047016599 | Open | GMS ELEGANT BUILDERS (I) PVT LTD | Net Work Diesels - Potheri | 2055 | 516166/0 error code clear the dtc | Closed | Mr. NandhaGopal | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
7 | North | 211687135 | 06/02/2025 | 15 | GP3.8501.../2420028 | INSTANCE ID:-100740393 SITE ID:- 17876 CALL BY CUSTOMER// DG ISSUE:- DG BELT/STARTING PROBLEM NAME:- PRAMOD NUMBER:- 9871953792 | Task Start | Bharti Airtel MO-Delhi | Vidyut Engineers - New Delhi | 2360 | Attend the site checked engine oil level and radiator coolent level V belts replaced after that the DG set tested 30 minutes on load checked | Closed | Kapil Solanki | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
16 | WEST | 211757903 | 26/02/2025 | 82.5 | 5H.8901.../2420963 | EGR ISSUE | Task Start | Perennial Technologies Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 1LR | Ambient Air temperature sensor connector was disconnected from GOEM side. So connected the same and cleared the DTC. | Open | Jagdeep Saini | ECU fault. GOEM report to check | [8 empty] | Temperature Sensor | 7 | 5 | 4 | 140 | Moderate
17 | North | 211693620 | 07/02/2025 | 125.4 | 4H.8041.../2420745 | Starting/Stopping Issue | Task Start | JAIN GENERATOR HIRING CO.. | OVN Industries Private Limited - New Delhi | 1577.45 | Found Radiator was chocked condition, Send to the Quatation to Customer for radiator cleaning | Closed | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
9 | North | 211686848 | 05/02/2025 | 15 | GP3.8501.../2421667 | Under voltage alarm and preventive maintanance Called by customer Name: YOGESH Number : 6375000318 | Open | BAGTESH INFRA | Rajdhani Diesels and Electricals - Jodhpur |  | Cancelled- Problem solve in PM Visit | Cancelled | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
17 | West | 211697221 | 08/02/2025 | 40 | 3H.8951.../2420258 | Starting/Stopping Issue | Task Start | Wintech Engineering Works | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 42 | Fuse between mains and battery charger found burn so change the fuse. | Closed | Jagdeep saini | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
1 | North | 211758818 | 26/02/2025 | 58.5 | T4.8941.../2421613 | Fuel Sensor Issue Email by KGD Name - Rinki Maheshwari | Task Start | Darshan Power Solutions | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1557 | Engine Coolant tem. High because Radiator found chocked (Last CSP 1171 on 22-01-2025) | Open | Kapil Solanki | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
1 | South | 211685003 | 05/02/2025 | 125.4 | 4H.8042.C4../2420460 | Error Code & Voltage problem Call by : Customer Name : Selvinchristopher Contact : 9486985201 | Open | V. P. Synergic Weld Solutions Pvt. Ltd. | Madhu Engineering Sales & Service - Kavaraipettai, Chennai | 38 | 516166/0 fault code found clear the DTC. | Closed | Mr. NandhaGopal | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
9 | North | 211754345 | 25/02/2025 | 320 | F6.8802.../2420078 | Code issue | Closed | Chirag Industries | SAAN Royal Power Solutions Private Limited - Sonipat | 108.1 | Coolant level low alarm occurred but coolant found in radiator,check the coolant level switch,which found faulty so need to replace the same | Closed | Ved Prakash Gupta | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
71 | North | 211685324 | 05/02/2025 | 160 | 6H.8475.../2420335 | LINE REJECTION | Closed | BHARATIYA JANATA PARTY | SAAN Royal Power Solutions Private Limited - Zirakpur | 2(LR) | NRV Found faulty ; will replace the same | Open | Ved Prakash Gupta | [9 empty] | NRV | 6 | 5 | 4 | 120 | Moderate
11 | North | 211756348 | 25/02/2025 | 40 | 3H.8951.../2421197 | Starting issue Called by customer Name: Dhruv Number : 7409793115 | Open | Axis Bank Ltd | R K Engineers - Meerut |  | Cancelled | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
68 | North | 211686684 | 05/02/2025 | 58.5 | T4.8941.../2422427 | Coolant Leakage issue Call By Customer Name: Sumit No:- 9896695251 | Closed | Aadi International | SAAN Royal Power Solutions Private Limited - Panipat | 5.37 | Coolant Leakage found from radiator to water pump(Bottom side) due to clamp found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Water Pump | 7 | 6 | 4 | 168 | Moderate
10 | North | 211756609 | 25/02/2025 | 40 | 3H.8951.../2420569 | Diesel Leakage Problem Email By KGD Name:-United Power Solution | Open | Mr. Sandeep Aggarwal | OVN Industries Private Limited - New Delhi |  | Cancelled | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
14 | East | 211688696 | 06/02/2025 | 25 | GP3.8702.../2420248 | Automation Issue | cancelled | Palsit Pure & Sure Filling Station | Revenus Industries Pvt. Ltd. - Purba Burdwan | 12 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Prosanjit saha | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
65 | North | 211687601 | 06/02/2025 | 320 | F6.8802.../2420225 | DG Alarm Issue Email by Customer Name - Pankaj | Open | MORARJI DESAI RESIDENCEAL SCHOOL | Suraj Motor Store - kathua | 1167 | Under Cancellation-wrongly Open SR | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
64 | North | 211688011 | 06/02/2025 | 82.5 | 5H.8901.../2420565 | Starting Issue & Preventive Maintenance Call By Customer Name :- Nitin Agarwal Mobile No :- 9466650667 | Closed | VERMA TRADING COMPANY | SAAN Royal Power Solutions Private Limited - Hisar | 13 | Canopy door lock faulty , fix by hinge & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | North | 211758046 | 26/02/2025 | 125.4 | 4H.8041.../2420034 | Starting/Stopping Issue | Task Start | S. G. Wires | Paluck Technologies Ltd. - Faridabad | 545 | During starting DG take was long cranking after Check NRV Air pass from both side then NRV valve change after that issue resolve | Closed | Kapil Solanki | [9 empty] | NRV | 6 | 5 | 4 | 120 | Moderate
62 | North | 211690167 | 06/02/2025 | 15 | GP3.8501.../2420659 | Amber lamp On Alarm Issue Call By Customer Name :Reshan .. No :9002207788 | Open | M. H. Joinery Machines | Suraj Motor Store - Srinagar | 39.41 | Under Cancellation-resolved on telephonic discussion | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | South | 211684828 | 05/02/2025 | 160 | 6H.8475.../2420103 | Coolant leakage problem Call by : Customer Name : Mohan kumar Contact : 9008101385 | Task Start | Fact Entry Data Solutions P. Ltd. | Ultimate Power Source - Vellore | 62 | Coolant leakage from radiator hose clamp. Loose tighten the Same. | Closed | Mr. NandhaGopal | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
61 | North | 211690790 | 06/02/2025 | 125.4 | 4H.8041.../2420624 | Low Level Urea Alarm issue Call By Customer Name :- Shivam Mittal Mobile No :-8727852470 | Cancelled | Ganpati Plastic Industries. | Industrial Power Solutions - LUDHIANA | 22.3 | Under Cancellation-Issue resolved on Telephonic discussion | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
11 | North | 211662502 | 30/01/2025 | 160 | 6H.8475.../2420030 | Starting Issue Call By Customer Name :-Rajiv Sir Mobile No :-9968080005 | Closed | Sri Vijayrama Impex Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 3.04 | Battery voltage low, charger not charge the battery | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
56 | North | 211692822 | 07/02/2025 | 58.5 | T4.8941.../2421651 | Starting/Stopping Issue | Closed | Mr. Rajesh Kumar | SAAN Royal Power Solutions Private Limited - Hisar | 18 | Air locking due to Low Fuel Level so Top-up the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
3 | WEST | 211679227 | 03/02/2025 | 500 | DV8.8501.C4../2420423 | Parameter not showing | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | lr | CAN commounication parameter not showing in DCU Bank A , Change the DCU. | Closed | Jagdeep saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | North | 211758272 | 26/02/2025 | 25 | GP3.8702.../2420003 | I & C Work | Open | BHARTI AIRTEL LIMITED | SAAN Royal Power Solutions Private Limited - Karnal | LR | Under Cancellation-work done on Paid basis | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | WEST | 211684247 | 05/02/2025 | 58.5 | T4.8941.../2420879 | Starting Issue And red light alarm Issue . Call By Customer Name :- Sandip Ambre Mobile No:-7020544726 | Closed | KAMAL MADAN AMBRE | KALA Care Global LLP - Babhleshwar | 77 | loose connection in AMF panel so tight the wire issue solved. | Closed | Jagdeep saini | [9 empty] | Loose Connection | 5 | 6 | 4 | 120 | Moderate
13 | North | 211664207 | 31/01/2025 | 125.4 | 4H.8041.../2420586 | Leakage Issue | Closed | Capital Spindles India Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 38 | Wrong report- Canopy door lock issue new, lock reqirement | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
49 | North | 211695054 | 08/02/2025 | 250 | F6.8841.../2420110 | Genset Trip | Closed | KIDS CLINIC INDIA LIMITED | OVN Industries Private Limited - New Delhi | 1653 | emergency swich on mode because engine not start and found the engine emergency swich off mode then start the engine ok battery water lavel check ok radiator dust in fins | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
48 | North | 211695059 | 08/02/2025 | 25 | GP3.8702.../2421287 | Genset Trip | Closed | NEERU MATERITY CENTRE | OVN Industries Private Limited - New Delhi | 3.9 | Found maintenance alarm, removed the alarm and battery tarminal tight start the DG then issue resolve | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
47 | North | 211695166 | 08/02/2025 | 125.4 | 4H.8041.../2420586 | Genset Trip | Closed | Capital Spindles India Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 40.31 | Found canopy door lock defective change the lock then issue resolve | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
46 | North | 211695206 | 08/02/2025 | 125.4 | 4H.8042.C4../2420669 | Amber lamp alarm issue & Preventive Maintenance Call By Customer Name :- Pranav Mishra Mobile No :-7482897729 | Cancelled | Arihant Contractor | S.S. Enterprises - Allahabad |  | Under Cancellation | Cancelled | Sudhir awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
7 | WEST | 211685086 | 05/02/2025 | 15 | GP3.8501.../2520181 | OIL LEAKAGE FROM FILTER | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from oil filter so Relpace oil filter | Closed | Jagdeep saini | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
30 | South | 211660630 | 30/01/2025 | 15 | GP3.8501.../2420250 | Starting/Stopping Issue | Closed | Raghavendra Constructions. | Laxmi Diesels - Visakhapatnam | 2.1 | Checked the DG observed Observed controller wire 2d wire is in loose contact, checked and reconnected the same and checked the battery cables self motor battery distillery water checked due to observed Single pole MCB 2B positive Cable disconnected because Cable loose Contact Tight fitted Display on DG running problem rectified | Closed | Mr. MD Saleem | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
7 | North | 211681724 | 04/02/2025 | 20 | GP3.8601.../2421269 | Starting/Stopping Issue | Task Start | SHITAL HOSPITAL | Paluck Technologies Ltd. - Faridabad |  | Battery stolen, So, new battery buy to market | Closed | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
8 | East | 211698133 | 09/02/2025 | 20 | GP3.8601.../2421651 | Automation Issue Call By Customer Name :-Dhval patel Mobile No :-9031030322 | Open | Girish chanachur &snacks pvt. ltd | HACS Engineering and Tech Private Limited - Jamshedpur | 7 | SR cancelled -Tele discussion -Visit not req | CANCELLED | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
23 | North | 211695304 | 08/02/2025 | 62.5 | T4.8941.../2420119 | Starting Issue & Diesel Leakage Issue Call By Customer Name :-Deepak Mobile No :-7015196453 | Task Start | Jain Garments | SAAN Royal Power Solutions Private Limited - Hisar |  | Under Cancellation-same rectified on call | Cancelled | Ved Prakash Gupta | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
9 | East | 211679333 | 03/02/2025 | 40 | 3H.8951.../2420560 | KRM App Issue Call By Customer Name :- Shankar Kumar Mobile No :- 9835666455 | Task Start | Usha Singh | Globalline India Services Private Limited - Patna | 143 | No issue was in DG customer complaint was that KRM is not operating so visited site found KRM was ok but by mistake customer uninstall the KOEL Igreen app and was not able to install and login so SE done all this but the customer was not satisfied as on starting DG it shows after few minutes that DG is in running | OPEN | Prabhakar Kumar | [9 empty] | KRM | 6 | 5 | 4 | 120 | Moderate
12 | East | 211707501 | 11/02/2025 | 40 | 3H.8951.../2421571 | Automation issue Called by customer Name : EC FARM Number : 8327779009 | Cancelled | M/s. Shyam Power Solution. | Gangpur Sales and Services - Bhubaneswar | 14 | SR will be cancelled, by telephonic discussion issue was resolved, Customer side over load issue | CANCELLED | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
16 | South | 211750330 | 24/02/2025 | 20 | GP3.8601.../2420622 | Starting Problem Call by : Customer Name :Basha Contact : 9059052038 | Task Start | Navya Enterprises | Ultimate Power Source - Kadappa | 40 | Battery dischared | Task Start | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
31 | North | 211748778 | 23/02/2025 | 58.5 | T4.8941.../2423259 | Coolant Leakage Issue. Call By Customer. name:-Hemsingh Rajpurohit Mobile No.:-9799985291 | Closed | Ponom Tent house | Rajdhani Diesels and Electricals - Jodhpur | 86 | Coolant leakage from radiator hose clamp was loose tightess the same after that issue resolve | Closed | Gourav Sharma | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
2 | South | 211711895 | 13/02/2025 | 200 | 6H.8435.../2420134 | AMF Panel Problem Call by : Customer Name :ShivKumar Contact :9901443626 | Task Start | Nirmithi Kendra | Surya Power Services - Kalyan Nagar | 250 | As per the customer complaint check the engine running condition. Problem found in 3364/10 DEF TANK. SO remove the def level sensor and reconnect properly. Using the I ikonnect tool to clear the DTC alarm. | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
14 | South | 211750515 | 24/02/2025 | 125.4 | 4H.8041.../2420809 | Starting Problem Call by : Customer Name : Srinivas Contact : 9640416879 | Closed | Saksham InfraSolution Pvt. Ltd. | Powerlinks Infra Tech Pvt Ltd - Uppal | 141 | Attended site inspected dg set found battery discharged due to battery charger connections not given so retighten found ok | Closed | Mr. MD Saleem | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
32 | North | 211748701 | 23/02/2025 | 25 | GP3.8702.../2421228 | Maintenance due alarm issue Call By Customer Name :Pankaj . No :9810637769 | Open | V6 WAREHOUSING LLP | Vidyut Engineers - Noida |  | Cancelled | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
33 | North | 211748292 | 22/02/2025 | 125.4 | 4H.8042.C4../2420132 | Miantanance due alarm issue Called by customer Name : Iliyas Number : 8290497792 | Open | DESERT VALLEY RESORT | Rajdhani Diesels and Electricals - Jodhpur |  | Cancelled-Problem solve in PM visit | Cancelled | Gourav Sharma | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
26 | North | 211745197 | 22/02/2025 | 30 | 3H.8902.../2420414 | VOC -Starting/Stopping Issue Customer Name -Vikky Panchal Customer Number -9548694250 Mode- SR Generated through CDI calling. | Open | Tanu Engineering Products Private Limited.** | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Cancelled | Cancelled | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
3 | West | 211753567 | 25/02/2025 | 625 | DV0.8501.C4../2420032 | Inspection/Maintenance | Task Start | Transworld Logistics Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Baroda | 24.5 | Visited on site and Removed the water pump pully belt & cleaned the pully. Fitted the existing old belt and checked the belt tension in four readings- 40,43,40,43HZ. Removed the fan pully belt & interchange the radiator side belt(Already loose) in place of nearest belt, checked the tension and found from radiator side- 90,54,85HZ. So replaced the all three belt of fan pully. | Closed | Amit Sandlya | [9 empty] | Water Pump | 7 | 6 | 4 | 168 | Moderate
13 | South | 211750603 | 24/02/2025 | 30 | 3H.8902.../2421107 | Under speed problem Call by : Customer Name : K. Anjineyulu Contact : 8919032320 | Closed | Amrutha Varshini. | Ultimate Power Source - Ananthapuramu | 23 | Air Lock issue, due to low fuel level | Closed | Mr. NandhaGopal | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
12 | North | 211684333 | 05/02/2025 | 58.5 | T4.8941.../2421963 | Coalent Leakage Issue Call By Customer Name :- 8650181984 Number:- 8650181984 | Task Start | SHYAM ORTHOPAEDIC AND TRUMA CENTRE | R K Engineers - Saharanpur | 27 | Coolant leakage from radiator hose clamp so, tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
48 | South | 211655833 | 29/01/2025 | 200 | 6H.8435.../2420070 | Leakage Issue | Closed | Ripple Developers Pvt. Ltd. | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 14 | Attend the site check the engine coolant leakage problem observed the radiator hoses pipe to leakage fitting the house clamp found ok check the engine oil level and coolant level found ok check the battery daistal water ok started the dg working ok | Closed | Mr. MD Saleem | ikonnect log | [8 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
8 | West | 211630814 | 22/01/2025 | 5.5 | CC1.1013.../2400406 | Starting/Stopping Issue | Closed | AMRUT SHRY CONTAINER COMPANY | Unique Techno Services Pvt Ltd. - Gandhidham | 477 | Canopy damage by accident , canopy changed by chargeable basis. | Closed | Amit shandilya | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
6 | South | 211711245 | 12/02/2025 | 125.4 | 4H.8042.C4../2420366 | Shutdown alaram | Open | AMP Rose Private Limited | Surya Power Services - Kalyan Nagar | 167.43 | As per the customer complaint came and visit the site and checked the all wiring connection and condition . Problem found in temp switch. code 3532/16 So connect the Ikonnect tool and clear the DTC alarm | Closed | Mr. Anil Kumar H G | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
5 | East | 211685330 | 05/02/2025 | 40 | 3H.8951.../2420197 | Air Lock issue Called by customer Name : Robin Contact no: 7546967718 | Task Start | Maa Annapurna Foods | Globalline India Services Private Limited - Patna | 64 | task cancelled- yesterday se not visited the site | OPEN | Prabhakar Kumar | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
1 | WEST | 211760057 | 26/02/2025 | 20 | GP3.8601.../2420050 | Automation and Current issue Call By Customer Name :- Ganesh Mobile No:-9730580949 | Cancelled | Suzanne Merwanji. | Mahalaxmi Diesels - Goa |  | cancelled | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
49 | South | 211655746 | 29/01/2025 | 25 | GP3.8702.../2422044 | OIL PRESSUE SENDOR FAILURE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Check the engine oil sensor not working. Replaced the New sender work done. | Closed | Mr. NandhaGopal | [9 empty] | Engine Oil | 7 | 5 | 4 | 140 | Moderate
10 | North | 211684691 | 05/02/2025 | 40 | 3H.8951.../2320020 | Starting Issue Call By Customer Name : Anup Bajaj No : 9999786017 | Closed | BR. Containers | Paluck Technologies Ltd. - Faridabad | 674 | Battery voltage low during Cranking Battery voltage near about 8v, start the DG from other battery | open | Kapil Solanki | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
5 | South | 211644627 | 25/01/2025 | 82.5 | 5H.8901.../2420337 | Starting Problem Call by : Dealer Name : chandrashekar Contact : 9959715131 Dealer number : 7013939726 | Task Start | Imax Diagnostics | Ultimate Power Source - Ananthapuramu |  | Battery low voltage issue | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
15 | South | 211682834 | 04/02/2025 | 250 | F6.8841.../2320041 | Alaram issue | Task Start | ST. Marys Hospital | Bharath Diesel Sales and Service - Salem | 116 | 5461/8,520527/16,4365/2 Error code clear the DTC. | Closed | Mr. NandhaGopal | [9 empty] | DTC | 6 | 5 | 4 | 120 | Moderate
4 | North | 211754799 | 25/02/2025 | 100 | 4H.8042.C4../2420743 | Starting/Stopping Issue | Task Start | PRATEEK RESORTS & BUILDERS PRIVATE LIMITED | GLOBALVISION POWER SOLUTIONS PVT LTD - DEHRADUN | 2.2 | Found Battery positive terminal loose so, tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
11 | WEST | 211716720 | 14/02/2025 | 50 | T4.8941.../2423324 | ENGINE NOT STARTING | Task Start | Bharti Airtel Limited | Shree Engineering Service - Satna | LR | Communication error CanH voltage with respect to ground- 2.5V & CanL voltage with ground 2.49V. Checked the continuity and cross continuity, Cross continuity was find between CAN H & CAN L. Panel side CAN line is ok but engine side is not ok. so EDO placed for the same. | Open | Vijay Patil | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | North | 211754710 | 25/02/2025 | 82.5 | 5H.8901.../2420865 | Door look issue Call By Customer Name :- Indrani Sharma Mobile No :-9818231206 | Closed | ST. ALBANS SCHOOL | Paluck Technologies Ltd. - Faridabad | 18 | Canopy door lock adjust | Closed | Kapil Solanki | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
60 | South | 211651751 | 28/01/2025 | 15 | GP3.8501.../2420086 | Starting/Stopping Issue | Closed | T. Savithri | Madhu Engineering Sales & Service -Poonamallee,Chennai | 47 | Visited the site and attend the engine, checked the alarm alarm is under speed, checked the Air lock is nil, checked the battery distilled water and voltage is normally found ok,checked the control panel connections found ok,in fuel pump rack sticky condition, & socket is in loose connection ,then disconnect the connector connect tightly , started the engine in manual mode engine starting and stopping condition is found ok, checked in auto mode gived the load 20 mins engine parameters and running and stopping is found ok. | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
1 | East | 211709081 | 12/02/2025 | 250 | F6.8841.../2420134 | Leakage Issue | Task Start | TNZ CENEMA HALL | Green Powerline - Tezpur | 71 | Lube oil leakage from the oil filter so tighten properly after removing filter again fitted properly issue resolved | OPEN | Ujjwal Das | [9 empty] | Oil Filter | 6 | 5 | 4 | 120 | Moderate
58 | South | 211653222 | 28/01/2025 | 58.5 | T4.8941.../2421400 | Fuel sensor problem Call by : Customer Name : Ranjan Contact : 9632002808 | Task Start | Sri Gavisiddheshwara Samsthan Sri Gavimath | Vijayshree Diesel Sales and Service - Hospet | 55 | Check the fuel sensor not working check the wiring found ok next connect the fuel sensor negative cable and battery negative cable not working fuel sensor filling the diesel and full tank not showing the full sensor | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
57 | South | 211653229 | 28/01/2025 | 160 | 6H.8475.../2420130 | Starting/Stopping Issue | Closed | PARK CONTROLS AND COMMUNICATIONS PRIVATE LIMITED | Surya Power Services - Bangalore | 20.5 | AS PER THE CUSTOMER COMPLAINT VISITED THE SITE AND CHECK THE ENGINE SIDE COOLANT LEAKAGE FROM RADIATOR COOLANT HOSE CHECK AND TIGHTENED THE CLAMP AND STARTED THE ENGINE RUNNING CONDITION WORKING FOUND OK | Closed | Mr. Anil Kumar H G | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
20 | South | 211750109 | 24/02/2025 | 25 | GP3.8702.../2421253 | Starting/Stopping Issue | Closed | Axis Bank Ltd | Surya Power Services - Kalyan Nagar | 8.57 | As per the customer complaint check the engine properly. Problem found in battery. Battery is fully discharged (2.73V).so remove the battery and handover the battery to customer for recharge the battery.and started the customer standby battery and start the engine running normal | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
54 | South | 211654226 | 28/01/2025 | 58.5 | T4.8941.../2421335 | Starting/Stopping Issue | Closed | Anantha Departmental Stores. | Genearth Services - Marthandam | 66 | visit the site, checked the engine Controller alarm in emergency switch shutdown alarm, control panel emergency switch wiring (ferrule no10), retighten now alarm cleared checked the engine oil level, radiator coolant level, battery electrolyte level, belt tension, battery charging now engine normal running with load check up in auto mode | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
16 | South | 211682787 | 04/02/2025 | 30 | 3H.8902.../2421036 | Starting Issue Call BY Customer Name:-k Perumal No:-8939541036 | Task Start | Sia Carriers LLP... | Bharath Diesel Sales and Service - Chengalpattu | 3 | Visit to the customer site then inspection the engine , sometime not starting the engine due to starter motor wiring problem (3C) loose , after reconnected the wiring harness | Closed | Mr. NandhaGopal | [9 empty] | Starter Motor | 7 | 4 | 5 | 140 | Moderate
16 | North | 211683289 | 04/02/2025 | 15 | GP3.8501.../2420698 | Automation issue Call By Customer Name : Prabhit ... No : 8090631313 | Open | Iqbal Singh | Espiem Engines & Machines (P) Limited - KANPUR |  | Under cancellation- Out of scope work | Cancelled | Sudhir Awasthi | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
8 | WEST | 211763396 | 27/02/2025 | 125.4 | 4H.8041.../2420758 | Coolant Leakage Issue Call by Customer Name :Bahadur Singh Number :6260524337 | Task Start | Jay Gopal Gaushala Borkhera Bhalla | Natraj Power Tech - Ujjain | 79 | Coolant leakage from radiator to dosing module coolant pipe Sd engineer on site with pipe. The SD engineer got the coolant pipe repaired from the market. | Open | Vijay Patil | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
17 | South | 211750209 | 24/02/2025 | 25 | GP3.8702.../2420693 | Automation and Maintenance Due Alarm issue Call By Customer Name :- Shijo Mobile No:-9986782800 | Task Start | Lenexis Food Works | Surya Power Services - Bangalore | Cancelled | Cancelled | Cancelled | Mr. Anil Kumar H G | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
16 | North | 211753959 | 25/02/2025 | 58.5 | T4.8941.../2422917 | Starting Issue Call By Customer Name :-Aslam Ali . Mobile No :-9284049835 | Closed | K. K. International Safety C/o. | Paluck Technologies Ltd. - Faridabad | 35 | Found Battery voltage 11v so, check the Battery charger found Battery charger output wire was removed same coonect the wire after battery charging then issue resolve | Closed | Kapil Solanki | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
11 | East | 211707790 | 11/02/2025 | 40 | 3H.8951.../2520007 | Starting issue Called by customer Name : SUBRAT KUMAR Number : 9090008823 | Cancelled | SUBRAT KUMAR NAYAK | Gangpur Sales and Services - Jajpur | 23 | SR will cancelled- as on telephonic communication issue resolve emergency switch was pressed. | CANCELLED | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
4 | South | 211644844 | 25/01/2025 | 160 | 6H.8475.../2420277 | Electrical Problems | Task Start | BAR Readymix Concrete | Ultimate Power Source - Tirupati | 81 | DEF Tank to supply module inlet & outlet pipe interchanged. | Closed | Mr. NandhaGopal | GOEM issue | [8 empty] | Supply Module | 7 | 5 | 4 | 140 | Moderate
21 | North | 211741458 | 21/02/2025 | 40 | 3H.8951.../2421197 | starting issue Call By Customer Name :-Dhruv Mobile No :-9219633120 | Closed | Axis Bank Ltd | R K Engineers - Meerut | 45 | Found Fuel level sensor negative wire loose in Connector after fitted proper then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Fuel Level Sensor | 7 | 5 | 4 | 140 | Moderate
12 | North | 211706037 | 11/02/2025 | 40 | 3H.8951.../2420797 | Automation and Under Speed Alarm issue Call By Customer Name :- Anuj Mobile No :- 8808477189 | Closed | ANUJ MISHRA | S. R Engines Sales And Service - Gorakhpur | 135 | found in controller auto button not press by customer & Radiator chocked required Cleaning quatation send to customer | Closed | Sudhir Awasthi | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
9 | West | 211750639 | 24/02/2025 | 58.5 | T4.8941.../2421287 | servicing | Cancelled | Supreeme Wood Furniture. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune |  | CANCELLED | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
2 | WEST | 211748879 | 23/02/2025 | 82.5 | 5H.8901.../2420146 | Tripping Issue Call By Customer Name :- Mobile No :-9322397308 | Cancelled | Shree Krishna Homes | Transcreek Engineers Pvt. Ltd. - Ambernath |  | Cancelled | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
51 | North | 211706009 | 11/02/2025 | 125.4 | 4H.8042.C4../2420289 | Starting/Stopping Issue | Closed | VARDHMAN X-RAY & ULTRASOUND CENTRE | SAAN Royal Power Solutions Private Limited - Sonipat | 2.32 | Starting issue due to Battery Voltage found low,DG was in offcondition since last month &battery Charger was disconnected by customer from mains supply,connected the same & same communicated to customer | Closed | Ved Prakash Gupta | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
17 | West | 211746662 | 22/02/2025 | 125.4 | 4H.8041.../2420945 | Uria level issue Called by customer Name : Prakash Number : 9892799739 | Cancelled | QbD Research & Development Lab Pvt. Ltd. | Transcreek Engineers Pvt. Ltd. - Thane |  | Cancelled | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
14 | South | 211683168 | 04/02/2025 | 160 | 6H.8475.../2420282 | Adblue low level & Alarm Problem Call by : Customer Name :Muniyan Contact :8681944593 | Open | RANGA NEURO MULTISPECIALITY | Bharath Diesel Sales and Service - Dharmapuri | Cancelled | Cancelled | Cancelled | Mr. NandhaGopal | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
5 | North | 211685309 | 05/02/2025 | 200 | 6H.8435.../2420245 | Exhaust Fan Issue Call By Customer Name - Ashraf Number - 7607466413 | Completed | St.Thomas School | Espiem Engines & Machines (P) Limited - KANPUR | 23 | Found v belt was loose tightness the same, but Radiator fan was not proper working | open | Sudhir Awasthi | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
14 | South | 211709719 | 12/02/2025 | 58.5 | T4.8941.../2422426 | Starting Problem Call by : customer Name : Yadav Contact :7093085532 | Closed | perol yadav | Ultimate Power Source - Tirupati | 32 | checked the battery low distill water. | Closed | Mr. NandhaGopal | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
11 | East | 211681458 | 04/02/2025 | 30 | 3H.8902.../2420583 | Leakage Issue | Task Start | Shine Enterprise | Green Powerline - Dhemaji | 243 | Radiator found damage due to foregin particle strikes to the radiator so coolant leakage start, it is covered under post warranty because its and customer end mistake. | CLOSED | Ujjwal Das | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
13 | West | 211751727 | 24/02/2025 | 15 | GP3.8501.../2421965 | RADIATOR CAP DAMAGED | Task Start | Shoaib Mehboob | Mahalaxmi Diesels - Goa | LR | RadiaTor cap found damage, so need to change the cap | Closed | Jagdeep Saini | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
6 | West Zone | 211705127 | 11/02/2025 | 625 | DV0.8501.C4../2420058 | Inspection/Maintenance | Task Start | Transworld Logistics Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Baroda | 15.7 | The radiator fan belt was found to be damaged so it needs to be replaced. | OPEN | Amit Shandilya | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
12 | West | 211754361 | 25/02/2025 | 58.5 | T4.8941.../2421353 | Starting/Stopping Issue | Task Start | Krishna Mega Projects LLP. | KALA Care Global LLP - Aurangabad | 35 | Air lock in fuel system | Closed | Jagdeep Saini | [9 empty] | Air Lock | 6 | 5 | 4 | 120 | Moderate
10 | South | 211710035 | 12/02/2025 | 58.5 | T4.8941.../2423158 | Starting Problem Call by : Customer Name :Sundar Contact :9952578534 | Task Start | Supreme Traders | Madhu Engineering Sales & Service - TIRUVALLUR | 7 | Inspected the generator for engine not Start complaint battery voltage down due to battery charger not working charger Power supply disconnected to battery charger so battery not able to charge now connected the wire battery charging working normal Battery charger connected to battery should teken 8 hours for fully charging | Closed | Mr. NandhaGopal | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
5 | West Zone | 211706581 | 11/02/2025 | 625 | DV0.8501.C4../2420032 | V Belt issue Call By Service Dealer Name :- Manoj Mobile No :- 9879616348 | Task Start | Transworld Logistics Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Baroda | 21 | The radiator fan belt was found to be damaged so it needs to be replaced. | OPEN | Amit Shandilya | [9 empty] | Radiator | 7 | 5 | 4 | 140 | Moderate
9 | South | 211710290 | 12/02/2025 | 15 | GP3.8501.../2420138 | Automatically switching off AND Abnormal Sound Call by : Customer Name :Ananda Contact :9591384060 | Closed | K. G. Venkatesh Naik. | Prasad Power Engineers - Davangere | 98 | Visit the site check the engine all system the battery distilled water is low level. engine not starting then add the distilled water ok wait 30mint ok then start the engine running condition ok all perimeter working condition | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
8 | South | 211710866 | 12/02/2025 | 15 | GP3.8501.../2420882 | Automation Issue Email by KGD Name - GURUMURTHY | Task Start | SRI KRISHNA BRAHAMANA SEVA MANDALI | Prasad Power Engineers - Tumkur | 11 | After visited the site observed thet there is a battery got fully discharged so suggested tha customer battery needs to be recharge immediately | Closed | Mr. Anil Kumar H G | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
49 | North | 211762900 | 27/02/2025 | 58.5 | T4.8941.../2421792 | Automation & Display Issue Call By Customer Name :-Bittu . Mobile No 8619101790 | Closed | NIKHIL BUILDCON PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - BIKANER | 50 | Battery voltage low, charger connection not done, Service due | Closed | Gourav Sharma | [9 empty] | Battery | 8 | 6 | 4 | 192 | Moderate
10 | West | 211744316 | 21/02/2025 | 625 | DV0.8501.C4../2420043 | BNS PORT Call by : Customer Name : Hariprasad Contact : 9158977737 | Cancelled | Mind Space Shelters LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune |  | CANCELLED | Closed | Jagdeep Saini | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
11 | South | 211750682 | 24/02/2025 | 15 | GP3.8501.../2420769 | Starting/Stopping Issue | Closed | The Karur Vysya Bank Limited. | Laxmi Diesels - Visakhapatnam | 13 | Visited the site check the generator battery was discharged connected the battery charger and after 3 hours started the generator running condition are ok | Closed | Mr. MD Saleem | [9 empty] | Battery Charger | 7 | 5 | 4 | 140 | Moderate
15 | South | 211709624 | 12/02/2025 | 125.4 | 4H.8042.C4../2420294 | SENSSOR FITTING | Task Start | Suresh Hangal | Vijayshree Diesel Sales and Service - Hospet | LR | attend the site checked the all DG condition found ok the temperature sensor missing so fitted the new sensor and removed the alarm and checked the all DG condition found ok taken trial dg is good working | Closed | Mr. Anil Kumar H G | GOEM issue | [8 empty] | Temperature Sensor | 7 | 5 | 4 | 140 | Moderate
14 | East | 211665836 | 31/01/2025 | 15 | GP3.8501.../2420312 | Starting Issue Call By Customer Name :- Kumar Lokesh Mobile No :- 8770308831 | Open | Department Of Military Affairs Manipur | M/S JHA EQUIPMENT - IMPHAL |  | SR will be cancelled, no issue in DG | CANCELLED | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
15 | East | 211646328 | 26/01/2025 | 15 | GP3.8501.../2420615 | Load Issue Call By Customer Name ;- Bittu Soni Mob No ;- 8794016784 | cancelled | M/S Marcofed Heningkunhlwa | Hibreed Engineering Pvt. Ltd. - Jorhat | 148 | SR cancelled as no telephonic communication | CANCELLED | Ujjwal Das | [9 empty] | CAN | 7 | 5 | 4 | 140 | Moderate
14 | East | 211683967 | 05/02/2025 | 20 | GP3.8601.../2420881 | Diesel Leakage Issue Call By Customer Name - MD SUMNA Mobile No - 9830286277 | Closed | MD SUMNA | Revenus Industries Pvt. Ltd. - Howrah | 4 | SE found fuel was leakaging from fuel tank due to overflow for unbalancing of DG set. So, open the fuel level sensor & then refitted it properly & educated the customer to keep the DG in proper balance to avoid such issues. | CLOSED | Prosanjit saha | [9 empty] | Fuel Tank | 8 | 5 | 4 | 160 | Moderate
3 | South | 211761081 | 27/02/2025 | 125.4 | 4H.8041.../2420337 | Starting Problem Call by : Customer Name :Pydinaidu Contact :8096351584 | Open | AMR. India Limited. | Ultimate Power Source - Ananthapuramu |  | Visit Pendig | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | South | 211761260 | 27/02/2025 | 125.4 | 4H.8041.../2421020 | oil Leakage Problem Call by : Customer Name :Manikandan Contact :9952356079 | Task Start | Kothanya Construction. . | Bharath Diesel Sales and Service - Arni | 290 | Oil Sump drain bolt side leakage | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | South | 211761183 | 27/02/2025 | 250 | F6.8841.../2420414 | Starting Issue Call By Customer Name:-Mohammad Anas No:-9738472322 | Task Start | KIDS CLINIC INDIA LIMITED | Surya Power Services - Peenya, Bangalore | 161 | 97/5 Error code, coming 2-3 times so interchange the sensor from the other dg. | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | South | 211761265 | 27/02/2025 | 30 | 3H.8902.../2420998 | Lock Compliant | Task Start | P. Naryanan | G-Care +J2731:J2747Diesels Private Limited - Calicut | 204 | Check the engine panel door lock faulty , found lock clamp Bolt loose tighten the bolt issue resolve,then started the engine running ok. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
46 | North | 211673234 | 01/02/2025 | 125.4 | 4H.8041.../2420677 | KG740 C replacement | Task Start | Ek Noor Neki Da Hospital | Industrial Power Solutions - LUDHIANA |  | Visit Pending | open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | East | 211731631 | 18/02/2025 | 10 | GP3.8301.../2420056 | Starting issue and fuel pump leakage issue Call By Customer Name :- Saurabh Rai Mobile No :- 7008755713 | Closed | Sainik Mining and Allied Services Ltd. | Gangpur Sales and Services - Jharsuguda | 1650 | No leakage Issue in DG ,Engine running condition was normal Customer required Service | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211746366 | 22/02/2025 | 82.5 | 5H.8901.../2420270 | Starting/Stopping Issue | Open | BLUESAIL FASHION PRIVATE LIMITED | S. R Engines Sales And Service - Gorakhpur |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211740258 | 20/02/2025 | 200 | 6H.8435.../2420012 | Starting Problem Call by : Customer Name :Subham pall Contact :8878625521 | Open | INOX. Air Products Private Limited | Paluck Technologies Ltd. - Ghaziabad |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211739829 | 20/02/2025 | 20 | GP3.8604.../2420177 | Under Voltage trip Issue | Task Start | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Mau | 560 | Under voltage alarm reset | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211739565 | 20/02/2025 | 25 | GP3.8702.../2421654 | Starting Issue Call By COSTOMER-Ram Baran Pal Name :-9354343817 Mobile No :-9354343817 | Open | Mohit Generator Power Solution | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211747666 | 22/02/2025 | 400 | DV8.8542.C4../2420140 | Electrical Problems | Task Start | Apollo Hospitals (Indraprastha Medical Corporation Ltd.) | Vidyut Engineers - Noida | 19 | Idle running time 160sec. set 30sec. Cool down time 180 sec. | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211758229 | 26/02/2025 | 58.5 | T4.8941.../2420922 | Charging problem And loading issue Call By Customer Name :- Mahesh Chand Mobile No :- 9816035098 | Task Start | MILLENIUM EMBROIDERY | Vidyut Engineers - Noida | 120 | WRONG REPORTING BY CUSTOMER CUSTOMER EDUCATED | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211762222 | 27/02/2025 | 40 | 3H.8951.../2420397 | Starting/Stopping Issue | Task Start | Executive Officerr. | Revenus Industries Pvt. Ltd. - Malda | 7.5 | SE check the engine found fuel Lekage from fuel filter banjo washer damage change the Banjo Washer problem solved so engine running found ok | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211759047 | 26/02/2025 | 250 | F6.8841.../2420263 | Electrical Problems | Task Start | Jai Prakash Associates Ltd. | K.C. Diesel Services - East Sikkim |  | Update Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211739101 | 20/02/2025 | 20 | GP3.8601.../2421061 | Starting issue Called by customer Name : ANAND SHANKAR Number : 9830952272 | Task Start | Anand Shankar Mall. | Pratap Diesels Pvt. Ltd. - BIKANER |  | Visit pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | East | 211731720 | 18/02/2025 | 10 | GP3.8301.../2420058 | Oil leakage issue Call By Customer Name :- Saurabh Rai Mobile No :-7008755713 | Closed | SAINIK MINING AND ALLIED SERVICES LIMITED | Gangpur Sales and Services - Jharsuguda | 1660 | No leakage Issue in DG ,Engine running condition was normal Customer required Service | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211758429 | 26/02/2025 | 320 | F6.8802.../2320028 | COOLANT CONSUPTION Call By Customer Name :. SOURABH. Mobile No :9690706146 | Open | Arocon rainbow | Paluck Technologies Ltd. - Ghaziabad | 451 | WRONG REPORTING BY CUSTOMER CUSTOMER EDUCATED | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | South | 211759032 | 26/02/2025 | 125.4 | 4H.8041.../2420814 | Dg Auto stoping issue | Closed | KALYAN JEWELLERS INDIA LTD | Surya Power Services - J C Road, Bangalore | 140 | Check the engine control unit alaram showing mains phase reversed. Reconnect the phase properly and now working | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | East | 211731728 | 18/02/2025 | 10 | GP3.8301.../2420063 | Oil leakage issue Call By Customer Name :- Saurabh Rai Mobile No :-7008755713 | Closed | SAINIK MINING AND ALLIED SERVICES LIMITED | Gangpur Sales and Services - Jharsuguda | 1650 | No leakage Issue in DG ,Engine running condition was normal Customer required Service | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | North | 211746683 | 22/02/2025 | 160 | 6H.8475.../2420174 | Genset Trip | Open | STRIKER&BROTHERS | SAAN Royal Power Solutions Private Limited - Baddi | 1014 | Engine starting issue due to llop sensor wire found loose & fuse found burnt so tightened & replaced respectively & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | South | 211759065 | 26/02/2025 | 25 | GP3.8702.../2421634 | VOC -Automation Issue Customer Name -Senthil Kumar Customer Number -7025086344 Mode- SR Generated through CDI calling. | Open | Senthil | Electro Controls - Kattappana |  | Visit Pendig | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211735078 | 19/02/2025 | 320 | F6.8802.../2420117 | Starting Issue Call By Customer Name :- Rohit Sir Mobile No :-7338272338 | Task Start | TRENT LIMITED (ZUDIO) | Gangpur Sales and Services - Bargarh | 41 | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
30 | North | 211745786 | 22/02/2025 | 125.4 | 4H.8041.../2320034 | Starting/Stopping Issue | Task Start | Abhitex International | SAAN Royal Power Solutions Private Limited - Panipat | 321 | error code show 3031/14 then code cleaning and flashing DG starting ok and working okay | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211764500 | 27/02/2025 | 58.5 | T4.8941.../2422910 | Control panel Issue Call By Customer Name :- Sheetal Gupta Mobile No :- 6299024030 | Open | HARE RAM HARE KRISHNA ENTERPRISES | HACS Engineering and Tech Private Limited - Hazaribagh | 42 | Visit Pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211734512 | 19/02/2025 | 82.5 | 5H.8901.../2420242 | Starting Issue Call By Customer Name - Subhashish Number - 7029800243 | Task Start | Godrej Properties Pvt. Ltd. | Revenus Industries Pvt. Ltd. - South Kolkata | 2 | No Issue in DG Customer required Service | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | South | 211758887 | 26/02/2025 | 20 | GP3.8601.../2421692 | Starting Problem Call by : Customer Name :Shijesh Contact :9526023109 | Closed | M/s. PARASSINI BAKERS | Surya Power Services - Kolar | 54 | C1(10) wire of relay found loose so tighten the same | Closed | Mr. Anil Kumar H G | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
11 | South | 211759990 | 26/02/2025 | 40 | 3H.8951.../2320035 | Under speed alarm issue Called by custtomer Name : Karuna Number : 9385753704 | Task Start | Karuna Educational Trust | Bharath Diesel Sales and Service - Chengalpattu | 65 | Last oil service done at one year before there is no first oil service so controller panel showing Maintenance due alarm (due at Nov 2024)check the oil level and coolant level found ok.belt condition check found ok.battery distilled water Is very low and we informed to customer and educated .engine mounting bolt tightness checked found ok.air filter cleaning done all sensor connector tightness check found ok.then started the engine running normal sound smoke is normal | Closed | Mr. NandhaGopal | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
18 | South | 211758852 | 26/02/2025 | 25 | GP3.8702.../2420800 | Starting/Stopping Issue | Task Start | South Canara District Central Co Operative Bank Ltd. | Prasad Power Engineers - Puttur | 43 | 653/5 error code, connector remove & then reconnected issue resolve | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211760060 | 26/02/2025 | 125.4 | 4H.8042.C4../2420168 | Display Showing "Maintenance Due"Problem Call by : Customer Name :Sunil Contact :8848377561 | Open | VEDASUDHA AYURVEDIC HOSPITAL VAYALA | Electro Controls - Kottayam |  | Visit Pendig | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | South | 211758811 | 26/02/2025 | 82.5 | 5H.8901.../2420674 | Oil Service | Completed | FNF Motor sports | Powerlinks Infra Tech Pvt Ltd - Madinaguda | LR | Oil Service | completed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211758533 | 26/02/2025 | 30 | 3H.8902.../2421225 | Cranking Issue and starting Issue. Call by Customer. name:-Bushpreet singh Mobile No.:-8076271828 | Open | DIVYANSHI POWER SOLUTION. | Paluck Technologies Ltd. - Ghaziabad | 102 | Found relay card output sensing wire is loose from the Relay card 12RB1-RL2 so, tightness the same after that issue resolve | Closed | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
25 | South | 211661493 | 30/01/2025 | 125.4 | 4H.8042.C4../2420583 | Oil Leakage | Task Start | GOWRI HALL MARK | Powerlinks Infra Tech Pvt Ltd - Madinaguda | LR | As per the customer complaint to attend the site and Checked the problem is drain bolt oil leakage so removed drain bolt and cleaned and adjusted the washiner and started the dg set in manual mode running condition is ok . Photo | Closed | Mr. MD Saleem | GOEM issue | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211646029 | 26/01/2025 | 30 | 3H.8902.../2420005 | Starting Problem Call by : Customer Name : Sunil kumar Contact : 9492463069 | Closed | HOSANNA MANDIR | Ultimate Power Source - Kurnool | 20 | Airlock issue due to low diesel in tank(15%) | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211760090 | 26/02/2025 | 20 | GP3.8601.../2420590 | Starting Problem Call by : Customer Name : Malar Contact :8675777797 | Task Start | Muthu Fuels | Electro Controls - Erode | 37 | Fip rack stuck so free the rack now running ok | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
34 | North | 211744399 | 21/02/2025 | 400 | DV8.8542.C4../2420007 | Excessive Smoke | Open | Fetch Construction | Suraj Motor Store - Srinagar |  | Engine was replaced earlier (3 Month ago),SR Opened for transport claim charges | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | South | 211646743 | 27/01/2025 | 30 | 3H.8902.../2421299 | Starting Issue & Current Supply Issue Call By Customer Name :- Sidha Murti Naidu Mobile No :- 7729082793 | Open | K. Subramaniyam Naidu | Surya Power Services - Bangalore | 20 | As per the customer complaint visit the site dg not starting.check the dg and observe the problem.check the event log in kg645 emergency stop issue.check the emergency stop push found ok.check the wire connector loose.tighted the wire connector ok.then tighter to cable tye in wire connector found ok.started the dg check running time found ok.c | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
35 | North | 211742890 | 21/02/2025 | 500 | DV8.8501.C4../2420339 | Starting/Stopping Issue | Closed | MUBARAKPUR FARMING COMPANY | SAAN Royal Power Solutions Private Limited - Zirakpur | 116 | Starting issue due to Fuel level found low on site , Top-up the same & educate customer to keep fuel minimum 30% | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211731904 | 18/02/2025 | 25 | GP3.8702.../2421722 | Genset Trip | Closed | SUPERITENDENT OF POLICE KORAPUT | Gangpur Sales and Services - BHUBANESWAR | 12 | Customer Pressed the emergency switch after that SE released the switch but not resolved so check the all wiring connection are tightening the same,Issue resolved | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | South | 211760620 | 26/02/2025 | 200 | 6H.8435.../2420096 | Sound/Vibration Issue | Task Start | Bojjaiah Convention | Ultimate Power Source - Ananthapuramu | 52.42 | Found V-belt loose so tighten the same. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | South | 211661546 | 30/01/2025 | 20 | GP3.8601.../2420035 | Leakage Issue | Task Start | G. Sasikumari & Y. Padmaja | Laxmi Diesels - Visakhapatnam | 1.6 | Checked the DG observed diesel pipes Diesel filter Nozzle pipes checked due to observed Suction pipe Thread loose contact tight fitted DG running problem rectified | Closed | Mr. MD Saleem | GOEM issue | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | South | 211661428 | 30/01/2025 | 20 | GP3.8601.../2420537 | Leakage Issue | Task Start | Tasneemunissa And Others | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 29 | Diesel filter leakage. Will replace the filter | Task Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | North | 211673575 | 01/02/2025 | 58.5 | T4.8941.../2420812 | Starting/Stopping Issue | Closed | Hemkunt Petrol Pump | Gen Powers - PATIALA | 180.4 | Oil Leakage found from turbo drain pipe (Update Pending) | open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211762409 | 27/02/2025 | 7.5 | D3.8305.../2400098 | Genset Trip | Task Start | FOREST RANGE OFFICER - BHUBANESWAR | Gangpur Sales and Services - BHUBANESWAR |  | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211730608 | 18/02/2025 | 5.5 | CC1.1013.../2400171 | Starting Issue Call By KGD Name :- Sanjeev Mobile No:-9308664303 | Open | Mahadev Advertiser | Globalline India Services Private Limited - Bhagalpur |  | The DG is install on vehicle and at present it is in Jharkhand so need to transfer Asset | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211742320 | 21/02/2025 | 62.5 | T4.8941.../2320161 | Starting/Stopping Issue | Closed | Chowdhary Hospital | SAAN Royal Power Solutions Private Limited - Rohtak | 130 | Customer complaint as late cranking but no such issue found in DG , water separator connector seems to be some loose so tightend half circle & run the DG,Start/Stop done many times,no issue found | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211665939 | 31/01/2025 | 160 | 6H.8475.../2420246 | Error code Issue Call By Customer Name :- Mishra .. Mobile No :-6370301613 | Closed | M/S SANJEEB KUMAR DAS | Gangpur Sales and Services - Dhenkanal | 106 | Low Adblue level alarm after clearing by Ikonnect issue resolved and customer using thirdparty adblue so educated customer not to use otherwise if any issue created related ATS then its will be on paid basis | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | WEST | 211761225 | 27/02/2025 | 30 | 3H.8902.../2421657 | Automation issue Call By Customer Name :- Mohanlal Mobile No:-9752259762 | Task Start | NOHAR LAL SAHU | Shree Engineering Service - Bilaspur | 2 | DG auto starting issue. MC contact relay 13RB2 coil connector was came out from its position. So fitted it properly. | Closed | Vijay Patil | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
13 | WEST | 211733557 | 19/02/2025 | 58.5 | T4.8941.../2421158 | Starting issue Call by customer Name - Vinay Chotele No - 9179310723 | Task Start | Axis Bank Ltd | Natraj Power Tech - Bhopal | 1 | DG starting issue due to low fuel level. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | North | 211762087 | 27/02/2025 | 15 | GP3.8501.../2420690 | Under Speed Alarm Issue Call by customer name :Bharat Kumar no :8619796848 | Task Start | Friends Trading Company | Rajdhani Diesels and Electricals - Jodhpur |  | Update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | North | 211761900 | 27/02/2025 | 125.4 | 4H.8041.../2420003 | Starting Issue Call By Customer Name :- Kamaljeet Mobile No :-7837470887 | Task Start | Star Smile Manufacturing Private Limited | Vidyut Engineers - New Delhi |  | Engineer visit today | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | WEST | 211735946 | 19/02/2025 | 500 | DV8.8501.C4../2420142 | Engine abnormal noise issue | Task Start | JAKSON & COMPANY | Unique Techno Services Pvt Ltd. - Vapi | LR | Air leakage from air hose pipe. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211735731 | 19/02/2025 | 250 | F6.8841.../2320038 | Inspection/Maintenance | Closed | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 211 | Campaign activity | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
58 | North | 211758950 | 26/02/2025 | 25 | GP3.8702.../2420158 | Starting/Stopping Issue | Closed | Precision Building Contractor | SAAN Royal Power Solutions Private Limited - Baddi | 162 | Starting Issue due to low fuel level alarm,float found stuck so re-fitted the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | WEST | 211756623 | 25/02/2025 | 15 | GP3.8501.../2421529 | Red Lamp On Alarm Issue & Shut Down Alarm Call By Customer Name :- Deepak Parajapti Mobile No :- 9755773002 | Closed | ASHA FUELS | Natraj Power Tech - Mandsaur | 7.34 | Emergency stop button was pushed from customer side, so reliase the same and educated to the customer. | Closed | vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
30 | North | 211761751 | 27/02/2025 | 40 | 3H.8951.../2421197 | Starting/Stopping Issue | Task Start | Axis Bank Ltd | R K Engineers - Meerut | 47 | Found no issue in DG Customer run the DG both mode no issue found | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211761660 | 27/02/2025 | 62.5 | T4.8941.../2320056 | Genset Trip | Task Start | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 1208 | FOUND DG WATER MIX IN DIESEL SO AFTER THAT CLEAN THE FILTER AND REFITTED BACK FOUND DG RUNNING OK | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211761250 | 27/02/2025 | 160 | 6H.8475.../2420031 | Starting/Stopping Issue | Task Start | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 3148 | Found Maintenance due alarm reset & service due | Closed | Kapil Solanki | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
8 | WEST | 211733391 | 19/02/2025 | 20 | GP3.8601.../2420164 | Leakage Issue | Closed | Aurangabad Carbon Products Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 43 | No issue with dg required 1st oil servicing. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
55 | North | 211760074 | 26/02/2025 | 250 | F6.8841.../2420208 | Sound/Vibration Issue | Closed | Sawaraj Overseas | SAAN Royal Power Solutions Private Limited - Panipat | 117.15 | Abnormal sound found due to Air filter assembly to turbo pipe,mounting bolt at engine found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
35 | North | 211764347 | 27/02/2025 | 20 | GP3.8604.../2420177 | INSTANCE ID:-100742276 SITE ID:- I-UE-BNDH-ENB-9069 CALL BY CUSTOMER// DG ISSUE:- DG CONTACTOR FAULTY NAME:- GRISH BABU NUMBER:- 9696104358 | Open | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Mau |  | Visit pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211643208 | 25/01/2025 | 200 | 6H.8435.../2420137 | Starting/Stopping Issue | Closed | M/s. Kanthi Precisions Pvt. Ltd. | Surya Power Services - Bommasandra, Bangalore | 27 | Engine was not starting due to alarm issue (516166/0) and Tool connect and rest the alarm and engine start running found ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | North | 211736641 | 20/02/2025 | 15 | GP3.8501.../2320024 | Over current alarm issue and Preventive Maintenance Call By Customer Name :- Monoj Kumar Varma Mobile No :-6394828613 | Task Start | Shri Panchmukhi Sewa Trust | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | North | 211737612 | 20/02/2025 | 40 | 3H.8951.../2420483 | AMF Panel not working,not working properly.-512798 | Open | ICICI Bank Limited | Suraj Motor Store - Jammu | 275.68 | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211763449 | 27/02/2025 | 40 | 3H.8951.../2421038 | DG ISSUE | Open | ATC Telecom Infrastructure Private Limited | Excel Diesel Private Limited - Sultanpur |  | Visit pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211642585 | 25/01/2025 | 15 | GP3.8501.../2421417 | Alarm problem Call by : Customer Name :Venkatesh Contact :9791252987 | Open | M/s. Vasan Glass | Genearth Services - Tuticorin |  | Dealer intransition | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | WEST | 211734004 | 19/02/2025 | 40 | 3H.8951.../2420953 | Expansion bellow broken | Closed | ISC Projects Pvt Ltd. | Dicksons Engineering Co.Pvt.Ltd. - Yavatmal | 1435 | Alingment was correct but due to vibratation expansion bellow broken so change the bellow. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | North | 211763364 | 27/02/2025 | 7.5 | D3.8305.../2400081 | Starting/Stopping Issue | Closed | DA. Toll Road Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 149 | Found Fuel rack jammed so, it was rectified by adding oil | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | North | 211737594 | 20/02/2025 | 25 | GP3.8702.../2420264 | Starting/Stopping Issue | Open | Jamuna Agencay | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 166 | Starting issue with Crank rest alarm , -ve supply wire(2B1) on 32 Amp MCB found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | MCB | 5 | 4 | 3 | 60 | Low
44 | North | 211763178 | 27/02/2025 | 125.4 | 4H.8042.C4../2420419 | Automation Issue Call By Customer Name :- Jagdish Prasad Mobile No :- 9810511059 | Closed | JM. Engineers. | OVN Industries Private Limited - New Delhi | 3.25 | Auto Start problem but when Engineer visit the site Check the DG Auto & Manual found no issue | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
52 | North | 211761823 | 27/02/2025 | 40 | 3H.8951.../2421410 | voltage flactuation Issue Call By Customer Name :- Rskesh SHAUNAK N Mobile No :- 9870760486 | Task Start | S NANDEDKAR & ASSOCIATES | SAAN Royal Power Solutions Private Limited - Mandi | 389.7 | AVR Card found faulty ( Update Pending) | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | North | 211763162 | 27/02/2025 | 125.4 | 4H.8042.C4../2420965 | Starting/Stopping Issue | Closed | RBA DENTAL CARE | Paluck Technologies Ltd. - Faridabad | 2.2 | Relay connection loose | Closed | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
51 | North | 211762590 | 27/02/2025 | 58.5 | 6H.9840.../2420007 | Under Speed Alarm and Tripping issue Call By Customer Name :- M. D Afroj Mobile No:-8700479015 | Closed | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 34 | ECU reprogramming & engine fuel valve un load set 19.5 and dg set on load testing 2.30 hours proper running working ok dg set fuel valve on load 68 %. Unbalance load & Overload So, same Educate the customer for balancing the load | Monitoring | Kapil Solanki | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
46 | North | 211763140 | 27/02/2025 | 125.4 | 4H.8041.../2420236 | Starting/Stopping Issue | Closed | Arya Hospital | OVN Industries Private Limited - New Delhi | 21 | Found Emergency switch pressed condition so realeased the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211643180 | 25/01/2025 | 125.4 | 4H.8041.../2420970 | Oil Leakage Issue Call By Customer Name :- Sachin Mobile No :- 7879323284 | Task Start | Malwa Infracon Pvt. Ltd. | Vijayshree Diesel Sales and Service - Hospet | 364 | Flywheel side oil seal replace. Photo | Closed | Mr. Anil Kumar H G | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
29 | North | 211734926 | 19/02/2025 | 82.5 | 5H.8901.../2420334 | Cold Trail DG | Task Start | KIRLOSKAR OIL ENGINES LTD | Suraj Moters Stores - Leh | LR | SR Opened for cold start trail , Testing performed by CRE Team | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
48 | North | 211762958 | 27/02/2025 | 57 | T4.8941.../2320166 | AVR Fluctuation Issue Call By Customer Name :- SUNIL KUMAR Mobile No :-9887387270 | Task Start | CAPRI TRANSFORMERS PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Bhiwadi | 190 | Customer says that Compressor not working on DG but when mains line come Compressor working ok, Today Engineer visit again | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
30 | North | 211734920 | 19/02/2025 | 200 | 6H.8435.../2420011 | Cold Trail DG | Task Start | KIRLOSKAR OIL ENGINES LTD | Suraj Moters Stores - Leh | LR | SR Opened for cold start trail , Testing performed by CRE Team | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | South | 211642069 | 25/01/2025 | 20 | GP3.8601.../2421681 | Error problem Call by : Customer Name : Venkatasubbayya Contact : 9346641629 | Task Start | Bhargavi Engineering | Ultimate Power Source - Nellore | 1500 | visit the dg set ok,check oil filte and level found ok,coolent found ok, hose pipes condition bolts and nuts ok,DMI showing the error codes then we take Laptop and NIRA cable updated SEG software now it working fine checked all parameters fine | Closed | Mr. NandhaGopal | [9 empty] | Error Codes | 5 | 4 | 3 | 60 | Low
15 | North | 211747931 | 22/02/2025 | 20 | GP3.8601.../2420914 | DG PROBLERM | Open | ICICI Bank Limited | Pratap Diesels Pvt. Ltd. - Nagaur |  | Visit pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | WEST | 211733267 | 19/02/2025 | 58.5 | T4.8941.../2423130 | Over Voltage Alarm Issue Call By Customer Name :UJJAVAL PATEL No :8758642224 | Closed | VERTIGO AGRITECH PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Mahesana | 1.34 | Taken trail of the DG, no voltage issue found. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211646328 | 26/01/2025 | 15 | GP3.8501.../2420615 | Load Issue Call By Customer Name ;- Bittu Soni Mob No ;- 8794016784 | Open | M/S Marcofed Heningkunhlwa | Hibreed Engineering Pvt. Ltd. - Jorhat | 148 | Visit pending- no response from the dealer end | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211739019 | 20/02/2025 | 200 | 6H.8435.../2320025 | Radiator Issue Call By Customer Name :-sanjay jain Mobile No :-9772093093 | Closed | M. Safe India | Pratap Diesels Pvt. Ltd. - Bhiwadi | 224 | Fan belt loose tightness the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | North | 211741090 | 21/02/2025 | 160 | 6H.8475.../2420233 | Coolant Leakage Issue Preventive Maintenance Call By Customer Name :- goverdhan Choudhary Mobile No :-9602270032 | Open | Dr .Heera Diagnostic Centre Pvt ltd | Rajdhani Diesels and Electricals - Jodhpur | 13 | Coolent leakage from Thermostat to Radiator hose clamp loose so, tightness the same | Closed | Gourav Sharma | [9 empty] | Thermostat | 5 | 4 | 3 | 60 | Low
13 | North | 211741211 | 21/02/2025 | 125.4 | 4H.8042.C4../2420151 | Electrical Problems | Closed | Gagan Generators. | Vidyut Engineers - New Delhi | 1055 | update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | WEST | 211761816 | 27/02/2025 | 15 | GP3.8501.../2421866 | LVM NOT WORKING | Task Start | Bharti Airtel Limited | Natraj Power Tech - Gwalior | 15 | Customer side issue(Faulty LVM). | Closed | Vijay Patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211738888 | 20/02/2025 | 15 | GP3.8501.../2420835 | starting issue Call By Customer Name :-fatendra pratap sing Mobile No :-9044725003 | Task Start | R & C INFRA ENGINEER'S PVT LTD | S. R Engines Sales And Service - LUCKNOW |  | Engineer visit today | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | South | 211661668 | 30/01/2025 | 58.5 | T4.8941.../2420015 | Oil leakage Issue Call By Customer Name :- Shiva Kumar Mobile No :-9353586956 | Task Start | Consulate General of France in Bangalore | Surya Power Services - Kalyan Nagar | 45.5 | As per the customer complaint check the engine properly. Problem found in diesel suction line benjo washer. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211741318 | 21/02/2025 | 20 | GP3.1021.../2420343 | INSTANCE ID:-100777486 SITE ID:- I-RJ-GRCN-AG1-6001 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- NARSA NUMBER:- 9667016198 | Closed | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - Nagaur | 65 | Under voltage alarm | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | North | 211760617 | 26/02/2025 | 15 | GP3.8501.../2420348 | Starting issue called by customer Name : Deepak Singh Number : 9821071354 | Task Start | Mr. Balwant Singh Brijwal | Deep Jyoti Electricals and Services - Haldwani | 99 | Found 32A MCB Output wire was loose so tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | MCB | 5 | 4 | 3 | 60 | Low
1 | East | 211667228 | 31/01/2025 | 30 | 3H.8902.../2420405 | Auto Starting Issue Call By Customer Name ;- Ataullah ANSARI No :- 9870040345 | Task Start | M/s. Grace Urban Devlopment Corporation. | Globalline India Services Private Limited - Muzaffarpur | 192 | loose wiring connection (as per fsr) update pending at SE end | CLOSED | 211664638 | 31-01-2025 10:55 | 4H.8041.../2420093 | Under Speed Alarm Call By Customer Name - Vishal No - 9730711011 | Closed | Rhenus Contract Logistics India Private Limited | Transcreek Engineers Pvt. Ltd. - Bhiwandi | 153 | SPN: 1761 FMI: 16 ,Low adblue level , top up adblue level. | closed | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211734877 | 19/02/2025 | 320 | F6.8802.../2420038 | Trai DG | Task Start | KIRLOSKAR OIL ENGINES LTD | Suraj Moters Stores - Leh | LR | SR Opened for cold start trail , Testing performed by CRE Team | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211665887 | 31/01/2025 | 35 | 3H.8902.../2420344 | starting issue Email By - OEM Name -Neeraj Mishra | Task Start | Safe Decor | Globalline India Services Private Limited - Patna |  | visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211665836 | 31/01/2025 | 15 | GP3.8501.../2420312 | Starting Issue Call By Customer Name :- Kumar Lokesh Mobile No :- 8770308831 | Open | Department Of Military Affairs Manipur | M/S JHA EQUIPMENT - IMPHAL |  | visit pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211738870 | 20/02/2025 | 58.5 | T4.8941.../2420585 | Load issue Call By Customer Name :- Prem Mobile No :- 9871245671 | Task Start | S. R. S. Auto | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 159 | Customer side panel issue | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | North | 211738470 | 20/02/2025 | 40 | 3H.8951.../2320081 | Excessive Smoke | Under Monitoring | Hindustan Chemical | Pratap Diesels Pvt. Ltd. - Alwar | 526 | found exhaust bellow was broken so, need to be replace | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | WEST | 211665704 | 31/01/2025 | 320 | F6.8802.../2420148 | ECU And Amber lamp on alarm issue Call By Customer Name :- Suhas Mobile No :-9657715792 | Closed | MONGA STRAYFIELD PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 138 | Low adblue level so top up adblue level. | closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211738392 | 20/02/2025 | 20 | GP3.1021.../2420288 | INSATANCE ID:-100777788 SITE ID:-I-UE-TMKH-ENB-G005 CALL BY CUSTOMER:- DG ISSUE :-DG UNDER VOLTAGE ALRAM NAME:-RAJKUMAR NUMBER :- 9771691146 | Open | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | South | 211663212 | 30/01/2025 | 15 | GP3.8501.../2420928 | Automation Issue Call By Customer Name - HARISH V Number - 9980107172 | Task Start | GEETHANJALI HARISH | Surya Power Services - Kalyan Nagar | 13.57 | Auto senscing issue. Senscing cable connected. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | WEST | 211762170 | 27/02/2025 | 58.5 | T4.8941.../2421588 | White Smoke Issue Call By Customer Name :- Mobile No :- | Task Start | Richtech Industries Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Vapi | 359 | Customer complained about white smoke problem. SE visited the site and found that there is no white smoke in DG but light smoke is coming out of brither pipe but there is no problem in DG. | Closed | Amit Sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211737801 | 20/02/2025 | 40 | 3H.8951.../2420081 | Starting/Stopping Issue | Task Start | NEW BHARDWAJ ELECTRICAL WORKS | Paluck Technologies Ltd. - Faridabad | 414 | DG vibrating to be high | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | WEST | 211759829 | 26/02/2025 | 30 | 3H.8902.../2420180 | Starting Problem & lamp Problem Call by : Customer Name :Rajesh Contact :7397336597 | Closed | L & T CONSTRUCTION. | Transcreek Engineers Pvt. Ltd. - Boisar | 405 | 520528/31, 5838/3, 2091/31 error code connect ikonnect and clear error code. | Closed | Jagdeep Saini | Under Observation | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211737657 | 20/02/2025 | 750 | DV2.8501.C4../2420022 | Low coolant issue Call By Customer Name :- Dipak . Mobile No :- 9896391384 | Task Start | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 36 | SR open for Sync. Purpose | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211759460 | 26/02/2025 | 82.5 | 5H.8901.../2320032 | Electrical Problems | Closed | Mayura Textiles | Paluck Technologies Ltd. - Faridabad | 92 | Update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211742709 | 21/02/2025 | 125.4 | 4H.8041.../2320108 | Load & RPM Call By Customer Name :- Vijay Kumar Mobile No :-9829973147 | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 174 | ITV jammed & Under speed alarm | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | North | 211737615 | 20/02/2025 | 750 | DV2.8501.C4../2420113 | Starting Issue Call By Customer Name :- Dipak . Mobile No :- 9896391384 | Task Start | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 9 | SR open for Sync. Purpose | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211742889 | 21/02/2025 | 57 | T4.8941.../2420054 | Red Lamp On Alarm Issue Call By Customer Name :- Vishal Mobile No :- 9319413539 | Task Start | VD. Blue Max Ventilation | Paluck Technologies Ltd. - Faridabad | 399 | maintenance due alarm was comig so, reset the same | Closed | Kapil Solanki | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
23 | North | 211759356 | 26/02/2025 | 58.5 | 6H.9840.../2420007 | Starting Issue. Call By Customer Name :- M. D Afroj Mobile No :-8700479015 | Task Start | Cinturones Alvi (India) Pvt. Ltd. | Vidyut Engineers - Noida | 29 | DG set starting issue problem HT cable problem 6 no plug HT cable 5 no interchange now DG run ok (Under observation) | Monitoring | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | WEST | 211730551 | 18/02/2025 | 58.5 | T4.8941.../2520260 | oil leakage | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Oil leakage from main galary plug,tightened the same. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211737604 | 20/02/2025 | 750 | DV2.8501.C4../2420150 | Starting Issue Call By Customer Name :- Dipak . Mobile No :- 9896391384 | Task Start | Adhikaansh Realtors Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 9 | SR open for Sync. Purpose | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | WEST | 211730557 | 18/02/2025 | 30 | 3H.8902.../2520054 | OIL LEAKAGE | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Oil leakage from main galary plug,tightened the same. | Closed | [10 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | WEST | 211731083 | 18/02/2025 | 20 | GP3.8601.../2520175 | oil leakage | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | Oil leakage from flywheel side. | Closed | [10 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
6 | North | 211742105 | 21/02/2025 | 30 | 3H.8902.../2422441 | DG Not Start, Alarm - Protect Lamp On | Closed | ATC Telecom Infrastructure Private Limited | R K Engineers - Bijnor | 2.6 | check xdbk1 1c2 wire was found loose so retight 1c2 wire and check all connections and retight than started dg working ok. | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211760579 | 26/02/2025 | 125.4 | 4H.8042.C4../2420447 | Starting/Stopping Issue | Task Start | Gaup Automotive Technologies Private Limited. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 53 | Found Auto wire was loose in the panel so, tightness the same after that issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211751566 | 24/02/2025 | 20 | GP3.8601.../2421416 | Under Speed Alarm Call By Customer Name :- Ajit Sir Mobile No :- 8050705848 | Open | MS. Power Systems | Prasad Power Engineers - Hassan |  | Visit pending | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | WEST | 211751450 | 24/02/2025 | 40 | 3H.8951.../2520302 | Line Rejection | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | LR | no issue with dg | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
63 | South | 211745111 | 22/02/2025 | 250 | F6.8842.C4../2420102 | Starting/Stopping Issue | Closed | KIDS CLINIC INDIA LTD | Surya Power Services - Peenya, Bangalore | 110 | Checked water separator filter sensor and drain water and cleand filter and tighten all wiring connection | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211755443 | 25/02/2025 | 250 | F6.8841.../2420347 | Fuel Leakage Issue Email By GOEM Name -Power Generators | Task Start | Rontix Imaging Center & Hospital | Almas Engineers - Dibrugarh | 2.8 | visit pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
65 | South | 211742898 | 21/02/2025 | 20 | GP3.8601.../2421055 | Starting/Stopping Issue | Closed | NX SPORTS LLP | Surya Power Services - Bangalore | 21 | Found Engine Auto not working check the All Electrical connection ok then check the sensing cable voltage ok then remove the sensing cable And re fitting properly ok | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211664984 | 31/01/2025 | 125.4 | 4H.8041.../2420497 | Starting/Stopping Issue | Closed | VEE TEE AUTO MANUFACTURING COMPANY PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Bhiwadi | 260.43 | Maintenance due alarm, increase the date & time & reset the alarm | Closed | Gourav Sharma | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
45 | South | 211656370 | 29/01/2025 | 20 | GP3.8601.../2421250 | Light Blinking Problem Call by : Customer Name : Sampath kumar Contact : 9894782881 | Task Start | MURUGAN AGENCIY | Bharath Diesel Sales and Service - NAMAKKAL | 25.4 | Visit the site Inspected the engine started the engine with load , light flickering problem. Checked power factor,output voltage single phase and theree phase, Balancing load , frequency , and all wiring connection found ok.No issue observed in Engine,we have sent all the observations to kirloskar,they will analyze all the observations and tell you what to do in two days,we will send you an update. | Task Start | Mr. NandhaGopal | [9 empty] | Power Factor | 6 | 4 | 3 | 72 | Low
1 | East | 211753615 | 25/02/2025 | 625 | DV0.8501.C4../2420160 | Error Code Issue Call By Customer Name :- Vijay Kumar Samant Mobile No :-9178858896 | Task Start | RUNGTA SONS PVT LTD. | Gangpur Sales and Services - Keonjhar |  | Update Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
71 | South | 211741931 | 21/02/2025 | 125.4 | 4H.8041.../2420327 | Leakage Issue | Closed | M/s. Abyudhaya Welfare Society | Sri Manjunath Technical Services - Bhimavaram | 257 | Lub oil sump damaged. Welding issue | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | West | 211754251 | 25/02/2025 | 160 | 6H.8475.../2420121 | Starting Issue Call By Customer Name :-Sharath - Mobile No :-9946908909 | Closed | MALABAR GOLD AND DAIMONDS LIMITED-SANGLI | Mahalaxmi Diesels - Sangli | 76 | Adblue level low so top up adblue. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
44 | South | 211656681 | 29/01/2025 | 45 | 3H.8951.../2421507 | Error Code Issue | Open | RMD SUPER MARKET | Madurai Electro Controls - Ramanathapuram |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
72 | South | 211741834 | 21/02/2025 | 10 | GP3.8301.../2420365 | Starting Problem Call by : Customer Name :Sagar Contact :9980723899 | Open | Budans 7 Cafe. | Madhu Engineering Sales & Service - Teynampet,Chennai |  | visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211665755 | 31/01/2025 | 160 | 6H.8475.../2420222 | Fan Belt Issue Email By GOEM Name:-Neeraj Saini | Closed | Yamuna Synthetics Pvt Ltd | Pratap Diesels Pvt. Ltd. - Bhiwadi | 33.4 | Found fan belt loose tightness the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
75 | South | 211741472 | 21/02/2025 | 15 | GP3.8501.../2420656 | Maintenance due alam Call By Service Dealer Name :- Elakhya Mobile No :- 7722070834 | Closed | THE KARUR VYSYA BANK LTD | Bharath Diesel Sales and Service - Chengalpattu | 40 | Red lamp alarm clear the alarm. Updated pending | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | West | 211753967 | 25/02/2025 | 200 | 6H.8435.../2420252 | errror code issue | Task Start | ISC Projects Pvt Ltd. | Mahalaxmi Diesels - Kolhapur | 4.28 | 4225/1 , 516166/0 Connect ikonnect tool and clear error code. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | West | 211726425 | 17/02/2025 | 58.5 | T4.8941.../2422377 | Oil Leakage Issue Call By Customer Name :- Mayur Mobile No :-7385803063 | Closed | Mayur Shrirang Usapker | Mahalaxmi Diesels - Goa | 65 | LLOP sensor found loose so tighten the same. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
78 | South | 211741042 | 21/02/2025 | 20 | GP3.8601.../2421219 | Display problem Call by : Customer Name : Ranjith Contact : 9745583451 | Closed | THE MOUNTAIN TABLE | Electro Controls - Thodupuzha | 29 | Fuse blown replaced with new one | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | West | 211754363 | 25/02/2025 | 82.5 | 5H.8901.../2420221 | Starting/Stopping Issue | Task Start | Infinix Funland LLP. | KALA Care Global LLP - Aurangabad | 397 | no issue with dg | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
81 | South | 211712986 | 13/02/2025 |  | GP3.8501.../2422056 | CC | Open | SREE DURGA CONSTRUCTIONS | Surya Power Services - Kalyan Nagar |  | Oil leakage from head side | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211750604 | 24/02/2025 | 40 | 3H.8951.../2420429 | Coolant Issue Call By Customer Name :- Kishan Mobile No :- 7667676649 | Task Start | Kisan Bauri | HACS Engineering and Tech Private Limited - Dhanbad | 93 | Coolant leakge found at thermostat byepass hose after tightening the clamp issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | Thermostat | 5 | 4 | 3 | 60 | Low
73 | South | 211741779 | 21/02/2025 | 82.5 | 5H.8901.../2420776 | Customer Need Commissioning | Open | Sangam milk producer company limited | Ultimate Power Source - Chittoor |  | visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
47 | South | 211656260 | 29/01/2025 | 25 | GP3.8702.../2420831 | Genset Trip | Closed | M/s. Sri Chaitanya Furniture and Furnishings | Laxmi Diesels - Rajahmundry | 3 | Found DG tripping due to Y phase fuse burnt so replaced the same. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | South | 211656748 | 29/01/2025 | 5.5 | CC1.1013.../2400676 | Starting Issue Call By Customer Name :- POONAM SHEDGE Mobile No :- 7767013675 | Open | Accurate Powertech India Private Limited . | Prasad Power Engineers - Tumkur | 0.1 | No issue in DG. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
60 | South | 211745378 | 22/02/2025 | 250 | F6.8842.C4../2520013 | COOLANT LEAKAGE | Completed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur |  | visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211662306 | 30/01/2025 | 30 | 3H.8902.../2421851 | DG Fail to Start. | Closed | ATC Telecom Infrastructure Private Limited | S. R Engines Sales And Service - Gorakhpur | 48 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | South | 211658596 | 29/01/2025 | 200 | 6H.8435.../2420168 | Display problem Call by : Customer Name : Raja sheker Contact : 9591370686 | Task Start | Ayati Constructions & Estates LLP | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 5.53 | During cranking time (102/4, 51/6) ITV closed so replaced ITV. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211757971 | 26/02/2025 | 20 | GP3.8601.../2420047 | AMF Panel Problem Call by : Customer Name :Papayan Contact :8760022704 | Task Start | Sumathi Sekar | Bharath Diesel Sales and Service - Karappakkam | 77 | Check the EB sensing voltage found 194VAC inform the customer EB side voltage issue | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | South | 211758012 | 26/02/2025 | 20 | GP3.8601.../2421088 | Inspection/Maintenance | Task Start | B. Peera Reddy | Sri Manjunath Technical Services - Narasaraopet | 84 | Low fuel level Alarm. So topup the fuel issue resolved | Task Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211758161 | 26/02/2025 | 15 | GP3.8501.../2421726 | Under Speed Problem& AMF Panel Issues Call by : Customer Name :MR.RAJESH Contact :7358938005 | Task Start | MR.RAJESH SIR | Electro Controls - Marthandam | 68 | Under speed alarm found panel side MR fuse burnt so change the fuse | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211758198 | 26/02/2025 | 30 | 3H.8902.../2420982 | Starting Problem Call by : Dealar Contact :8870478403 Customer name :S.VENKATACHALAM Customer number :8124647906 | Task Start | S.Vengatachalam | Bharath Diesel Sales and Service - Puducherry | 13 | Customer side AMF start relay wire connection problem | Closed | Mr. NandhaGopal | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
48 | South | 211747810 | 22/02/2025 | 40 | 3H.8951.../2420186 | Starting Problem Call by : Customer Name :naveen Contact : 9885410549 | Task Start | Sathya Agency | Ultimate Power Source - Ananthapuramu |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
49 | South | 211747771 | 22/02/2025 | 20 | GP3.8601.../2421720 | Starting Problem & Display " Showing Communication Problem" Call by : Customer Name :Sreekuttan Contact :8281075668 | Closed | PAULOSE GEORGE & CONSTRUCTION COMPANY | Electro Controls - Thiruvananthapuram | 31 | Control panel DC supply fuse loose contactComplaint solved. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211664418 | 31/01/2025 | 40 | 3H.8951.../2420281 | Starting/Stopping Issue | Closed | Vedanta Jyoti Eye Hospital | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 62 | Found self wire loose and sparking so engine not started connected proper self red wire and tight | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
50 | South | 211747644 | 22/02/2025 | 82.5 | 5H.8901.../2420059 | Starting Issue Call By Customer Name :-Ram Chandra Desai Number:- 9481913902 | Completed | Swayamboo Hanumann Petrolpump | KALA Care Global LLP - Belagavi |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
52 | South | 211747542 | 22/02/2025 | 125.4 | 4H.8041.../2420765 | Tripping issue Call By Customer Name:-Yashwant . No:-8792864829 | Open | Prakash Retail Pvt Ltd | Surya Power Services - Mysuru |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
53 | South | 211746347 | 22/02/2025 | 40 | 3H.8951.../2421561 | Starting/Stopping Issue | Task Start | Antioch educational trust | Surya Power Services - Kalyan Nagar | 57 | Engine not starting in auto mode found customer side sencing cable issue. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211758315 | 26/02/2025 | 20 | GP3.8601.../2420131 | Oil Leakage Problem Call by : Customer Name :Raj Kumar Contact :9000993152 | Task Start | Ram Dham Apartment. | Powerlinks Infra Tech Pvt Ltd - Secunderabad |  | Visit pending | Task Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | South | 211758351 | 26/02/2025 | 20 | GP3.8601.../2421730 | Starting/Stopping Issue | Task Start | Ragav | Surya Power Services - Billekahalli | 4 | Customer connected sensing cable but in Auto mode dg not starting so SE found MR fuse blown so replace the new fuse now dg running in auto mode. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
55 | South | 211745958 | 22/02/2025 | 25 | GP3.8702.../2421176 | Starting/Stopping Issue | Closed | Flash Generator Hires | Electro Controls - Palakkad | 380 | Visited the site, checked the oil level , found low level . So checked leakages found normal.checked turbo , oil entry inlet manifold , so suspected turbo failure , is under observation . Topped up 2.5 ltre oil . Started the engine found performance ok | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211662570 | 30/01/2025 | 30 | 3H.8902.../2420788 | Starting Issue Email by KGD Name - Yogendra Sharma | Closed | Jai Bajrang Seva Samiti | Espiem Engines & Machines (P) Limited - Aligarh | 30 | DG trip with under Frequency check & found RG1 wire connector was loose tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
58 | South | 211745730 | 22/02/2025 | 20 | GP3.8601.../2420581 | Red lamp alarm issue Call by : Customer Name : Ramprasad Contact : 9843804575 | Open | S. Meenakshi Sundaram Associates. | Net Work Diesels - Chennai |  | visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
59 | South | 211745560 | 22/02/2025 | 20 | GP3.8601.../2421530 | Starting Problem Call by : Customer Name : K Basavaraj Contact : 9880882360 | Task Start | Basavaraj K | Vijayshree Diesel Sales and Service - Bellary | 5 | dg emergency switch activated , check the emergency switch botton and wiring correction done, | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
51 | South | 211747556 | 22/02/2025 | 82.5 | 5H.8901.../2420161 | Genset Trip | Closed | Mohamed Sharif. A. Ve | Bharath Diesel Sales and Service - Pattanur | 165 | Emergency stop alarm notice. Found wiring loss connect in canpony emergency switch area ferule numbe 1H retigthed all wire started the put on load 20 min load test found ok. | Closed | Mr. NandhaGopal | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
11 | South | 211757927 | 26/02/2025 | 25 | GP3.8702.../2420926 | Starting Issue Call By Customer Name :- Sachin Mobile No :- 7879323284 | Open | Malwa Infracon Pvt. Ltd. | KALA Care Global LLP - Hospet |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211748892 | 23/02/2025 | 20 | GP3.8604.../2420089 | INSTANCE ID:-100740918 SITE ID:- I-BR-DHKA-ENB-9025 DG ISSUE:-DG ALARM ISSUE NAME: DEEPRAJ NUMBER:-9229202768 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Purnia |  | Visit Pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211750262 | 24/02/2025 | 2.8 | AP1.7003.../2400155 | Starting Issue Email by KGD Name - PRADAN | Task Start | PRADAN | Gangpur Sales and Services - BHUBANESWAR |  | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211754965 | 25/02/2025 | 82.5 | 5H.8901.../2320078 | Leakage Issue | Open | Pragya Components Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 730 | Oil Leakage from tappet cover joint, Now tightness the all bolt of tappet cover & under observation | under monitoring | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | West | 211738343 | 20/02/2025 | 125.4 | 4H.8041.../2420898 | Door Lock Issue Call By Customer Name :- Sandip Deshpande Mobile No :- 9822894086 | Closed | DUA CONSTRUCTION | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 194 | door not locked properly , repair the lock. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | South | 211750112 | 24/02/2025 | 58.5 | T4.8941.../2423007 | Autoamtion Issue Email By - KGD Name - Surekha Auti | Closed | Asian Paints Limited | Laxmi Diesels - Rajahmundry | 29 | Found Auto start fuse failure. So replace the new fuse. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | West | 211746105 | 22/02/2025 | 58.5 | T4.8941.../2422819 | ERROR CODE ISSUE. | Completed | Padmavati Genset | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 0.17 | Emergency switch connection male female connector found loose and no cable tie on connector so connection tightened. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | South | 211750203 | 24/02/2025 | 58.5 | T4.8941.../2422978 | AMF Panel Connection. Call By Customer Name :- Basavraj Mobile No :- 9964221928 | Task Start | Rashtrotthana Vidya Kendra | Prasad Power Engineers - Davangere | 24 | Automation Sensing Connection done | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | West | 211736779 | 20/02/2025 | 5.5 | CC1.1013.../2400647 | Voltage Issue Email By - KGD Name - Surekha Auti | Closed | ABHIJEET BABURAO AHIRE | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune |  | Customer side issue | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | West | 211746488 | 22/02/2025 | 82.5 | 5H.8901.../2420332 | Starting Issue Email By KGD Name:-Ranajn Kowale | Closed | HAN GANG INTERNATIONAL HOSPITALITY PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune |  | customer side issue | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | West | 211741403 | 21/02/2025 | 20 | GP3.8601.../2520202 | oil leakage in flywheel side | Closed | Montana Cooperative Housing Society Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 4 | oil leakage from flywheel side change the old oil seal with new one. | Closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
2 | North | 211754876 | 25/02/2025 | 400 | DV8.8542.C4../2420026 | Automation Issue Call By Customer Name :-Amit Kumar Mobile No :- 9540978813 | Task Start | SHREE NURSINGSAHAY MUDUNGOPAL ENGINEERS PVT LTD.. | Vidyut Engineers - Noida | 8.35 | Customer required for Auto | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | West | 211736784 | 20/02/2025 | 25 | GP3.8702.../2520006 | ENGINE NOT START | Task Start | Krishna Auto Links | Mahalaxmi Diesels - Satara | 16 | cheked engine found locked so open the rocker cover & rocker assembly found oil not supply to rocker assembly. Open the rocker arm found rocker arm damage . engine need to be replaced | open | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | West | 211738985 | 20/02/2025 | 0 | T4.8941.../2520161 | alternator disc not fitting into engine flywheel | Closed | JAKSON & COMPANY | Unique Techno Services Pvt Ltd. - Vapi | LR | Found flywheel damage. | Closed | Amit Sandlya | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
64 | South | 211651433 | 28/01/2025 | 82.5 | 5H.8901.../2320001 | Red lamb alarm Call by Customer Name : shefali No :9094379963 | Closed | Starrk Revolution | Madhu Engineering Sales & Service - Teynampet,Chennai | 161 | 1761/16 ADBLUE LEVEL IS LOW SO ADVICE THE CUSTOMER NEEDS TO BE A ADBLUE TOPUP. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | South | 211754175 | 25/02/2025 | 58.5 | T4.8941.../2421560 | Fuel sensor problem Call by : Customer Name : Naveen Contact : 9900070909 | Open | REVAMP POWER | Surya Power Services - Bangalore | 9 | Fuel properly not showing then check the wiring connections.fuel guage connector not properly fitting then connected then check the fuel percentage working found ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | South | 211753579 | 25/02/2025 | 15 | GP3.8501.../2420360 | Door lock problem Call by : Customer Name :Liji Sir Contact :7994333204 | Task Start | Mr. Jayapalan. | G-Care Diesels Private Limited - Thrissur | 18 | Door locks problem rectified. Door lock clamp nut loose condition. Tight the nuts. Problem clear. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | South | 211752583 | 24/02/2025 | 30 | 3H.8902.../2421393 | Starting Problem Call by : Customer Name : Srinivas banguru Contact : 9246286549 | Closed | AGAPE BAPTIST CHURCH | Powerlinks Infra Tech Pvt Ltd - L B Nagar | 2.2 | Emergency alarm. Checked and found wire loose. Corrected | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211752423 | 24/02/2025 | 82.5 | 5H.8901.../2420772 | Display Showing "ECU Error" Problem Call by : Customer Name :Nanas Contact :9895612402 | Task Start | JC S HOLIDAYS | EMKAY MOTORS - Kollam |  | Visit pending | Task Start | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211752302 | 24/02/2025 | 15 | GP3.8501.../2421973 | Genset Trip | Open | YELLUR AND PATIL PETROLEUMS | KALA Care Global LLP - Belagavi |  | Visit pending | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211751987 | 24/02/2025 | 58.5 | T4.8941.../2423122 | error code problem Call by : Customer Name :Ramakirshna Contact : 6301361204 | Closed | R K COLOUR LAB | Ultimate Power Source - Kadappa | 9 | 2791/ 18 Error code | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | South | 211750663 | 24/02/2025 | 160 | 6H.8475.../2420450 | Display Issue Call By Customer Name :- Das Sir Mobile No :- 8906492785 | Task Start | KNC INFRASTRUCTURES | Prasad Power Engineers - Tumkur |  | Visit pending | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211748869 | 23/02/2025 | 30 | 3H.8902.../2422023 | Alarm Issue Call By Customer Name :-Satpal Mobile No :-9549347688 | Task Start | M/S F. DKHAR AUTOMOBILE SPARE PARTS | Hibreed Engineering Pvt. Ltd. - Guwahati |  | Update pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211748955 | 23/02/2025 | 20 | GP3.8601.../2420171 | Coolant Leakage Issue Call By Customer Name :- Pavitra . Mobile No :-9812667969 | Task Start | Smt Sumitra Rani | SAAN Royal Power Solutions Private Limited - Hisar | 96.5 | Coolant leakage found from Radiator hose near water body assembly due to clamp found loose so tightened the same , Air Filter assembly also found loose due to mounting bracket bolt found loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
15 | North | 211749720 | 24/02/2025 | 20 | GP3.8601.../2421115 | Starting/Stopping Issue | Task Start | HILAL BAKERY.. | Suraj Motor Store - Srinagar | 31.18 | Visit Pending | open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | West | 211731599 | 18/02/2025 | 750 | DV2.8501.C4../2420055 | Starting/Stopping Issue | Closed | SHREE GANESH ENGINEERING WORKS UNIT I | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 14 | The report was pending so SR opened. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211748817 | 23/02/2025 | 25 | GP3.8702.../2420184 | Starting Issue Call By Service Dealer Name :- Rik Mobile No :-6294129433 | Closed | Md. Shamshad Alam. | Revenus Industries Pvt. Ltd. - Asansol | 8.23 | DG shutdown due to 516166 (Inductment alram) after that clear the code Issue resolved. | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
29 | North | 211750376 | 24/02/2025 | 125.4 | 4H.8041.../2320116 | Mil lamp issue and code issue | Closed | Vatsalya Hospital | Paluck Technologies Ltd. - Gurgaon | 258 | Engineer visit on site found no any issue in DG | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | North | 211750629 | 24/02/2025 | 125.4 | 4H.8041.../2420641 | Fuel Meter Issue And Urea Leakage Issue Call By Customer Name :- Sudhakar Dubey Mobile No :-8128313601 | Task Start | KALYAN JEWELLERS INDIA LTD | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 79 | Customer raise the Complaint for Urea leakage but found not issue of Urea leakage | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | North | 211745340 | 22/02/2025 | 30 | 3H.8902.../2421175 | Starting/Stopping Issue | Task Start | MAJISA RESTRO | Pratap Diesels Pvt. Ltd. - BIKANER |  | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | North | 211745364 | 22/02/2025 | 25 | GP3.8702.../2421882 | Leakage Issue | Closed | GURUKRIPA TRADERS | Pratap Diesels Pvt. Ltd. - BIKANER | 8.13 | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | North | 211747517 | 22/02/2025 |  | GP3.8702.../2520300 | LINE REJECTION | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR- | Common rail faulty so, replace the same after that issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211747634 | 22/02/2025 | 20 | GP3.1021.../2420431 | INSTANCE ID:-100782497 SITE ID:- I-UE-MILK-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG starting problem NAME:-SATETSH SINGH NUMBER:- 9919232310 | Task Start | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Faizabad |  | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211754850 | 25/02/2025 | 82.5 | 5H.8901.../2420143 | Starting/Stopping Issue | Task Start | Yogesh Kumar. | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211741602 | 21/02/2025 | 125.4 | 4H.8042.C4../2420423 | Starting Issue Call By Customer Name :- Suraj Mobile No :- 6386439451 | Task Start | Kumar Fuel | Excel Diesel Private Limited - Sultanpur | 53 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211742237 | 21/02/2025 | 58.5 | T4.8941.../2420811 | Battery Charging Issue Call By Customer Name :-Ram Mobile No :-7982975198 | Task Start | SETHI BUILDCON | Vidyut Engineers - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
53 | South | 211654297 | 28/01/2025 | 58.5 | T4.8941.../2421905 | Starting issue Call By Customer Name :-Vinaygan . Mobile No :-6385235499 | Open | DEVTA GENSETS [P] LTD | Bharath Diesel Sales and Service - Karappakkam |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211752293 | 24/02/2025 | 125.4 | 4H.8042.C4../2420669 | Maintenance Due alarm issue Call By Customer Name :- Shrikant Kumar Mobile No :-8210295791 | Closed | ARIHANT CONTRACTORS PRIVATE LIMITED | S.S. Enterprises - Allahabad | 344 | Maintenance alarm reset | Closed | Sudhir Awasthi | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
8 | North | 211751329 | 24/02/2025 | 125.4 | 4H.8041.../2420549 | Display Issue Call By Customer Name :- Sarjeet Ji Mobile No :- 9810090015 | Task Start | Ankur Generators | Vidyut Engineers - Noida | 139 | found maintenance Alarm show in Ems 640 Display After that reset the maintenance Alarm | Closed | Kapil Solanki | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
10 | North | 211750686 | 24/02/2025 | 320 | F6.8802.../2420073 | Diseal Leakage Issue Call By Customer Name :- Rishi Pal Mobile No :- 7838955880 | Task Start | A.G. Pipes Pvt. LTD. | Paluck Technologies Ltd. - Faridabad | 234 | Found oil leakage from oil drain bolt tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
56 | South | 211653283 | 28/01/2025 | 40 | 3H.8951.../2421102 | DG is running Plz do OT | Open | Sigma Marketing Services | Sri Manjunath Technical Services - Bhimavaram |  | Visit pending | Open | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
59 | South | 211652200 | 28/01/2025 | 125.4 | 4H.8041.../2420387 | Detective Lamp On Alarm Issue Call By Customer Name :-Pranav Patil Mobile No :-7269825555 | Closed | NATIONAL HIGHWAYS INFRA PROJECTS PRIVATE LIMITED | KALA Care Global LLP - Belagavi | 254 | Adblue low top up the same | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211754636 | 25/02/2025 | 58.5 | T4.8941.../2423014 | Low Fuel Alarm Issue Call By Customer Name :- Punit.. Mobile No :- 8762914587 | Task Start | DARSHAN POWER SERVICES | Paluck Technologies Ltd. - Gurgaon | 55 | Oil leakage from oil filing cap tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | North | 211742057 | 21/02/2025 | 57 | T4.8941.../2420185 | Automation Issue Call By Customer Name :- Atmaram Mobile No :-9810571470 | Task Start | Jay Garud Gas Station | OVN Industries Private Limited - New Delhi | 39 | found dg amf panel control wiring was break, we connect the wire and check the dg set and runnning ok | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | WEST | 211751439 | 24/02/2025 | 82.5 | 5H.8901.../2420929 | Line Rejection | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | LR | no issue with dg | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
42 | South | 211748856 | 23/02/2025 | 25 | GP3.8702.../2420678 | Automatically switching off Call by : Customer Name : Ramesh Contact : 7989763455 | Task Start | Mr. Ashrit Kishan | Ultimate Power Source - Ananthapuramu | 259 | Emergency Alarm. So tight the wire issue resolve | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
40 | South | 211748918 | 23/02/2025 | 250 | F6.8841.../2420235 | Starting Issue Call by : Customer Name : Naga raj Contact : 9880429191 | Open | SHUBHAM THE VENUE | KALA Care Global LLP - Kalaburagi |  | visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211744425 | 21/02/2025 | 82.5 | 5H.8901.../2420067 | Starting issue Called by customer Name : yusuf Number : 8989161747 | Task Start | Jharkhand Machinery | HACS Engineering and Tech Private Limited - Jamshedpur |  | Update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | WEST | 211758357 | 26/02/2025 | 20 | GP3.8601.../2520175 | Oil seal replacement | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from flywheel side need to change the oil seal. | Closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
1 | WEST | 211760417 | 26/02/2025 | 20 | GP3.8601.../2520301 | OIL LEAKAGE | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from flywheel side need to change the oil seal. | Closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
28 | North | 211664271 | 31/01/2025 | 125.4 | 4H.8041.../2420510 | Starting/Stopping Issue | Closed | SUNLIGHT ENGINEERS | OVN Industries Private Limited - New Delhi | 39.5 | Found when start the DG, Dg was cranking but not start check in panel found 2C wire was loose tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211752769 | 24/02/2025 | 58.5 | T4.8941.../2520157 | Red lamp on alarm issue Called by customer Name : RAVI Number : 9018466062 | Task Start | RAVI | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211739071 | 20/02/2025 | 20 | GP3.8604.../2420180 | INSATANCE ID:-100742007 SITE ID:-I-BR-AGIN-ENB-9022 CALL BY CUSTOMER:- DG ISSUE :-DG GCU ALRAM NAME:-RATESH KUMAR NUMBER :- 8340233128 | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | Update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | North | 211665927 | 31/01/2025 | 750 | DV2.8501.C4../2320007 | Inspection/Maintenance | Open | Merino Industries Ltd. | Paluck Technologies Ltd. - Ghaziabad |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211737340 | 20/02/2025 | 45 | 3H.8951.../2520086 | VOLTAGE ISSUE Call By KGD Name :kumkum Number : 9234456624 | Open | MUNDHRA HOSPITAL PRIVATE LIMITED | HACS Engineering and Tech Private Limited - Jamshedpur | 4 | SE found voltage fluctuation P-N 220-235 so adjusted the AVR stability after that checked found voltage ok 229-231V | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | WEST | 211752602 | 24/02/2025 | 15 | GP3.8501.../2520175 | Smoke issue | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | white Smoke from 2nd cylinder need to check . | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211753693 | 25/02/2025 | 25 | GP3.8702.../2421189 | Under Load Alarm Issue Call By Customer Name :- Pankaj Number:- 9805887886 | Open | Lenexis Foodworks Pvt. Ltd. | Megatron Engineers - Amritsar |  | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | East | 211734797 | 19/02/2025 | 58.5 | T4.8941.../2422206 | Voltage Fluctuation Issue And Preventive Maintenance Call By Customer Name :- Zafar . Mobile No :-8051021281 | Task Start | Laiba Developers & Construction Pvt. Ltd. | HACS Engineering and Tech Private Limited - Ranchi | 2 | Customer complaint was voltage fluctating but when SE visited and checked the found no fluctuation in voltage only 1-2 V were fluctuating that is normal. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211734112 | 19/02/2025 | 30 | 3H.8902.../2420892 | Starting Issue Call By Customer Name :- Rawat Ji Mobile No :- 8637507378 | Open | LINKCON ENGINEERING PRIVATE LIMITED | Hibreed Engineering Pvt. Ltd. - Guwahati | 25 | SE visited and Cranksensor issue (637/5) so checked the cranksensor connector and SE suspected that there was extra gap in female pin connector so adjusted it by pressing that reconnected and started found no issue tested for 3-4 time. | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | East | 211733456 | 19/02/2025 | 45 | 3H.8951.../2421129 | Mobil Leakage Issue Call By Customer Name :- Rajesh . Mobile No :- 9471465472 | Task Start | A R ENTERPRISES | Globalline India Services Private Limited - Madhepura |  | lube oil leakage was from the rocker cover joint so changed the joint and after that refitted the rocker cover and test for 1hr found no leakage. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | East | 211747493 | 22/02/2025 | 30 | 3H.8902.../2420349 | Starting Issue & redlamp alaram Issue Call By Customer Name :- Snatan Sir Mobile No :- 9831077965 | Open | Matri Enterprise | Revenus Industries Pvt. Ltd. - South Kolkata |  | Visit Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211757722 | 26/02/2025 | 125.4 | 4H.8041.../2420022 | Oil leakage issue | Closed | NAV. Ambika Agro LLP. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 295 | Lube Oil leakage found near filter due to filter found loose so tightened the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211751374 | 24/02/2025 | 15 | GP3.8501.../2420945 | Tripping issue and Starting issue Call By Customer Name :- Samarth Mobile No :-7411117663 | Open | Bijapur DG Power Controls | KALA Care Global LLP - Bagalkote |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | East | 211747493 | 22/02/2025 | 30 | 3H.8902.../2420349 | Starting Issue & redlamp alaram Issue Call By Customer Name :- Snatan Sir Mobile No :- 9831077965 | Open | Matri Enterprise | Revenus Industries Pvt. Ltd. - South Kolkata |  | Visit Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211758097 | 26/02/2025 | 125.4 | 4H.8042.C4../2420692 | Starting/Stopping Issue | Open | Bharat Tech and Engineering | Suraj Moters Stores - Leh |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211736964 | 20/02/2025 | 15 | GP3.8501.../2420550 | Red alarm issue Call by customer Name - Bipin Barla No - 9570025083 | Task Start | Assisi Bhawan | HACS Engineering and Tech Private Limited - Ranchi | 1 | Emergency switch alarm showing so checked the emergency switch screw also cleaned properly and tighten screw issue resolved | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | East | 211742850 | 21/02/2025 | 0 | DV0.8501.C4../2420102 | LOW COOLANT LAVEL | Task Start | ELMECH ENGINEERS | Revenus Industries Pvt. Ltd. - Howrah |  | Visit Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
29 | South | 211660697 | 30/01/2025 | 58.5 | T4.8941.../2423054 | Amber Lamp Alarm Call By Customer Name :- MAHADEV NILAJKAR Mobile No :- 9108727222 | Task Start | FLOWTEX ENGINEERS | KALA Care Global LLP - Belagavi | 28 | Update pending | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | WEST | 211742065 | 21/02/2025 | 0 | GP3.8501.../2520348 | OIL leakage | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from LLOP switch change the switch . | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | WEST | 211741191 | 21/02/2025 | 25 | GP3.8702.../2421920 | LINE REJECTION | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | LR | no issue with dg | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | North | 211665215 | 31/01/2025 | 15 | GP3.8501.../2420723 | Starting/Stopping Issue | Closed | PEEPAL FARM FOUNDATION. | Megatron Engineers - Amb | 142 | DG Hunting Issue with Red Lamp on ; will attend Today | open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | South | 211660766 | 30/01/2025 | 200 | 6H.8435.../2420159 | Starting/Stopping Issue | Closed | NP Ramesh | Surya Power Services - Bommasandra, Bangalore | 127 | 1761/14 Adblue low topup the same | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | North | 211737612 | 20/02/2025 | 40 | 3H.8951.../2420483 | AMF Panel not working,not working properly.-512798 | Closed | ICICI Bank Limited | Suraj Motor Store - Jammu | 278 | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | West | 211745295 | 22/02/2025 | 125.4 | 4H.8042.C4../2420112 | Leakage Issue | Closed | MSLR. Private Limited | Shree Engineering Service - Satna | 754.42 | Engineer found fuel filter cracked so replaced it. | Closed | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | West | 211742710 | 21/02/2025 | 15 | GP3.8501.../2420196 | Starting Issue Call By Customer Name :- Anjay Gupta Mobile No :- 9399028325 | Closed | Neelam Fuels. | Shree Engineering Service - RAIGARH | 301 | DG auto starting problem and auto wire damage found. So changed it. | Closed | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | West | 211741152 | 21/02/2025 | 82.5 | 5H.8901.../2420307 | Black smoke | Closed | Mrs. Baby Mallick | Shree Engineering Service - Jagdalpur | 391 | Smoke was coming out from the exhaust side. Engineer checked and found red band in vacuum indicator because there was polythene in the air filter. So cleaned it and educated to the customer. | Closed | Vijay patil | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
36 | North | 211665814 | 31/01/2025 | 15 | GP3.8501.../2421242 | Starting/Stopping Issue | Open | ALIF EMPORIUM | Suraj Motor Store - Srinagar | 369.11 | Visit Pending | open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211745345 | 22/02/2025 | 58.5 | T4.8941.../2420645 | Starting issue Call by customer Name - Mukesh Kumar No - 9859911810 | Open | Nirmalya Baruah. | Hibreed Engineering Pvt. Ltd. - Guwahati | 22 | SE visited site and found DG starting in mannual mode normally in healthy condition but in automode DG was not starting because its negative sensing wire found loose after tightening issueresolved. | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
35 | North | 211665895 | 31/01/2025 | 15 | GP3.8501.../2420328 | Error Code issue Call By Customer Name - Saksham No - 8700988806 | Task Start | Hra Rice Mills | Dynamic Engineering Services - Jalandhar | 59.53 | Visit Pending | open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | West | 211746397 | 22/02/2025 | 15 | GP3.8501.../2421866 | Instance ID:-100801462 Site ID :- GMR Call By Customer :- DG Issue :- CONTACTER PROBLEM Name :- PRAMOD SHARMA Number :-7999852471 | Closed | Bharti Airtel Limited | Natraj Power Tech - Gwalior | 13 | Customer side LVM issue. | Closed | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | West | 211745154 | 22/02/2025 | 58.5 | T4.8941.../2422339 | ABNORMAL SOUNG IN ENGINE Call By Customer Name :- RAMESH Mobile No:-9979650985 | Closed | Ramesh Ji B. Rathod | Unique Techno Services Pvt Ltd. - Anand | 26 | The V belt was loose so tightened it. | Closed | Amit sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | WEST | 211731083 | 18/02/2025 | 20 | GP3.8601.../2520175 | oil leakage | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from flywheel side need to change the oil seal. | Closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
7 | WEST | 211741189 | 21/02/2025 | 0 | T4.8941.../2520180 | line rejection | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | no issue with dg | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | WEST | 211741800 | 21/02/2025 | 20 | GP3.8601.../2520216 | Oil leakage | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | LR | oil leakage from benjo bolt. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | West | 211742548 | 21/02/2025 | 320 | F6.8802.../2420235 | Synchronization activate | Closed | AVADHUT SATHE TRADING ACADEMY PRIVATE LIMITED | Transcreek Engineers Pvt. Ltd. - Panvel | 247 | Open for syncronization | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211676848 | 02/02/2025 | 58.5 | T4.8941.../2420845 | Starting issue Call by customer Name - Ram Sharan No - 7982975198 | Open | Sahib Generator | Vidyut Engineers - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | West | 211727852 | 17/02/2025 | 125.4 | 4H.8042.C4../2420063 | Genset Trip | Closed | Hukumchand Shantikumar Bros. | Dicksons Engineering Co.Pvt.Ltd. - Nagpur | 17 | Adblue level low so top up adblue. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | West | 211746422 | 22/02/2025 | 40 | 3H.8951.../2421212 | VOC - LOOSE WIRING /CONNECTIONS IN KOEL AMF PANEL Customer Name -L K Parasar Customer Number -9644009101 Mode- SR Generated through CDI calling. | Closed | LG ELECTRONICS INDIA LIMITED | Natraj Power Tech - Indore | 2.39 | Customer side AC issue. | Closed | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | South | 211748899 | 23/02/2025 | 200 | 6H.8435.../2420064 | Over Heat Problem Call by : Customer Name :Moosa Abdulla Contact :7306429978 | Closed | FRESHCO HOTELS | Surya Power Services - Bommasandra, Bangalore | 63 | Engine over heating due to V belt is loose conditon after tight the V belt after checking the engine all parameters after start the engine running coundtion ok | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | East | 211740284 | 20/02/2025 | 500 | DV8.8501.C4../2320020 | Starting Issue Call By Customer Name :- Vishwjeet .. Mobile No :- 6370803738 | Closed | Action Ispat & Power. | Gangpur Sales and Services - Jharsuguda | 35 | Update Pending | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211758633 | 26/02/2025 | 82.5 | 5H.8901.../2420421 | Oil leakage issue | Closed | Green Ecoplast LLP. | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 42 | Lube Oil leakage found from oil filler cap due to O-ring was disaligned so corrected the samewhen DG is in running condition so tightened all the bolts & clean the poured Oil,run the DG ,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | South | 211735603 | 19/02/2025 | 82.5 | 5H.8901.../2420641 | Starting Problem &BatteryProblem Call by : Customer Name :venkat Ramani Contact 9443168577 | Open | E. M. A. R. Mahal | Electro Controls - Tirunelveli | 19 | Starting problem due to engine control wiring line turbo side burnt out. EOD has been place | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
34 | South | 211660474 | 30/01/2025 | 320 | F6.8802.../2420124 | Leakage Issue | Task Start | TALIPARAMBA CO-OPERATIVE HOSPITAL SOCIETY LTD. | G-Care Diesels Private Limited - Kannur | 46 | Visited the site found oil leakage from oil transfer adaptor O ring Side | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211661345 | 30/01/2025 | 15 | GP3.8501.../2420629 | Starting/Stopping Issue | Closed | S. S. V. Industries | SAM Engineering corporation - Varanasi Cantt. | 39.3 | Self +ve wire loose trightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | South | 211738927 | 20/02/2025 | 15 | GP3.8501.../2320019 | Oil Leakage issue and Preventive Maintenance Call By Customer Name :- Padmini Mobile No :- 9841661712 | Completed | KPG SOLUTIONS PRIVATE LIMITED | Net Work Diesels - Sholinganallur | 45 | FOUND DIESEL LEAK FROM DIESEL TANK DRAIN NUT SIDE DUE TO LOOSE CONDITION.RETIGHTENED ISSUE RESOLVE. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | South | 211738096 | 20/02/2025 | 15 | GP3.8501.../2421008 | Leakage Issue | Completed | KAVIN ESTATE | Bharath Diesel Sales and Service - Dindigul | 31 | Checked and found the Diesel mixing with oil so Oil level above the recommended level so oil leakage from breather side. Photo attached. | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | South | 211737869 | 20/02/2025 | 10 | GP3.8301.../2420627 | Leakage Issue | Closed | POINT SALES AND SERVICES | Electro Controls-Coimbatore 2 | 9 | Found observed the problem oil leak from oil pressure dummy Bolt.( The oil pressure dummy Bolt was removed and the copper washer in it was damaged,. So a new copper washer was replaced and the oil leakage was arranged.)The engine was run for 30 minutes and there no oil leakage. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | South | 211659518 | 30/01/2025 | 58.5 | T4.8941.../2422611 | Auto Starting Issue Call By Customer Name :-IMRAN WAJID Mobile No :- 8217064637 | Closed | IMRAN WAJID | Surya Power Services - Mysuru | 14 | Visit the site check the amf panel wiring is mc gc really is mc really out is not comming and sper plot is connected the Mr 4 wire no and check the all external condition is found ok start and run the engine all working parameters condition is satisfied | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | South | 211736753 | 20/02/2025 | 20 | GP3.8601.../2421946 | Starting Problem Call by : Customer Name :Aarumugam Contact : 8300477122 | Closed | M. AMBEDKAR | Bharath Diesel Sales and Service - Dindigul | 6 | Emergengy Alarm topup.Found Emergency switch element voltage found only 8Volt so Given the Negative supply Emergency switch element from battery negative and carried out the necessary parameters found normal and carried out the load test two hours found normal, DG running normal | Closed | Mr. NandhaGopal | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
16 | South | 211736682 | 20/02/2025 | 82.5 | 5H.8901.../2420884 | Starting/Stopping Issue | Closed | ICICI Bank | Surya Power Services - Mysuru | 4 | Visited the site checked the wiring connections,alarms and then found that diesel supply issues so airlock out the complete diesel supply line and also removed the nozzles and checked the diesel spray and finally refitted all the nozzles and started the engine. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | South | 211736637 | 20/02/2025 | 15 | GP3.8501.../2422038 | Trip_Genset_Low_Voltage | Completed | ALMADEENA PETROLEUM AGENCIES | Bharath Diesel Sales and Service - Kallakurichi | 10 | Alternater under voltage problem repoted the customer visited Checked the alternater shake in rotor assmblyInspected the removed the alternater and hand over to them after completing theri service to the alternater their work shop and moved it the customer site Fitted the alternater and load test done okRunning found normal ok | Closed | Mr. NandhaGopal | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
17 | South | 211755168 | 25/02/2025 | 15 | GP3.8501.../2422178 | VOC - Shut Down Alaram Issue Customer Name -Shiva Kumar Customer Number -9986290851 Mode- SR Generated through CDI calling. | Open | M/s. SRI MARUTHI ENTERPRISES | Surya Power Services - Peenya, Bangalore |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | South | 211659517 | 30/01/2025 | 15 | GP3.8501.../2420980 | Starting Issue Call By Customer Name :- Subish . Mobile No :-6364078042 | Closed | Cake World Bakery Sweets | Prasad Power Engineers - Chithradurga | 70 | Visit the site check the dg and check the dinom condition not charging condition check the fuse bring and replace the fuse and start the dg running ok oil and battery distilled water and v-belt and air filter coolant level and cable tarminal and voltage condition found ok start the dg running ok | Closed | Mr. Anil Kumar H G | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
14 | South | 211755376 | 25/02/2025 | 58.5 | T4.8941.../2423159 | Abnormal Sound Call by : Customer Name :N.PANDIYARAJAN Contact :7010016081 | Completed | Visalam Technologies LLP | Net Work Diesels - Chennai | 7 | 2791/18 Error code | completed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | South | 211732780 | 19/02/2025 | 15 | GP3.8501.../2420804 | Red Lamp Alarm Problem Call by : Customer Name :Nageshreddy Contact :8248058460 | Task Start | BRUNDAVANA CONSTRUCTIONS PRIVATE LIMITED. | Vijayshree Diesel Sales and Service - Hospet | 250 | Control pannel wire burning suspected Emergency connector wire loose & burn | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211661393 | 30/01/2025 | 30 | 3H.8902.../2420639 | Starting/Stopping Issue | Closed | Setwell Coating India Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Agra | 2 | Control wiring loose tightn the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211662123 | 30/01/2025 |  | 3H.8951.../2520140 | line rejection | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR-2 | Found in panel 2C wire was loose tightness the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | South | 211749812 | 24/02/2025 | 0 | GP3.8702.../2422057 | LEAK OFF PIPE REPLACMENT | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Leakoff pipe damage. So Change the new leakoff pipe | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | South | 211748954 | 23/02/2025 | 250 | F6.8842.C4../2420060 | Oil Leakage Problem Call by : KGD Name : Srikanth Contact : 8686837779 | Task Start | NEW ROYAL CONVENTION | Powerlinks Infra Tech Pvt Ltd - Warangal | 11 | Oil leakage issue. Found dipstik isd remove condition, Suspected leakage from breather side but customer not allowed to checked properly. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | South | 211735972 | 19/02/2025 | 15 | GP3.8501.../2420865 | Automation issue Call By Customer Name :-Kavita Bhatia Mobile No :-9513902829 | Closed | Kavita Bhatia | Surya Power Services - Kalyan Nagar | 110 | Visited the site checked the engine based on complaint reported found under speed tripping. SE visit found no under speed alarm | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | South | 211660581 | 30/01/2025 | 125.4 | 4H.8042.C4../2420997 | Electrical Problems | Closed | M/s. Nakoda Dairy Pvt Ltd | Surya Power Services - Bommasandra, Bangalore | 2 | Customer side change over issue | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | South | 211660523 | 30/01/2025 | 58.5 | T4.8941.../2520053 | ENGINE HUNTING | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the engine and noticed that the problem in the turbo side air flow which is due to the blockage of turbo by rubber material this rubber material seems to be came from the air filter hose it may bethe excess pips of rubber which might came wite hose at the time hose manufacturing dis casting so chakead the air filter hose also and cleared it remove the turbyrefitted the same load test runing ok | Closed | Mr. NandhaGopal | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
26 | South | 211754342 | 25/02/2025 | 125.4 | 4H.8042.C4../2420294 | DG Issue | Open | AIRPLAZA RETAIL HOLDINGS PRIVATE LIMITED | KALA Care Global LLP - Hospet |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211758621 | 26/02/2025 | 500 | DV8.8501.C4../2420049 | Error Code Issue And Starting Issue Call By Customer Name :-Saed Juned Mobile No :- 8491858984 | Open | Mir Cold Store Pvt. Ltd. | Suraj Motor Store - Srinagar |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | East | 211736842 | 20/02/2025 | 58.5 | T4.8941.../2422211 | Leakage Issue | Closed | M/S OM POULTRY FARM | Gangpur Sales and Services - Bargarh | 153 | SE found no leakage in DG,DG running condition was normal | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211674386 | 01/02/2025 | 200 | 6H.8435.../2420008 | Sound/Vibration Issue | Closed | AASHA DREAMESTATE LLP | Pratap Diesels Pvt. Ltd. - Alwar | 202 | Found fan belt loose tightness the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211757767 | 26/02/2025 | 45 | 3H.8951.../2421154 | Starting Issue Call By Customer Name :-Sudhir Rana Mobile No:-8167013473 | Closed | Tusar Kanti Bandyopadhyay | Revenus Industries Pvt. Ltd. - Bankura | 57 | DG shutdown due to 516166 (Inductment alram) after that clear the code Issue resolved. | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211737817 | 20/02/2025 | 160 | 6H.8475.../2420298 | V belt Damage | Closed | LP LOGISCIENCE LLP. | Electro Controls - Coimbatore | 70 | V- belt loose found & layer damage so replaced the belt. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211759047 | 26/02/2025 | 250 | F6.8841.../2420263 | Electrical Problems | Task Start | Jai Prakash Associates Ltd. | K.C. Diesel Services - East Sikkim |  | Visit Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211755443 | 25/02/2025 | 250 | F6.8841.../2420347 | Fuel Leakage Issue Email By GOEM Name -Power Generators | Closed | Rontix Imaging Center & Hospital | Almas Engineers - Dibrugarh | 2.8 | As per the complaint SE found no leakage of fuel it was just due to over fuel in the tank. so on running condition it was flowing out from the top of the tank | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | South | 211660571 | 30/01/2025 | 82.5 | 5H.8901.../2420470 | Control Panel Issue Email by KGD Name - Arunraj MR | Open | Haims Ventures LLP. | Surya Power Services - Mysuru | 276 | Viste the site check the ems eb current show 1 phase . Phase is 0 0 so advice for customer to shows from eb so advice for change the change over | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211676844 | 02/02/2025 | 20 | GP3.1021.../2420337 | INSTANCE ID:-100777474 SITE ID:-I-UE-ABDD-ENB-0926 CALL BY CUSTOMER:- DG ISSUE :-DG UNDER VOLTAGE ISSUE NAME:-ANKIT NUMBER:- 9235964730 | Open | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211735458 | 19/02/2025 | 125.4 | 4H.8042.C4../2420955 | Umber lamp on alarm issue Call by customer Name:Sandeep Reddy Number: 7330620689 | Task Start | KMR CONVENTION | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 17 | 3031/14 Error code coming need to flash dummy file. Today SE will visit. | Task Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211758505 | 26/02/2025 | 20 | GP3.8601.../2420391 | Door lock issue Call by customer Name - Jitendra Kumar No - 7321991140 | Task Start | Arya Preparatory School. | Globalline India Services Private Limited - Muzaffarpur | 119 | SE visited and adjusted the door lock latch after that issue resolved | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211733948 | 19/02/2025 | 160 | 6H.8475.../2420271 | Oil leakage from fip pump side and coolant leak | Closed | Magtorq Private Limited. | Ultimate Power Source - Hosur | 33 | Checked found oil leakage from gear cover gasket side oil leakage due to gear case cover bolt tite not proper so re tite the gear case cover tited then oil leakage is arrested. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | South | 211737226 | 20/02/2025 | 5.5 | CC1.1013.../2400339 | Starting Problem Call by : Customer Name : RAJA Contact : 8526640266 | Open | V.RAJA | Ultimate Power Source - Ambur | 15 | Genset sensing wire damaged , genset started some mins after showing under speed issue.Genset sensing wire damaged , genset started some mins after showing under speed issue. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | South | 211750552 | 24/02/2025 | 25 | GP3.8702.../2421699 | Starting/Stopping Issue | Open | Axis Bank Ltd | KALA Care Global LLP - Kalaburagi |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | South | 211754338 | 25/02/2025 | 40 | 3H.8951.../2520071 | Starting/Stopping Issue | Task Start | Joylie Noronhaa | Prasad Power Engineers - Udupi | 15 | Update Pending | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211733098 | 19/02/2025 | 5.5 | CC1.1013.../2400332 | Starting Problem Call by : KGD Name :Nithya Contact :9562607535 | Closed | DDRC AGILUS PATHLABS LIMITED | G-Care Diesels Private Limited - Ernakulam | 3.8 | found on off switch wire loose rectified the issues | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | South | 211738494 | 20/02/2025 | 40 | 3H.8951.../2420549 | Hunting problem Call by : Customer Name : Ramesh Contact : 9949230983 | Task Start | P. Ramesh | Laxmi Diesels - Srikakulam | 188 | No issue. Found Fuel filter Chocked. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211676806 | 02/02/2025 | 125.4 | 4H.8042.C4../2420330 | Voltage Fluctuation Issue Vibration Issue And High oil temperature Issue Call by Customer Name :Kapil Kumar Number :7317645299 | Task Start | Shri Dhanushdhari Hotels and Resorts | Espiem Engines & Machines (P) Limited - Jhansi | 58 | HIgh adblue alarm,Dosing grp warning alarm reset the alarm with tool | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211758338 | 26/02/2025 | 5 | CP1.1003.../2400192 | STARTING KEY NOT WORKING | Task Start | North East Powerline Equipment Pvt.Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 1 |  | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211738536 | 20/02/2025 | 10 | GP3.8301.../2420342 | Engine starting issue | Task Start | M/s. SRIDHANA LAXMI SWEETS | Gangpur Sales and Services - Rourkela | LR | Engine under EDO | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211728638 | 18/02/2025 | 5.5 | CC1.1013.../2400327 | Controller Pannel Call by : Dealer Name :Ranjith Contact :8870901991 | Task Start | Ratnm Infra | Bharath Diesel Sales and Service - Chennai |  | Control panel side fuse blown so replace the fuse | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211734797 | 19/02/2025 | 58.5 | T4.8941.../2422206 | Voltage Fluctuation Issue And Preventive Maintenance Call By Customer Name :- Zafar . Mobile No :-8051021281 | Task Start | Laiba Developers & Construction Pvt. Ltd. | HACS Engineering and Tech Private Limited - Ranchi | 1 | today SE will visit site | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211698949 | 10/02/2025 | 5.5 | CC1.1013.../2400378 | Starting Issue Call By Customer Name :- RITUKANTA SAHOO Mobile No :- 7008384008 | Task Start | Creative Image | Gangpur Sales and Services - BHUBANESWAR | 92 | There was no issue in DG, DG was tripping after running 30 mintues due to DG was kept in a van,after that remove the DG from the van and tested, no issue found | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | West | 211611129 | 16/01/2025 | 40 | 3H.8951.../2420861 | Starting/Stopping Issue | Task Start | Aakar Public School | Natraj Power Tech - Gwalior | 36 | error 157/14 CONNECT ikonnect and clear code , issue solved. | closed | Vijay Patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | West Zone | 211707537 | 11/02/2025 | 35 | 3H.8902.../2422238 | dg problem | Open | ICICI Bank Limited | Unique Techno Services Pvt Ltd. - Anand | 2 | Visit Pending. | CLOSED | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | West | 211643468 | 25/01/2025 | 35 | 3H.8902.../2422238 | FUEL LEAKAGE FILTER BODY | Closed | ICICI Bank Limited | Unique Techno Services Pvt Ltd. - Anand | 1 | Leakage from fuel filter benjo bolt so replaced the filter assembly , issue solved | Closed | Amit shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | West | 211659492 | 30/01/2025 | 125.4 | 4H.8042.C4../2420162 | Leakage Issue | Completed | YMCA OASIS | Unique Techno Services Pvt Ltd. - Ahmedabad | 297 | oil leakage from flywheel side oil side , changed the seal. Gallery plug found loosen tighten the same issue resolved. | Closed | Amit shandilya | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
2 | North | 211707631 | 11/02/2025 | 20 | GP3.1021.../2420471 | Fuel Leakage & Air Lock | Task Start | Reliance Jio Infocomm Limited | Excel Diesel Private Limited - Faizabad | 108 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211707531 | 11/02/2025 | 57 | T4.8941.../2320129 | Starting and Preventive Maintenance Call By Customer Name :- Rajesh Mobile No :- 8527341102 | Open | Country Home Fashions Pvt. Ltd. | Vidyut Engineers - New Delhi |  | Visit Pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211706784 | 11/02/2025 | 20 | GP3.1021.../2420382 | INSTANCE ID:-100779499 SITE ID:- I-UE-MNGJ-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG AUTOMATION/UNDER VOLTAGE ALARM ISSUE NAME:- MANISH NUMBER:- 9839439345 | Open | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - LUCKNOW |  | Visit Pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211706589 | 11/02/2025 | 57 | T4.8941.../2320121 | Abnormal Sound Issue. Call By Customer Name :- Upendra Gupata Mobile No :- 6367929800 | Closed | Hind Chemisales. | Pratap Diesels Pvt. Ltd. - Alwar | 441 | Fan belt damage and earthing wire broken due to chemical industries. | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211706580 | 11/02/2025 | 250 | DV8.9840.../2420003 | Voltage voltage increase & Heating Call By Customer Name :- Ghanshyam ji Mobile No :- 9560364465 | Task Start | Kundan Refinery P. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | Visit Pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211706192 | 11/02/2025 | 57 | T4.8941.../2320067 | Alarm issue | Closed | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 1520 | Maitenance due alarm celar the alarm, Last Service (30/11/24-1209) | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | North | 211706154 | 11/02/2025 | 200 | 6H.8435.../2320015 | Leakage Issue | Closed | TCI Supply Chain Solutions - A division of Transport Corporation of India Limited | Paluck Technologies Ltd. - Ghaziabad | 254 | Found Minor leakage from oil from sump then check oil drain bolt was loose so, tightness the same | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | South | 211681462 | 04/02/2025 | 20 | GP3.8601.../2421691 | Starting/Stopping Issue | Open | Thirupathi Gen-z Private Limited | Ultimate Power Source - Vellore | 3 | When SE found Emergency stop pressed by Customer | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211706102 | 11/02/2025 | 45 | 3H.8951.../2520068 | Oil Leakage issue Call by customer Name - Vikas Number - 9793099995 | Closed | INDIA MOTOR | Espiem Engines & Machines (P) Limited - KANPUR | 12.22 | oil leakage from block 10 no. bolt got loose therefore oil leakage issue than tight bolt | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211705776 | 11/02/2025 | 20 | GP3.1021.../2420458 | INSTANCE ID:-100782496 SITE ID:- I-UE-ABDD-ENB-0932 CALL BY CUSTOMER// DG ISSUE:- DG GCU/KWH/UNDER VOLTAGE ALARM ISSUE NAME:- GULSHER NUMBER:- 9076882212 | Completed | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad | 5 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | North | 211705799 | 11/02/2025 | 500 | DV8.8501.C4../2420185 | Electrical Problems | Open | Infratech Solutions | Vidyut Engineers - Noida | 58 | Found Charging alaternator fuse was faulty, replace the same | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | West | 211648212 | 27/01/2025 | 0 | DV2.8501.C4../2420115 | Oil leakage for oil Sump Joint | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi |  | Oil leakage from oil gallary bolt thread, repair it issue solved. | Closed | Amit shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | West | 211664217 | 31/01/2025 | 15 | GP3.8501.../2421164 | Starting issue Call by customer Name: Ramesh Number: 7600524211 | Closed | GLOBAL POWER PROJECTS | Unique Techno Services Pvt Ltd. - Surendranagar | 42 | Engine crank but not start due to relay card loose connection tight the wire issue solved. | Closed | Amit shandilya | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
19 | North | 211705381 | 11/02/2025 | 125.4 | 4H.8042.C4../2420330 | Voltage Fluctuation | Closed | Shri Dhanushdhari Hotels and Resorts | Espiem Engines & Machines (P) Limited - Jhansi | 68 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211705356 | 11/02/2025 | 25 | GP3.8702.../2421217 | Automation Issue Call By Customer Name - Manish Number - 7897201173 | Closed | hotel raj darbaar | Excel Diesel Private Limited - Faizabad | 13 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | North | 211705300 | 11/02/2025 | 82.5 | 5H.8901.../2320110 | Excessive Smoke | Completed | Gyan Prakash | Pratap Diesels Pvt. Ltd. - Ajmer | 60 | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211705162 | 11/02/2025 | 250 | F6.8841.../2320013 | Starting Issue Email by Customer Name - GAYATRI | Task Start | Gayatri Construction Machinery | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Visit Pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | North | 211705021 | 11/02/2025 | 500 | DV8.8501.C4../2420058 | Inspection/Maintenance | Closed | Regal Emporia Infratech Pvt. Ltd. | Vidyut Engineers - Noida | 94 | Wrong report- Found no any issue | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | North | 211704898 | 11/02/2025 | 58.5 | T4.8941.../2421555 | Door lock Issue. Call By customer. Name:-Rakesh Kumar Mobile No.:-9997173716 | Closed | Global Health Spine Joint & Laser Centre | Deep Jyoti Electricals and Services - Haldwani | 92 | Adjust the Door lock alighnment after that issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | North | 211704892 | 11/02/2025 | 125.4 | 4H.8042.C4../2420669 | Urea Consumption issue Call By Customer Name :- Shrikant Kumar Mobile No :- 7979779535 | Closed | ARIHANT CONTRACTORS PRIVATE LIMITED | S.S. Enterprises - Allahabad | 115 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | North | 211704735 | 11/02/2025 | 58.5 | T4.8941.../2421748 | Starting Issue. Call By Customer. Name:- Ajay Yadhav. Mobile No.:-7704834099 | Closed | R & C INFRA ENGINEER'S PVT LTD | S. R Engines Sales And Service - LUCKNOW | 634 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211705960 | 11/02/2025 | 30 | 3H.8902.../2320178 | Starting issue Call By Customer Name :Sanjiv kumar No: 9873761619 | Closed | Nagpal Nursing Home | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 147 | Update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | North | 211704667 | 11/02/2025 | 15 | GP3.8501.../2420019 | INSTANCE ID:-100740392 SITE ID:-18667 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:- MANOJ KUMAR NUMBER:-9999567157 | Task Start | Bharti Airtel MO-Delhi | Vidyut Engineers - Noida | 23 | found DG set not making voltage Due to AVR V phase wire is broken After that We change the new wire and check DG set proper start and output voltage working Ok | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211698974 | 10/02/2025 | 45 | 3H.8951.../2520085 | Door Lock Issue And emergency Stop Alarm Issue Call By KGD Name ;Sheetal Gupta no :6299024030 | Task Start | Jai Prakash Kesari. . | HACS Engineering and Tech Private Limited - Hazaribagh | 64 | update pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | South | 211680965 | 04/02/2025 | 250 | F6.8841.../2420248 | Starting/Stopping Issue | Open | Trinetra Constructions. | G-Care Diesels Private Limited - Ernakulam | 5 | No issue from Dg Side. Customer want cooling time to be reduced. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211682555 | 04/02/2025 | 58.5 | T4.8941.../2422776 | Leakage Issue | Completed | Chaudhary Tent & Generator. | Espiem Engines & Machines (P) Limited - Etawah | 59 | Oil leakage from sump, oil drain side nut was loose tightness the same | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211685147 | 05/02/2025 | 58.5 | T4.8941.../2420403 | Under Speed Alarm Call By Customer Name :- Ravi Kumar Mobile No :-9934852155 | Task Start | Ravi Soni | Globalline India Services Private Limited - Muzaffarpur | 149 | update pending call not received by SE and cordinator | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211698024 | 09/02/2025 | 125.4 | 4H.8041.../2420627 | Starting Issue Call by customer Name :- Rajesh Roy No :- 9337241741 | Open | TRILOKNATH ENTERPRISES | Gangpur Sales and Services - Berhampur |  | Today SE will Visit site | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211697120 | 08/02/2025 | 200 | 6H.8435.../2420112 | Leakage Issue | Open | Bharat Parivar Rice Mill | Revenus Industries Pvt. Ltd. - Purba Burdwan |  | Today SE will Visit site | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | East | 211696445 | 08/02/2025 | 15 | GP3.8501.../2420151 | Starting Issue & Emergency Stop Alarm Call By Customer Name :- Santosh Mobile No :-9658166969 | Open | M/S MAHARISHI RAM RAJ TRUST | Gangpur Sales and Services - BHUBANESWAR | 58 | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | East | 211692952 | 07/02/2025 | 125.4 | 4H.8042.C4../2420767 | Starting/Stopping Issue | Closed | Shree raj Trading | K.C. Diesel Services - SILIGURI | 426 | Low adblue level,SE will visit to educate the customer and filling up the adblue,Issue resolved. | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | East | 211692755 | 07/02/2025 | 30 | 3H.8902.../2421262 | Automation Starting Issue Call By Customer Name :- Khokan Maity Number:- 9382778900 | Open | ABIS Exports India Private Limited. . | Gangpur Sales and Services - Bargarh |  | Update Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | East | 211698837 | 10/02/2025 | 58.5 | T4.8941.../2420350 | Under Speed Alarm Issue Call By Service Dealer Name :- Vikas Pradhan Mobile No :-8917400481 | Task Start | Tulsi Nxt | Gangpur Sales and Services - Bhawanipatna |  | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211701508 | 10/02/2025 | 20 | GP3.8601.../2421221 | Starting/Stopping Issue | Open | REAL BUILDING CONSTRUCTIONS | SAAN Royal Power Solutions Private Limited - Zirakpur | 3 | DG Starting issue in auto mode,found mains sensing supply not connected to change-over so re-copnnected the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211699755 | 10/02/2025 | 40 | 3H.8951.../2420854 | Starting/Stopping Issue | Open | Malhotra Bone Joint Sugical Center and Multispeciality Clinic. | Industrial Power Solutions - LUDHIANA |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211682590 | 04/02/2025 | 58.5 | T4.8941.../2421888 | Automation Issue Call By Customer Name :- Karamat . Mobile No 8948469117 | Task Start | SSK CAR SALES | S. R Engines Sales And Service - LUCKNOW | 18 | DG not start found in panel 2A wire was loose tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211699586 | 10/02/2025 | 15 | GP3.8501.../2422130 | job work | Completed | Om Ispat (Harsh Jaiswal)) | S. R Engines Sales And Service - Gorakhpur | LR | CC SR | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211703705 | 10/02/2025 | 45 | 3H.8951.../2421641 | Starting issue Called by customer Name : Prabhakar Number : 8709322290 | Open | N D Mart | HACS Engineering and Tech Private Limited - Deoghar | 242 | visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211699528 | 10/02/2025 | 40 | 3H.8951.../2320109 | VOC -STARTER SOLENOID DEFECTIVE. Customer Name - Neel Kamal Customer Number -8899928066 Mode- SR Generated through CDI calling. | Task Start | Jammu Kashmir Cricket Association | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211683282 | 04/02/2025 | 20 | GP3.8601.../2420437 | Automation issue Call By Customer Name : Prabhit ... No 8090631313 | Task Start | Iqbal Singh | Espiem Engines & Machines (P) Limited - KANPUR |  | Customer side panel issue- Auto connection not done from customer side panel | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | North | 211698065 | 09/02/2025 | 20 | GP3.8601.../2420179 | Automation Issue Call By Customer Name - Nitin Jain Number - 8130295000 | Closed | Shree Shyam Civil Work. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 26 | Found Under speed alarm, reset the alarm then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | North | 211696486 | 08/02/2025 | 62.5 | T4.8941.../2420261 | voltage fluctuation Call by service dealer name - preeti no - 8427103008 | Task Start | Amson Transformers | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Voltage flactuation problem on load(When delta connectedmotors run ,Power factor reachs near 3) so we connected load analizer with IEC and nidec team . We collect load analysis data ,and share to HO Pune , | Open | Ved Prakash Gupta | [9 empty] | Power Factor | 6 | 4 | 3 | 72 | Low
22 | North | 211695379 | 08/02/2025 | 62.5 | T4.8941.../2420297 | Starting issue | Closed | Ecowalk Impex Private Limited | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 93 | R-Phase under voltage alarm occurred,fuse found faulty so replace the same & resolve the same | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211700712 | 10/02/2025 | 125.4 | 4H.8042.C4../2420732 | Starting/Stopping Issue | Task Start | Mondal Electricals | Revenus Industries Pvt. Ltd. - Asansol |  | Visit Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211699129 | 10/02/2025 | 40 | 3H.8951.../2421575 | LINE REJECTION | Task Start | MANOJ KUMAR BARIK | Gangpur Sales and Services - Dhenkanal |  | Today SE will visit site | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211698949 | 10/02/2025 | 5.5 | CC1.1013.../2400378 | Starting Issue Call By Customer Name :- RITUKANTA SAHOO Mobile No :- 7008384008 | Task Start | Creative Image | Gangpur Sales and Services - BHUBANESWAR |  | Update Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211682657 | 04/02/2025 | 15 | GP3.8501.../2420880 | Starting/Stopping Issue | Task Start | G.S.Paniraj | Surya Power Services - J C Road, Bangalore | 35 | Check the alarm EB Line phase reversed.reconnect the connection properly now running | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211698195 | 09/02/2025 | 20 | GP3.8604.../2420182 | INSTANCE ID:-100742009 SITE ID:-I-BR-GAYA-ENB-0041 CALL BY CUSTOMER\\ DG ISSUE :-DG PROBLEM NAME:-DEEPAK KUMAR NUMBER:-8340312768 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Gaya |  | Task pending visited the site found under voltage alarm after shutdown DG on auto mode. | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211705277 | 11/02/2025 | 35 | 3H.8902.../2422394 | Amber Lamp Alarm Call By Customer Name :- Mobile No :- | Open | Axis Bank Ltd | Suraj Motor Store - Srinagar |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211705155 | 11/02/2025 | 40 | 3H.8951.../2420076 | Maintenance Due Alarm Call By Customer Name :- Satyapriya Mobile No :-8168354829 | Task Start | Delhi Vidyapeeth School | SAAN Royal Power Solutions Private Limited - Sonipat | 152.48 | Maitainance due alarm occurred so change the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211680562 | 04/02/2025 | 20 | GP3.8601.../2421621 | Starting Problem Call by : Customer Name : Prasad reddy Contact : 9550797110 | Task Start | A Raviteja Reddy | Ultimate Power Source - Kadappa | 151.1 | Airlock in fuel suction line. So relesed the Air now engine running ok. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211699127 | 10/02/2025 | 40 | 3H.8951.../2320034 | Automation issue | Task Start | Trikuta Retailers Pvt. Ltd. | Vidyut Engineers - New Delhi | 41 | found contactor faulty so we replace under warranty contactor and DG auto start stop ok | Closed | Kapil Solanki | [9 empty] | Warranty | 4 | 3 | 2 | 24 | Low
5 | West | 211677798 | 03/02/2025 | 30 | 3H.8902.../2422024 | Emergency stop alarm issue Call By Customer Name :- Gopal Mobile No :- 9221070922 | Closed | SHREE MANGLAM BUILDCON (I) PVT LTD | Unique Techno Services Pvt Ltd. - Godhra | 31 | Emergency alarm so refieted the connector and used the cable tie. | Closed | Amit shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211703592 | 10/02/2025 | 250 | F6.8841.../2420428 | Leakage Issue | Closed | Svasca Industries ( Ind) Ltd | Paluck Technologies Ltd. - Faridabad | 59 | oil leakage from Engine TC oil drain supply pipe hose clamp open tightness the same then issue resolve (CSP done on 29/12/2024) | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211702172 | 10/02/2025 | 20 | GP3.1021.../2420343 | DG Issue | Closed | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - BIKANER | 50.65 | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | South | 211709342 | 12/02/2025 | 15 | GP3.8501.../2421722 | Oil Leakage problem Call by : Customer Name : Ramesh Contact : 9704302507 | Task Start | M/S GUNTUR RAMESH FUELS | Ultimate Power Source - Tirupati | 67 | Oil leakage isuue found sump drain bolt loose tighten the same | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211673520 | 01/02/2025 | 58.5 | T4.8941.../2420951 | Starting/Stopping Issue | Open | B. A. C. Infratech Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Guwahati | 960 | Update Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | South | 211709185 | 12/02/2025 | 25 | GP3.8702.../2420371 | fuel level guage issue | Task Start | Muralya Dairy Products Private Limited | Bharath Diesel Sales and Service - Dindigul | 89 | Fuel level variation issue Checked and found the fuel level Gauge connector side negative cable leg damaged condition So Diesel level gauge not properly working | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | South | 211707982 | 11/02/2025 | 35 | 3H.8902.../2421867 | Shutdown Alarm Issue Call By Customer Name :- TS Bahseer No :- 9744880980 | Task Start | T.S.Basheer & Co | G-Care Diesels Private Limited - Calicut | 53 | Attended the above mentioned site checked the health check up done then check the problem found alaram 157/14,change the wire 2A1(1sq to 2.5sq),all electrcal connectiontighted trail running done confirm that the dg performance is good and working parameters are within the operation limit.overall engine performance is good | Closed | Mr. Sanjaimon S | Detail to be share | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | South | 211707769 | 11/02/2025 | 82.5 | 5H.8901.../2420653 | Starting Problem Call by : KGD Name : Harsha Contact : 9176923123 KGD contact No : 9347338159 | Closed | M/S.BALAJIHOSPITAL | Ultimate Power Source - Tirupati | 1 | Cleared the alaram . All the parameters are running good condition no issue | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | South | 211707396 | 11/02/2025 | 30 | 3H.8902.../2420966 | Automation Issue Call By Customer Name :- Mobile No :- | Open | Pampapathi | Vijayshree Diesel Sales and Service - Bellary | 151 | Customer side automation issue. | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
29 | South | 211706197 | 11/02/2025 | 15 | GP3.8501.../2420947 | Electrical-engine not starting | Closed | SRI PALANIMURUGAN TYRES | Bharath Diesel Sales and Service - Salem | 17 | Inspect the engine not starting reason for control board on and off switch cable loose ( 2b and 2e) . control board working start the engine running normal | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | South | 211705978 | 11/02/2025 | 320 | F6.8802.../2420124 | Leakage Issue | Task Start | TALIPARAMBA CO-OPERATIVE HOSPITAL SOCIETY LTD. | G-Care Diesels Private Limited - Kannur | 51.4 | Visited the site found oil leakage from oil transfer adaptor then change oil transfer adaptor O ring then start the engine leakage not stopped | Task Start | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211678675 | 03/02/2025 | 160 | 6H.8475.../2420162 | V Belt found loose & Preventive Maintenance Email By - GOEM Name - Arup Kr. Ray | Task Start | Ms Ankur Enterprise | Hibreed Engineering Pvt. Ltd. - Nagaon | 196 | Eye bolt broken (Update Pending) | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211679333 | 03/02/2025 | 40 | 3H.8951.../2420560 | KRM App Issue Call By Customer Name :- Shankar Kumar Mobile No :- 9835666455 | Task Start | Usha Singh | Globalline India Services Private Limited - Patna | 143 | Update pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
36 | South | 211705128 | 11/02/2025 | 250 | F6.8842.C4../2420022 | Load problem Call by : Customer Name : Girish Contact : 9948977010 | Closed | Adishwar Auto Diagnostics Pvt Ltd | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 6.23 | update pending | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | South | 211704824 | 11/02/2025 | 160 | 6H.8475.../2420282 | Sound/Vibration Issue | Closed | RANGA NEURO MULTISPECIALITY | Bharath Diesel Sales and Service - Dharmapuri | 100 | 1761/16 adblue level low.Top up the same | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211667228 | 31/01/2025 | 30 | 3H.8902.../2420405 | Auto Starting Issue Call By Customer Name ;- Ataullah ANSARI No :- 9870040345 | Task Start | M/s. Grace Urban Devlopment Corporation. | Globalline India Services Private Limited - Muzaffarpur | 192 | loose wiring connection (as per fsr) update pending at SE end | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | South | 211703551 | 10/02/2025 | 250 | F6.8841.../2420329 | Starting/Stopping Issue | Closed | Hansa Products | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 12 | start relay wire loose connection. retight the same | Closed | Mr. MD Saleem | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
4 | East | 211673172 | 03/02/2025 | 40 | 3H.8951.../2420658 | Coolant issue & silencer issue Call by customer Name - Jamshed Ansari Number - 7478587172 | Task Start | Raja Soft Coke | Revenus Industries Pvt. Ltd. - Asansol | 89 | Today SE will visit site | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
42 | South | 211702064 | 10/02/2025 | 200 | 6H.8435.../2420100 | Project Lamp On Alarm And Starting Issue Call By Customer Name :- Mohammad Rafik Mobile No :-9080187879 | Closed | Balan | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 37 | replaced new start Stop relay and start running condition dg sound and smoking is normal | Closed | Mr. NandhaGopal | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
3 | East | 211673465 | 01/02/2025 | 30 | 3H.8902.../2420243 | Starting Issue Call By Customer Name :- MITESH AGRAWAL Mobile No :-7894071139 | Closed | Arati Agrawal. | Gangpur Sales and Services - Bolangir | 57 | Update pending | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211673896 | 01/02/2025 | 58.5 | T4.8941.../2423028 | Leakage Issue | Closed | ENVYNN CLIMATECH SOLUTIONS PRIVATE LIMITED | Revenus Industries Pvt. Ltd. - Hooghly | 512 | There was oil seepage at drain plug banjo bolt washer due to worn out so replace copper washer then also oil service done by changing the oil and filters (oil, fuel) due to service needed. Then start and observe all parameters found engine runs normal and Leakage problem solved. | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | South | 211701783 | 10/02/2025 | 82.5 | 5H.8901.../2420330 | Starting Problem Call by : Customer Name :Shambi Contact :9535759530 | Open | Shri Pinaki Ashrama Seva Samithi | Vijayshree Diesel Sales and Service - Bellary |  | Dealer in transition | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
46 | South | 211700836 | 10/02/2025 | 125.4 | 4H.8042.C4../2420160 | Oil Leakage Problem Call by : Customer Name : Dinesh Contact :9791220392 | Completed | Maxivision Eye Hospitals Private Limited | Bharath Diesel Sales and Service - Kumbakonam | 35 | Checked found oil leakage complete due oil sump drain nut area cracked. so replace the new oil sump. | Completed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
48 | South | 211699430 | 10/02/2025 | 20 | GP3.8601.../2420466 | Leakage Issue | Closed | Dileep Andalamala | Surya Power Services - Bangalore | 85 | As per the customer complaint visit the site dg not starting.check the dg and observe the problem.the problem was water in exhaust silencer dg running back pressure then dg not running .remove the silencer pipe then started the engine running ok.need to be clean the silencer | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
52 | South | 211699224 | 10/02/2025 | 30 | 3H.8902.../2421896 | Starting Problem & Display Showing "Emergency Stop" Call by : Customer Name :Niviya Contact :9539777719 | Closed | KAVITHA ENGINEERING & CONTRACTORS | Electro Controls - Alappuzha | 13 | Attended the site check the engine emergency switch 1c wire loose problem resetting emergency switch 1c wire problem solving engine Star and Stop and emergency stopping working ok belt tensioner ok hose and hose clips ok | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
55 | South | 211698889 | 10/02/2025 | 15 | GP3.8501.../2420865 | Automation issue Call By Customer Name :-Kavita Bhatia Mobile No :-9513902829 | Closed | Kavita Bhatia | Surya Power Services - Kalyan Nagar | 97 | As per the customer complaint check the engine properly. Problem found in diesel suction line. From filter to fip So remove the all diesel line and reconnect properly. Check the all parameters of engine found ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
56 | South | 211698893 | 10/02/2025 | 82.5 | 5H.8901.../2420573 | Electrical Problems | Task Start | Sachin S.N. | Prasad Power Engineers - Udupi | 5 | DM1 - 3031/15,1761/16,3364/29,3364/10,3364/27,520527/18,3031/1,522120/10,522122/19,3224/2, DM2 -520527/16,4365/2. Replaced the 13RB1 relay board.Now working ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
58 | South | 211697437 | 08/02/2025 | 15 | GP3.8501.../2421401 | Automation issue Call By Customer Name :-AJOMON JOSEPH Mobile No :-9400181789 | Closed | AJOMON JOSEPH | Electro Controls - Thodupuzha | 12 | Temprature switch is loose. display showing high temperature. Checked all parameters found that temperature switch is loose . Check all wires found that wire and temperature switch is loose. Corrected the problem. Engine running good condition. No active problems | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211678645 | 03/02/2025 | 20 | GP3.8601.../2320037 | Abnormal sounds | Task Start | Anju Manyara Bibi | Revenus Industries Pvt. Ltd. - Berhampore | 55 | Today SE will visit site | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
40 | South | 211702449 | 10/02/2025 | 40 | 3H.8951.../2420869 | Starting Problem Call by : Customer Name : Sunil Contact : 9000002011 | Task Start | Sri Ranga Sai Food | Prasad Power Engineers - Chithradurga | 51 | Visit the site check the generator panel board insid fuse burning replace the new fusenow dg runing check the oil level check the air filter check the battery terminal check the battery distil water check the all parameter | Closed | Mr. NandhaGopal | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
13 | East | 211665887 | 31/01/2025 | 35 | 3H.8902.../2420344 | starting issue Email By - OEM Name -Neeraj Mishra | Task Start | Safe Decor | Globalline India Services Private Limited - Patna | 40 | DG was running on mannual mode but in Auto mode it fails to start so tighten the same | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211711069 | 12/02/2025 | 250 | F6.8841.../2420210 | OutputIssue Email By - GOEM Name - M.K.GURUMURTHY | Open | Rinac India Limited | Surya Power Services - Peenya, Bangalore |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211711784 | 13/02/2025 | 125.4 | 4H.8042.C4../2420371 | Inspection/Maintenance | Open | AIRPLAZA RETAIL HOLDINGS PRIVATE LIMITED | Surya Power Services - Mysuru |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | North | 211701933 | 10/02/2025 | 320 | F6.8802.../2420127 | VOC -ENGINE NOT TAKING LOAD DUE TO FAILURE OF NON RETURN VALVE IN FUEL LINE Customer Name - Kanhaiya Prajapati Customer Number -8890980358 Mode- SR Generated through CDI calling. | Closed | VIKAS POLYPLAST PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Alwar | 24 | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
35 | North | 211711169 | 12/02/2025 | 40 | 3H.8951.../2420285 | Tripping issue Called by customer Name :Balvindra Number : 8053458790 | Open | Asger Agro Pvt. Ltd. | Vidyut Engineers - New Delhi |  | Visit Pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
36 | North | 211711011 | 12/02/2025 | 160 | 6H.8475.../2420203 | Electrical Problems | Completed | HOTEL AVINASH | S.S. Enterprises - Sonbhadra |  | Visit Pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | North | 211709942 | 12/02/2025 | 58.5 | T4.8941.../2423262 | AMF Panel Fitting Issue. Call By Customer. Name:- Vikaram Singh. Mobile No.:8168436193 | Closed | V.S ELECTRICALS & POWER SOLUTIONS | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 331 | Customer want to Dg in Auto so, Connection done | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | North | 211709821 | 12/02/2025 | 125 | F6.9840.../2420031 | Automation and Under Speed Alarm issue Call By Customer Name :- Durgesh Awasthi Mobile No :- 9602907049 | Closed | UNIQUE POWER SOLUTION. | Vidyut Engineers - Noida | 21 | Found Gas filter was chocked due to trash & clean the filter | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211709723 | 12/02/2025 | 125.4 | 4H.8041.../2420452 | Leakage Issue | Closed | Aadya Industries. | Espiem Engines & Machines (P) Limited - Agra | 612 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
40 | North | 211709580 | 12/02/2025 | 40 | 3H.8951.../2421307 | Starting Issue Call By Customer Name :-Anil Kumar Mobile No :- 9671464299 | Closed | ANIL KUMAR GENSET | Paluck Technologies Ltd. - Gurgaon | 128 | Found 12RB1 relay was foulty so, replace the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
41 | North | 211709578 | 12/02/2025 | 125.4 | 4H.8041.../2420625 | Starting issue Call By Customer Name :- Akash Mobile No :- 9910337157 | Closed | RAO SCAFFOLDING | Paluck Technologies Ltd. - Gurgaon | 206 | update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
42 | North | 211709509 | 12/02/2025 | 200 | 6H.8435.../2420093 | DG not working properly | Open | RELIANCE PROJECTS & PROPERTY MANAGEMENT SERVICES LIMITED | Espiem Engines & Machines (P) Limited - Aligarh |  | Visit Pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211709481 | 12/02/2025 | 58.5 | T4.8941.../2420760 | Starting/Stopping Issue | Closed | Welcome Battery House. | Pratap Diesels Pvt. Ltd. - Bharatpur | 131 | Found Electrolite level low, toup the Electrolite after that issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
44 | North | 211709191 | 12/02/2025 | 40 | 3H.8951.../2420266 | Flickering | Closed | Kamla eye foundation pvt ltd | OVN Industries Private Limited - New Delhi | 9 | Found Control panel wire was loose so, tightness the same | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | North | 211709052 | 12/02/2025 | 125.4 | 4H.8041.../2420135 | Starting Issue Call By Customer Name : KUMAR VISHWAS No : 9911669257 | Closed | B & B GROWING PROMOTERS PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 263 | Emergency alarm reset | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
46 | North | 211708989 | 12/02/2025 | 58.5 | T4.8941.../2422602 | JOB WORK | Completed | THE GREEN VALLEY HOTEL & RESORT | S. R Engines Sales And Service - Gorakhpur | 8 | Visit the site connect the automation wire, with dg panel to auto panel, connect dg mains load cable then start dg | Closed | Sudhir Awasthi | [9 empty] | Auto Panel | 6 | 5 | 3 | 90 | Low
2 | West | 211679330 | 03/02/2025 | 58.5 | T4.8941.../2422032 | Black smock issue Call By Customer Name :-Sohail Diwan Mobile No :- 8153053986 | Closed | Mom DJ. Sound | Unique Techno Services Pvt Ltd. - Anand | 36 | Smoke issue, Vaccum indicator was showing RED band so opened the air filter hose and found polytheen in hose. | Closed | Amit shandilya | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
48 | North | 211711220 | 12/02/2025 | 40 | 3H.8951.../2420854 | Starting/Stopping Issue | Open | Malhotra Bone Joint Sugical Center and Multispeciality Clinic. | Industrial Power Solutions - LUDHIANA | 1.95 | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
49 | North | 211710896 | 12/02/2025 | 82.5 | 5H.8901.../2420192 | Electrical Problems | Task Start | Zudio Yamuna Nagar | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 57.81 | Update pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
50 | North | 211707354 | 11/02/2025 | 2.8 | AP1.7003.../2400026 | Loading issue Called by customer Name : SUNIL KUMAR Number : 8590600447 | Open | SUNIL KUMAR 1 | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211706081 | 11/02/2025 | 30 | 3H.8902.../2420729 | DG Issue | Open | Axis Bank Ltd | HACS Engineering and Tech Private Limited - Deoghar |  | visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211705995 | 11/02/2025 | 82.5 | 5H.8901.../2420734 | Automation issue Call by Customer Name : Vishwajit .. No : 7485881929 | Task Start | KALYAN JEWELLERS.. | Globalline India Services Private Limited - Gaya |  | Customer auto pannel side issue and SE statisfied with it. No issue was in DG it was running properly (issue was regarding auto mode that DG Start in auto mode but shtudown after 10-20 min so SE recommed to test their auto panel) | OPEN | Prabhakar Kumar | [9 empty] | Auto Panel | 6 | 5 | 3 | 90 | Low
4 | East | 211704976 | 11/02/2025 | 20 | GP3.8604.../2420062 | INSTANCE ID:-100740972 SITE ID:-I-BR-SIMR-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-Anuj Kumar NUMBER:-8084447706 | Task Close | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211703705 | 10/02/2025 | 45 | 3H.8951.../2421641 | Starting issue Called by customer Name : Prabhakar Number : 8709322290 | Open | N D Mart | HACS Engineering and Tech Private Limited - Deoghar | 242 | visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211698974 | 10/02/2025 | 45 | 3H.8951.../2520085 | Door Lock Issue And emergency Stop Alarm Issue Call By KGD Name ;Sheetal Gupta no :6299024030 | Task Start | Jai Prakash Kesari. . | HACS Engineering and Tech Private Limited - Hazaribagh | 64 | update pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211709225 | 12/02/2025 | 20 | GP3.8601.../2421566 | CHARGING ALTERNATOR FAULTY | Task Start | MULNIVASI FILLING STATION | Gangpur Sales and Services - BHUBANESWAR | 2.3 | update pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211710898 | 12/02/2025 | 125 |  | Fan pulley broken | open | National Highways Infra Projects Pvt. Ltd. | Hibreed Engineering Pvt. Ltd. - Bongaigaon | 0 | Line rejection- at the time of commissioning on trail found pully having radial play so checked found belt tension ok but the pulley having play due to improper assembly of fan pulley, after removing found that pulley,s center bolt was rotating which lead and radial play, need to replace the fan pulley. | OPEN | Ujjwal Das | Failed part | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | South | 211711909 | 13/02/2025 | 0 | F6.8842.C4../2420110 | COOLANT LEAKAGE FROM COOLER HEADER | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected the dg noticed the oil leak for cooler head, dismantle the cooler head noticed the oring damage, change the new oring solve the oil leakage issue | Task Start | Mr. NandhaGopal | Plant issue | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211711859 | 13/02/2025 | 160 | 6H.8475.../2420404 | Starting Problem Call by : Customer Name :Sanoy Contact :9074580156 | Task Start | Zaitoon Global Private Limited | Madhu Engineering Sales & Service - Teynampet,Chennai | 5 | Visited the site customer above customer complaint for engine not starting check the engine only cranking not pick-up check the control panel relay failure so engine not pick-up k88 ,2A6,2A8 | Closed | Mr. NandhaGopal | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
4 | South | 211711820 | 13/02/2025 | 20 | GP3.8601.../2421153 | Error problem Call by : Customer Name :Rahul Contact :9020780320 | Open | Ananda fuels | EMKAY MOTORS - Kollam |  | Visit pending | Task Start | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211693752 | 07/02/2025 | 250 | F6.8841.../2420383 | Door Lock & Tank Lock Issue Call By Customer Name :- Manoj Mobile No :-9065620515 | Closed | Mithila Earthing Solutions | Globalline India Services Private Limited - Patna | 8 | Customer's complain was related door lock issue. SE tried to satisfy the customer and educate how to close door but he doesnot statisfied with him. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
44 | North | 211674610 | 01/02/2025 | 40 | 3H.8951.../2420008 | Red Lamp Issue Call By Customer Name - ROHIT NAV Number - 7206450008 | Closed | R S UDHYOG | SAAN Royal Power Solutions Private Limited - Rohtak | 52 | Starting issue due to positive wire found loose so tightened the same & resolve the Issue (Update Pending) | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211681711 | 04/02/2025 | 320 | F6.8802.../2420259 | Trip_Genset_Low_Voltage | Closed | Budhiraja Electricals | Deep Jyoti Electricals and Services - Haldwani | 38.8 | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
74 | North | 211684408 | 05/02/2025 | 320 | F6.8802.../2420279 | Tripping Issue Call By Customer Name :- Jatin Bhardwaj Mobile No:-9541242592 | Closed | Orchid Hospitality Services Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Rohtak | 72 | AdBlue Level found 0% on site so Top-up the same & educate to customerregarding same | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | South | 211688882 | 06/02/2025 | 5.5 | CC1.1013.../2400294 | Display Not Seen Problem Call by : Customer Name :ABHILASH Contact :9744401069 | Open | TRIPTHI SALES CORPORATION | G-Care Diesels Private Limited - Kannur |  | Visit pending | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211688844 | 06/02/2025 | 5.5 | CC1.1013.../2400363 | Starting Problem &Alarm Problem Call by : Customer Name :Kirubanathan Contact :9841244023 | Open | Dr Rajini | Bharath Diesel Sales and Service - Puducherry | 9.5 | Checked the engine and noticed the engine due to service maintenance Alarm and informed to customers side and turn off the maintenance alarm and quotation summited for wet service | Closed | Mr. NandhaGopal | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
4 | South | 211688584 | 06/02/2025 | 40 | 3H.8951.../2420593 | Starting Problem Call by : Customer Name : Praneeth Contact : 7700957641 | Task Start | Axis Bank Ltd | Powerlinks Infra Tech Pvt Ltd - Secunderabad |  | Visit pending | Tast Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211683554 | 04/02/2025 | 15 | GP3.8501.../2421018 | Power supply problem & out put problem Call by : Customer Name : Chandrashekhar Contact : 9963722598 | Open | SRI SAI BAJRANG PETRO FILL | Powerlinks Infra Tech Pvt Ltd - L B Nagar |  | Visit pending | Open | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211688594 | 06/02/2025 | 250 | F6.8841.../2420273 | Leakage Issue | Task Start | Urban Sanctuary LLP. | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 213.3 | Diesel Leakage due to overflow in tank. Customer side issue. | Tast Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211688529 | 06/02/2025 | 58.5 | T4.8941.../2421244 | CONTROLLER DISPLAY COMPLAINT | Task Start | KAILASAM ESTATE | Electro Controls - Palakkad | LR | Visit the site checked everything system wise found control board display not working so need to replaced immediately. Photo | Tast Start | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | South | 211688412 | 06/02/2025 | 25 | GP3.8702.../2421238 | Automation Issue | Open | ATC Telecom Infrastructure Private Limited | Net Work Diesels - Potheri |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211688386 | 06/02/2025 | 25 | GP3.8702.../2421518 | DG Not Start | Task Start | ATC Telecom Infrastructure Private Limited | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 1.33 | Visit the above customer site the engine check the auto sensing not given by customer end and give the auto sensing, check the auto mode and manual mode working properly finally starting the engine found ok. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211683813 | 05/02/2025 | 25 | GP3.8702.../2421634 | Under Speed Alarm Issue & Automation Issue Call By Customer Name - Kumar Number - 7025086344 | Open | Senthil | Electro Controls - Kattappana |  | Visit pending | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | South | 211688208 | 06/02/2025 | 125.4 | 4H.8041.../2420568 | Error code issue Call By Customer Name :-Ravi Patel Mobile No :- 9925372802 | Open | VIPUL BUILDCON | Electro Controls - Marthandam |  | Visit pending | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | South | 211688088 | 06/02/2025 | 500 | DV8.8501.C4../2420094 | Barty issue Call By Customer Name :- Udaykumar . Mobile No 7090248309 | Task Start | TTP. Technologies | Prasad Power Engineers - Tumkur |  | Visit pending | Tast Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | South | 211684294 | 05/02/2025 | 125.4 | 4H.8041.../2420463 | Tripping Issue Call By Customer Name :- Kanan . Mobile No :-9840638763 | Open | Sonder Groups | Bharath Diesel Sales and Service - Chennai |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | West | 211681660 | 04/02/2025 | 30 | 3H.8902.../2421782 | ENGINER AUTO STARTING ISSUE | Closed | ATC Telecom Infrastructure Private Limited | Unique Techno Services Pvt Ltd. - Ahmedabad | LR | The genset was not starting in auto mode so remote start wire was provided. | Closed | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | South | 211687904 | 06/02/2025 | 125.4 | 4H.8042.C4../2420836 | Starting Problem Call by : Customer Name :Joshy Contact :9249579017 | Task Start | Hyson Motors | G-Care Diesels Private Limited - Thrissur |  | Visit pending | Tast Start | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | South | 211685719 | 05/02/2025 | 30 | 3H.8902.../2421554 | Stpping problem Call by : Customer Name :Manjunath Gatti Contact :8050063004 8050063004 Girish kulkarni 9845955111 | Open | Rashtrotthana Vidya Kendra | Vijayshree Diesel Sales and Service - Bagalkot |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | South | 211685494 | 05/02/2025 | 82.5 | 5H.8901.../2420039 | Starting Problem Call by : Customer Name : Chandu Contact : 9951893714 | Open | Baba Infra and Developers | Powerlinks Infra Tech Pvt Ltd - Secunderabad |  | Visit pending | Open | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | South | 211685264 | 05/02/2025 | 20 | GP3.8601.../2420504 | Starting/Stopping Issue | Closed | Mrs. Kavitha. | G-Care Diesels Private Limited - Calicut | 38 | Found diesel filter down washer side leakage tighten the same issue resolved | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | South | 211685173 | 05/02/2025 | 25 | GP3.8702.../2421457 | Battery Under Voltage Problem Call by : Customer Name :Sajin Contact :8943693555 | Closed | Muralya Dairy Products Pvt. Ltd. | Electro Controls - Thiruvananthapuram | 8 | Attend the site mains R phase fuse burned, so the battery charger output nil and battery voltage very low so replaced the fuse and started the dg load tested ok | Closed | Mr. Sanjaimon S | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
1 | East | 211690602 | 06/02/2025 | 20 | GP3.8601.../2421228 | Starting Issue & KRM Issue. Call By KGD. Name:-Sahil Mobile No.:-7909030218 | Open | Shakuntala Mart | Globalline India Services Private Limited - Patna | 25 | Visit Pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211684382 | 05/02/2025 | 20 | GP3.8601.../2420918 | Genset Trip | Task Start | SRI LAKSHMI VENKATESHWARA FUEL PARK | Surya Power Services - Kolar | 71 | Engine not starting due to alarm of speed sensor fault so checked all parameters found K4 speed sensor wire loosed condition so corrected the problem | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211686500 | 05/02/2025 | 30 | 3H.8902.../2422023 | Automation Issue Email By - KGD Name - Arup Kr. Ray | Open | M/S F. DKHAR AUTOMOBILE SPARE PARTS | Hibreed Engineering Pvt. Ltd. - Guwahati |  | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211686223 | 05/02/2025 | 25 | GP3.8702.../2421160 | Starting issue Called by customer Name : Amit Number : 8800309146 | Task Start | SMT MANORMA SINGH | Globalline India Services Private Limited - Biharsharif | 7.1 | Visit Pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211685760 | 05/02/2025 | 25 | GP3.8702.../2421218 | Auto panel issue Call By KGD Name :-Kumkum Neha Mobile No :- 9234456624 | Open | JAIN PETROL SUPPLY COMPANY | HACS Engineering and Tech Private Limited - Hazaribagh | 66 | door lock issue and 2791/17 alarm was showing after that SE flashing the dummy file,Issue resolved | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211685154 | 05/02/2025 | 20 | GP3.8604.../2420110 | RPM Issue | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Bhagalpur |  | Update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | East | 211685147 | 05/02/2025 | 58.5 | T4.8941.../2420403 | Under Speed Alarm Call By Customer Name :- Ravi Kumar Mobile No :-9934852155 | Task Start | Ravi Soni | Globalline India Services Private Limited - Muzaffarpur | 149 | Today SE will Visit site | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211684917 | 05/02/2025 | 5.5 | CC1.1013.../2400016 | Starting Issue Call By Customer Name :- Shakti Kumar Mobile No:-6294815565 | Open | East Coast Railway Andhra Pradesh | HACS Engineering and Tech Private Limited - Deoghar |  | Visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | South | 211687098 | 06/02/2025 | 20 | GP3.8601.../2421902 | Under Voltage Alarm Issue Call By Customer Name :- Karthik Prakash Mobile No :- 7348832292 | Open | A DARK FAMILY RESTAURANT | Surya Power Services - Peenya, Bangalore | 35.5 | Found fuel level low alarm so topup the fuel start the engine running ok | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211678007 | 03/02/2025 | 125.4 | 4H.8042.C4../2420815 | Starting/Stopping Issue | Open | Sailaja Commercial Construction Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 44 | Attended the site check the engine and check urea tank in urea found high level. Also check alarm DM 2 516166/0, 3031/14, 4095/1 and 6595/0. So drain the urea and set 81.60 level and clear the all code. After that started the engine good running and 2 hours load testing and check Relative Urea Pump Module Pressure 5005 hpa and Adblue dosing quantity 1109032217 mg/s | OPEN | Ujjwal Das | KRM Check | [8 empty] | Load Test | 5 | 4 | 3 | 60 | Low
8 | West | 211681788 | 04/02/2025 | 160 | 6H.8475.../2420390 | V belt Issue | Task Start | Conmix Infra | Unique Techno Services Pvt Ltd. - Dahej | 44 | V belt loose so tightened the same. | Closed | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | West | 211637917 | 24/01/2025 | 20 | GP3.1021.../2420178 | DG Under Volt Alarm | Task Start | Reliance Jio Infocomm Limited | KALA Care Global LLP - Aurangabad | 1557 | Under voltage issue still solution is not given to the field | OPEN | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | South | 211681725 | 04/02/2025 | 30 | 3H.8902.../2422376 | Starting/Stopping Issue | Task Start | dr.kh.vasudeva naidu | Ultimate Power Source - Tirupati |  | 2791/18, 5838/1 Fault code issue. | Tast Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211685339 | 05/02/2025 | 125.4 | 4H.8041.../2420197 | Oil issue & hunting issue Call By Customer Name :-Lalit Tyagi Mobile No :- 9810138700 | Task Start | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad | 1969 | Oil level is low, Found no leakage so, change the filter & oil because customer gives the spare parts - Under observation | Under Monitoring | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211685308 | 05/02/2025 | 25 | GP3.8702.../2421228 | under sapped issue Call By Customer Name :- Dipak Mobile No :-9548543079 | Task Start | V6 WAREHOUSING LLP | Vidyut Engineers - Noida | 217 | DG trip with under speed, Check then Found Customer side wire was short so, DG trip Customer self correct the wire then issue was resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | North | 211685305 | 05/02/2025 | 125.4 | 4H.8041.../2420205 | Automation Issue Call By Customer Name - Vandit Garg Number - 7536033334 | Task Start | Modi Mundipharma Pvt. Ltd. | R K Engineers - Meerut | 3.3 | Found High adblue alarm Flash the file then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211685284 | 05/02/2025 | 125.4 | 4H.8041.../2420660 | Genset Tabit cover leakage Call By Customer . Name:-Lalit Tyagi Mobi | Task Start | Sgs Diesel Power And Heavy Electrical. | Vidyut Engineers - Noida | 30.49 | Wrong report SR-Check & Found no any leakge in Engine | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | North | 211684959 | 05/02/2025 | 45 | 3H.8951.../2421695 | Automation Issue Call By Customer Name :- Mukesh Sharma Mobile No:-9829296566 | Task Start | Gaurannga Institute For Vedic Education | Espiem Engines & Machines (P) Limited - Agra | 213 | DG Contactor not to be hold on Auto because Auto panel distance from DG Approx 600 to 700 meter., So, Engineer educate the customer kindly panel set to near the DG | Closed | Sudhir Awasthi | [9 empty] | Auto Panel | 6 | 5 | 3 | 90 | Low
13 | North | 211683853 | 05/02/2025 | 320 | F6.8802.../2420330 | Starting/Stopping Issue | Closed | Hirohama India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 97.3 | DG MCB 2C wire was loose, tightness the same - Jackson panel | Closed | Gourav Sharma | [9 empty] | MCB | 5 | 4 | 3 | 60 | Low
14 | North | 211680913 | 04/02/2025 | 30 | 3H.8902.../2420488 | Abnormal Sound Issue Email By - KGD Name - JITENDRA GAJJA | Task Start | MARBLEX | Pratap Diesels Pvt. Ltd. - BIKANER | 2.24 | Engineer visit on site check the Dg found no any issue related sound, DG running well | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211681705 | 04/02/2025 | 320 | F6.8802.../2420073 | Door Lock Issue Coolant Leakage Issue & Coolant Lid Issue Call By Customer Name :- Rishi Pal Mobile No :- 7838955880 | Open | A.G. Pipes Pvt. LTD. | Paluck Technologies Ltd. - Faridabad |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211683081 | 04/02/2025 | 125.4 | 4H.8042.C4../2420757 | Automation Issue Call By Customer Name :- Sabastin .. Mobile No:-9810878972 | Open | Sanghamitra Apartment | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211682839 | 04/02/2025 | 58.5 | T4.8941.../2421074 | Abnormal Sound Issue Email By KGD Name:-Sagar Chopra | Open | Rural Development Department Uttar Pradesh. | S.S. Enterprises - Chunar - Mirzapur | 53 | Check the DG sound with Sound level meter Found 75 to 76 DB | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211681836 | 04/02/2025 | 30 | 3H.8902.../2421851 | VOC - WIRING CONNECTIONS LOOSE OF CONTROL PANEL Customer Name -Sandeep Pandey Customer Number -8127450229 Mode- SR Generated through CDI calling. | Open | ATC Telecom Infrastructure Private Limited | S. R Engines Sales And Service - Gorakhpur |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | West | 211683886 | 05/02/2025 | 58.5 | T4.8941.../2422038 | Leakage Issue | Closed | Heritage Resort Dholavira | Unique Techno Services Pvt Ltd. - Gandhidham | 42 | Oil leakage from oil drain plug and lube oil sensor so tightened the same and resolved the issue. | Closed | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211683984 | 05/02/2025 | 25 | GP3.8702.../2420138 | Genset Trip | Task Start | Himanshu Pradhan | HACS Engineering and Tech Private Limited - Jamshedpur | 505 | DG was not starting showing Emergency alarm so check all connections related to emergency Reconnect connetor properly after that tighten the emergency switch connection properly after that start the DG started. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211685760 | 05/02/2025 | 25 | GP3.8702.../2421218 | Auto panel issue Call By KGD Name :-Kumkum Neha Mobile No :- 9234456624 | Open | JAIN PETROL SUPPLY COMPANY | HACS Engineering and Tech Private Limited - Hazaribagh | 66 | Today SE will visit site | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211685154 | 05/02/2025 | 20 | GP3.8604.../2420110 | RPM Issue | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Bhagalpur |  | Update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211685147 | 05/02/2025 | 58.5 | T4.8941.../2420403 | Under Speed Alarm Call By Customer Name :- Ravi Kumar Mobile No :-9934852155 | Task Start | Ravi Soni | Globalline India Services Private Limited - Muzaffarpur |  | Today SE will Visit site | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | East | 211684917 | 05/02/2025 | 5.5 | CC1.1013.../2400016 | Starting Issue Call By Customer Name :- Shakti Kumar Mobile No:-6294815565 | Open | East Coast Railway Andhra Pradesh | HACS Engineering and Tech Private Limited - Deoghar |  | Visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211678007 | 03/02/2025 | 125.4 | 4H.8042.C4../2420815 | Starting/Stopping Issue | Open | Sailaja Commercial Construction Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 39 | Visit pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211681887 | 04/02/2025 | 15 | GP3.8501.../2421660 | Red Lamp ON Alarm Issue Call By Customer Name - Shams Number - 6200842634 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | HACS Engineering and Tech Private Limited - Ranchi | 27 | No issue was in DG only customers doubt was related to fuel level not decreasing and also emergency switch was pressed before visit on site operator released it, | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211685456 | 05/02/2025 | 320 | F6.8802.../2420079 | Starting Issue Call By Customer Name :-Nitu . Mobile No :- 9937413449 | Task Start | Puri Hotel Private Ltd | Gangpur Sales and Services - Puri | 45 | Today SE will visit site | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211682722 | 05/02/2025 | 25 | GP3.8702.../2421326 | Starting issue Call by Service Dealer Name:- Firod Kumar Mobile No - 9078630937 | Task Start | M/S Shree Mahavir Enterprises | Gangpur Sales and Services - Bhawanipatna | 34 | Today SE will visit site | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | East | 211681514 | 05/02/2025 | 7.5 | D3.8305.../2400158 | Maintenance Due Alarm Call By Customer Name :- Saurabh . Mobile No :-8609120321 | Closed | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - Angul | 56 | No issue in DG Customer required service | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | East | 211680240 | 06/02/2025 | 2.8 | AP1.7003.../2400155 | Starting Issue Email by KGD Name - PRADAN | Task Start | PRADAN | Gangpur Sales and Services - BHUBANESWAR | 10 | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | West | 211638282 | 24/01/2025 | 20 | GP3.1021.../2420185 | INSTANCE ID:-100748373 SITE ID:-I-MH-SATN-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- SOPAN NUMBER:- 9049618317 | Closed | Reliance Jio Infocomm Limited | Dhanashree Technocrats Pvt. Ltd. - Malegaon | 950 | Under voltage issue still solution is not given to the field | OPEN | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | West | 211638055 | 24/01/2025 | 30 | 3H.8902.../2420453 | Alternator issue | Closed | Kaushal K. Kapadia | Transcreek Engineers Pvt. Ltd. - Panvel | 20 | Main stator winding burn due neutral earthing is not connected properly, so repairing done on chargable basis. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211683846 | 05/02/2025 | 20 | GP3.8601.../2421238 | Starting Issue Email by KGD Name - sunrise power | Open | ROHIT KUMAR | Globalline India Services Private Limited - Darbhanga | 68 | update pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211690413 | 06/02/2025 | 40 | 3H.8951.../2420658 | VOC - Coolant issue & silencer issue Customer Name -Murtaza Ansari Customer Number -7478587172 Mode- SR Generated through CDI calling. | Open | Raja Soft Coke | Revenus Industries Pvt. Ltd. - Asansol | 57 | Visit pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211690057 | 06/02/2025 | 25 | GP3.8702.../2420136 | Coolant Leakage Issue Call By Customer Name :- Arun .. Number:- 7847955862 | Task Start | SAI UJWAL KSK | Gangpur Sales and Services - BHUBANESWAR | 117 | Visit pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211685456 | 05/02/2025 | 320 | F6.8802.../2420079 | Starting Issue Call By Customer Name :-Nitu . Mobile No :- 9937413449 | Closed | Puri Hotel Private Ltd | Gangpur Sales and Services - Puri | 4 | Low adblue level,SE will visit to educate the customer and filling up the adblue,Issue resolved. | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | North | 211693861 | 07/02/2025 | 30 | 3H.8902.../2420415 | White smoke issue Called by customer Name : Gopal Number : 8740979924 | Task Start | B. P. S. Products Private Limited. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 163 | Silencer cover welding was break, Engineer educate the customer for welding | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211693551 | 07/02/2025 | 40 | 3H.8951.../2420005 | Oil Leakage Issue | Task Start | Bharti Airtel ANG | Vidyut Engineers - Noida | 196 | update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211693459 | 07/02/2025 | 160 | 6H.8475.../2420031 | Fan Belt Broken Issue Call By Customer Name - Kunal Mobile No - 9318326116 | Task Start | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 2892.2 | found that eye bolt broken new 12mm stud welding on gearcasing. And refitted all accessories (Update pending) | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211693185 | 07/02/2025 | 125.4 | 4H.8041.../2420060 | Red Lamp Alaram Call By Customer Name :- Jagdish Yadav Mobile No :-9211308154 | Task Start | KEGGFARMS PVT. LTD. | Paluck Technologies Ltd. - Gurgaon | 272 | Update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211673759 | 01/02/2025 | 82.5 | 5H.8901.../2420441 | Written emergency stop | Closed | MAA KAPOOR BUILDERS AND DEVELOPERS LLP | Globalline India Services Private Limited - Gaya | 21 | When Fault code triggered on the display 516166 operator sudden push emergency switch, so SE visited and restore the issue by release the emergency switch and cleared fault code. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | North | 211692111 | 07/02/2025 | 125.4 | 4H.8041.../2420099 | Amber Lamp Alarm Issue Call By Customer Name :- Sumit Mobile No :-8295132515 | Task Start | MAA KAMAKHYA FERTILITY SOLUTIONS PVT. LTD. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211681458 | 04/02/2025 | 30 | 3H.8902.../2420583 | Leakage Issue | Task Start | Shine Enterprise | Green Powerline - Dhemaji | 243 | Today ASE is visiting the Site | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211681531 | 04/02/2025 | 45 | 3H.8951.../2420969 | SERVICE | Closed | SANGEETA MAM | Globalline India Services Private Limited - Patna | 19 | This DG's CC was not closed and when DG was not starting then customer tried to restore the DG by the help freelancer but they were fail to restore the DG then he register the complaint on helpdesk so dealer restore the DG on the paid basis after the ASM approval and also closed the CC SE found DG not starting so on inspection 2 no. cylinder exhaust pushrod bend and and turbo was clogged so replaced the pushrod and after clearing turbo refitted and issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211681692 | 04/02/2025 | 5.5 | CC1.1013.../2400156 | RPM Call By Service Dealer Name :- Yashika Mobile No :- 9693063331 | Task Start | Swapan Electrical. | HACS Engineering and Tech Private Limited - Jamshedpur | 937 | DG rpm was not exceding above the 2830-2840 and SE found speed adjusting lever screw lock seal was also broken, SE adjusted the level and RPM set to 2950 above this rpm was not increasing. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211681887 | 04/02/2025 | 15 | GP3.8501.../2421660 | Red Lamp ON Alarm Issue Call By Customer Name - Shams Number - 6200842634 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | HACS Engineering and Tech Private Limited - Ranchi | 27 | visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211689147 | 06/02/2025 | 125.4 | 4H.8042.C4../2420999 | Starting Issue Call By Customer Name :-Laxman .. Number:- 9891913259 | Task Start | Power Control System | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 8 | Check the panel connection tightness to be all then check & start the DG after that DG was start then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
34 | North | 211698050 | 09/02/2025 | 160 | 6H.8475.../2420225 | Oil Leakage Issue Call by Customer Name - Kartik Tyagi Mobile No - 9958362140 | Open | GROW MORE ENGINEERING COMPANY | Paluck Technologies Ltd. - Ghaziabad |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211693896 | 07/02/2025 | 20 | GP3.8601.../2420069 | Starting/Stopping Issue | Task Start | N. D. International Children School. | Excel Diesel Private Limited - Faizabad | 66 | update pending | open | Sudhir awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
35 | North | 211697405 | 08/02/2025 | 58.5 | T4.8941.../2422456 | Under speed alarm issue Called by customer Name : Bablu Number: 9958778186 | Open | JAGDAMBA GENERATOR SERVICE | Vidyut Engineers - Noida |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | North | 211695565 | 08/02/2025 | 20 | GP3.8601.../2320063 | Red Lamp Issue Call By Customer Name - Bharat Bhushan Number - 9810314268 | Closed | ASHA NAND SR. SEC. SCHOOL | Paluck Technologies Ltd. - Faridabad | 71 | Customer raise the complaint of starting issue but check the DG by SD Engineer Found No, any issue | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211683351 | 04/02/2025 | 15 | GP3.8501.../2422011 | oil leakage issue | Task Start | YUVRAJ TRADERS | Pratap Diesels Pvt. Ltd. - JAIPUR | LR-2 | Found Oil leakage from LN screw of Crankcase, SE change the washer but issue same | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
44 | North | 211695299 | 08/02/2025 | 40 | 3H.8951.../2420081 | expansion bellow change | Task Start | NEW BHARDWAJ ELECTRICAL WORKS | Paluck Technologies Ltd. - Faridabad | 412.13 | Engineer visit the site for change the Expension bellow, but he found the Exhaust silencer was damage so, bellow not change | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
50 | North | 211695053 | 08/02/2025 | 82.5 | 5H.8901.../2420347 | Auto Stopping issue Call By Customer Name :- Asad Bhatti Mobile No.:- 9968663656 | Closed | Annat C.G.H.S. Ltd. | OVN Industries Private Limited - New Delhi | 14 | found then engine controler wire loose R240 wire open and then wire tight all check proper and engine start and stop ok auto and Manuel | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211662002 | 30/01/2025 | 30 | 3H.8902.../2320151 | Leakage Issue | Closed | Saras Medical Services | OVN Industries Private Limited - New Delhi | 44 | Filter o' ring side leakage tightness the filter then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
54 | North | 211693008 | 07/02/2025 | 30 | 3H.8902.../2420951 | Starting/Stopping Issue | Task Start | Khalsa Construction Company | Gen Powers - Bathinda | 865.41 | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
57 | North | 211692274 | 07/02/2025 | 40 | 3H.8951.../2420941 | Starting/Stopping Issue | Closed | Brothers Genset Services | Gen Powers - PATIALA | 48 | Emergency switch alarm activated Genset control panel emergency swich wires 1H,10 and 1C2 checked & founs one wire broken on swich so connected the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
58 | North | 211692044 | 07/02/2025 | 15 | GP3.8501.../2421392 | Starting Issue | Task Start | Dynamics Solutions | Suraj Moters Stores - Leh |  | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
63 | North | 211688692 | 06/02/2025 | 40 | 3H.8951.../2420595 | Electrical Problems | Closed | Gurudwara Singh Sabha Talwandi. | Megatron Engineers - Hoshiarpur | 20 | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
66 | North | 211687498 | 06/02/2025 | 2.8 | AP1.7003.../2400026 | Starting/Stopping Issue | Open | SUNIL KUMAR 1 | SAAN Royal Power Solutions Private Limited - Zirakpur | 22 | Hunting issue found in DG so we change its carburetor and then start dg working ok | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
67 | North | 211686842 | 05/02/2025 | 15 | GP3.8501.../2421245 | Tripping issue Called by customer Name : Vijay Number : 9596287903 | Task Start | BHARAT GENERAL STORE | Suraj Motor Store - Jammu | 226.25 | Visit pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
69 | North | 211686405 | 05/02/2025 | 20 | GP3.8601.../2420237 | Starting issue Call By Customer Name :- Raju Mobile No :-7710590920 | Closed | SAI POWER ENGINEERS | Dynamic Engineering Services - Jalandhar | 36 | Emergency found pressed on site so release the same & same educated to customer | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | North | 211697009 | 08/02/2025 | 40 | 3H.8951.../2421608 | Starting issue Call by customer Name: Mahesh Gupta Number: 9810162611 | Closed | Mahesh Kumar Gupta | Vidyut Engineers - Noida | 13.58 | Found Emergency switch was pressed condition, realeased the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211667228 | 31/01/2025 | 30 | 3H.8902.../2420405 | Auto Starting Issue Call By Customer Name ;- Ataullah ANSARI No :- 9870040345 | Task Start | M/s. Grace Urban Devlopment Corporation. | Globalline India Services Private Limited - Muzaffarpur | 192 | There was an automation issue as on cutting of mains supply DG was not starting but in mannual DG was ok so after checking found mains voltage sensing wire was loose after tightening issue resolved. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211693952 | 07/02/2025 | 625 | DV0.8501.C4../2420049 | LINE REJECTION | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | 1 | Found relay card foulty, need to be replace | Closed | Gourav Sharma | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
11 | North | 211686293 | 05/02/2025 | 625 | DV0.8501.C4../2420014 | Abnormal Sound Issue Email By - GOEM Name - Sagar Chopra | Open | T. C. Health Care Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad |  | visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | WEST | 211678433 | 03/02/2025 | 82.5 | 5H.8901.../2420318 | Amber Lamp On Alaram & Under Speed Alarm Call By Customer. Name:-Ravi Narayan Raut Mobile No :-7440998052 | Task Start | Exotic Hospitality | Natraj Power Tech - Betul | 300 | Low adblue level so top up adblue. | Closed | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | WEST | 211684152 | 05/02/2025 | 40 | 3H.8951.../2421659 | Stopping Issue Email By - KGD Name -Poonam Shedage | Closed | Blinkit. . | Transcreek Engineers Pvt. Ltd. - Panvel | 20 | customer side issue. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211684957 | 05/02/2025 | 25 | GP3.8702.../2420200 | Starting/Stopping Issue | Task Start | K. M. E. S. Institution of Education. | Prasad Power Engineers - Karakala |  | Visit pending | Tast Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | WEST | 211684593 | 05/02/2025 | 320 | F6.8802.../2320009 | Black smoke problem | Closed | The Bishops CO-ED. School | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 261 | no issue found | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | West | 211642869 | 25/01/2025 | 58.5 | T4.8941.../2422973 | Error Code Issue And MIL Lamp On Alarm Call By Customer Name :- Nikhi Mobile No :-9823983099 | Task Start | OMKAR ENTERPRISES | Transcreek Engineers Pvt. Ltd. - Wadkhal |  | 97/5 self testing failed, found wire interchanged in XDBK . | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | West | 211638282 | 24/01/2025 | 20 | GP3.1021.../2420185 | INSTANCE ID:-100748373 SITE ID:-I-MH-SATN-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- SOPAN NUMBER:- 9049618317 | Closed | Reliance Jio Infocomm Limited | Dhanashree Technocrats Pvt. Ltd. - Malegaon |  | Under voltage issue | OPEN | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | West | 211637917 | 24/01/2025 | 20 | GP3.1021.../2420178 | DG Under Volt Alarm | Closed | Reliance Jio Infocomm Limited | KALA Care Global LLP - Aurangabad |  | Under voltage issue | OPEN | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | West | 211690051 | 06/02/2025 | 30 | 3H.8902.../2421479 | Automation issue Call By Customer Name :- Swaraj Mobile No :-8381067477 | Closed | Swaraj Poultry Farm | Dhanashree Technocrats Pvt. Ltd. - Malegaon | 2.1 | MR2a wire loose in amf panel on the selector switch so tight the wire issue solved now run in auto mode. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | West | 211674899 | 01/02/2025 | 20 | GP3.1021.../2420185 | INSTANCE ID:-100748373 SITE ID:- I-MH-SATN-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE/EB CONTACTOR FAULTY NAME:- SOPAN NUMBER:- 9049618317 | Closed | Reliance Jio Infocomm Limited | Dhanashree Technocrats Pvt. Ltd. - Malegaon | 991 | Mains contactor found faulty so change the contactor. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | West | 211693078 | 07/02/2025 | 125.4 | 4H.8041.../2420207 | Starting/Stopping Issue | Closed | SANVI ENTERPRISES | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | low adblue level ,top up adblue . | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211680240 | 04/02/2025 | 2.8 | AP1.7003.../2400155 | Starting Issue Email by KGD Name - PRADAN | Task Start | PRADAN | Gangpur Sales and Services - BHUBANESWAR |  | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | West | 211696424 | 08/02/2025 | 40 | 3H.8951.../2420708 | Starting/Stopping Issue | Closed | Piyush Mantri Washim. | Dicksons Engineering Co.Pvt.Ltd. - Akola | 26 | p06AC-F0 connect ikonnect and clear . | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | West | 211688608 | 06/02/2025 | 40 | 3H.8951.../2420623 | Automation Issue Call By Customer Name :- Mr. Rajesh Khandelwal Mobile No :9503260947 | Closed | Khandelwal Jewellers. | Dicksons Engineering Co.Pvt.Ltd. - AMRAVATI | 20 | Mains R phase wire not connected properly tightened the same issue resolved. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | West | 211688840 | 06/02/2025 | 40 | 3H.8951.../2421178 | Starting/Stopping Issue | Closed | Axis Bank Ltd | Dicksons Engineering Co.Pvt.Ltd. - Nagpur | 4 | tripped with under speed alarm reset the alarm issue resolved. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | West | 211685404 | 05/02/2025 | 20 | GP3.1021.../2420089 | INSTANCE ID:-100745506 SITE ID:- I-MH-IDPR-ENB-G004 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM ISSUE NAME:- RAVINDRA NUMBER:- 7588944055 | Closed | Reliance Jio Infocomm Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati |  | no issue found. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | West | 211692352 | 07/02/2025 | 58.5 | T4.8941.../2421245 | Genset Trip | Closed | SHANTI ENTERPRISES | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 78 | no issue with thye dg open for servicing | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | West | 211690053 | 06/02/2025 | 200 | 6H.8438.C4../2420025 | amber lamp on | Closed | Faith Automation System & Tooling Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 36 | Low adblue level so top up adblue | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | West | 211694388 | 07/02/2025 | 500 | DV8.8501.C4../2420138 | Tripping issue Call By Customer Name :- Suhas . Mobile No :-8550995874 | Closed | Kolte-Patil Integrated Townships Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | No issue with Dg open by mistaken | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | West | 211694071 | 07/02/2025 | 20 | GP3.1021.../2420201 | Mains Contactor faulty | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Godhra | 34.7 | Mains contactor faulty. SE will visit today. | Open | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211681514 | 04/02/2025 | 7.5 | D3.8305.../2400158 | Starting/Stopping Issue | Task Start | SANTOSH KUMAR SAHOO | Gangpur Sales and Services - Angul | 23 | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211678007 | 03/02/2025 | 125.4 | 4H.8042.C4../2420815 | Starting/Stopping Issue | Open | Sailaja Commercial Construction Pvt Ltd | Hibreed Engineering Pvt. Ltd. - Guwahati | 39 | Update pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211688614 | 06/02/2025 | 15 | GP3.8501.../2420377 | DG Automation Problem | Task Start | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 8.12 | Found Customer side Selector switch was in Manual mode so, then change the Auto mode then Start the DG in Auto | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211688612 | 06/02/2025 | 40 | 3H.8951.../2420402 | DG Automation Problem | Task Start | Bharti Airtel ANG | Vidyut Engineers - New Delhi | 6 | Relay was foulty 8 pin so, replace the same | Closed | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
4 | North | 211688611 | 06/02/2025 | 40 | 3H.8951.../2420398 | DG Automation Problem | Task Start | Bharti Airtel ANG | OVN Industries Private Limited - New Delhi | 15.55 | During night DG was stop, Because panel mode come in Manual but Check the Engineer found no any issue related Auto & manual starting issue | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211688321 | 06/02/2025 | 125.4 | 4H.8042.C4../2420717 | Amber lamp alarm Call by Customer Name : Shrif khan No : 9413917942 | Task Start | S.K.POWER SOLUTION | Pratap Diesels Pvt. Ltd. - Bharatpur | 2.47 | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211687885 | 06/02/2025 | 82.5 | 5H.8901.../2420148 | Automation Issue Email By - KGD Name - Rajesh Aggarwal | Task Start | Germinal Technologies Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 1479 | Checked the engine, dg starts in Auto when main voltage is cut but does not stop when mains voltage comes | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211687028 | 06/02/2025 | 125.4 | 4H.8042.C4../2420564 | Starting Issue Call By Service Dealer Name :- C L Gayri Mobile No :- 9414168576 | Open | Jodhana Heritage Resort Pvt LTD | BSES (I) Pvt. Ltd. - Dungarpur | 12 | update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
75 | North | 211684119 | 05/02/2025 | 125.4 | 4H.8042.C4../2420796 | Starting Issue Call By Customer Name : Rajesh Kumar No : 9416722520 | Closed | POLKA PASTRY | SAAN Royal Power Solutions Private Limited - Bahadurgarh | 29.19 | R-Phase under voltage alarm occurred,fuse found faulty so replace the same | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | North | 211664389 | 31/01/2025 | 625 | DV0.8501.C4../2320027 | Oil Leakage issue Call By Customer Name :- Shambhu Yadav Mobile No :-8005116000 | Closed | FORECH INDIA PLTD. | SAAN Royal Power Solutions Private Limited - Sonipat | 287.34 | Oil Leakage found from timing plate side due to 13 no. & 17 No. bolt found loose so tightened the same & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
64 | South | 211696566 | 08/02/2025 | 58.5 | T4.8941.../2421037 | . | Closed | Aatmi | Surya Power Services - J C Road, Bangalore | LR | DIP STICK MISSING | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
67 | South | 211695556 | 08/02/2025 | 125.4 | 4H.8042.C4../2420190 | Starting Problem Call by : Dealer Name : Priya Contact : 8870478403 | Closed | Maharishi Vidya Mandir (CBSE) School, | Bharath Diesel Sales and Service - Puducherry | 19 | Inspection the dg increase the preheater time in 20 sec and Crank time in 5 sec , after start the dg starting ok but dg under observation. DG not Start at first Crank | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211719681 | 15/02/2025 | 30 | 3H.8902.../2420582 | Leakage Issue | Closed | Maa Kali Bhandar | Revenus Industries Pvt. Ltd. - Contai | 32 | There was coolant leakage at thermostat outlet hose due to clamp loose after tightening issue resolved | CLOSED | Prosanjit saha | [9 empty] | Thermostat | 5 | 4 | 3 | 60 | Low
9 | East | 211717635 | 14/02/2025 | 20 | GP3.8601.../2420556 | Leakage Issue | Closed | Sanjay Energy Station. | Revenus Industries Pvt. Ltd. - Hooghly | 1052 | SE found the banjo waser on the fuel filter was damaged them change the banjo waser, now engine start running condition is normal. | CLOSED | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | South | 211676926 | 02/02/2025 | 20 | GP3.8601.../2421060 | Trip_Genset_Low_Voltage | Open | P.Nagaraju | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | Visit Pending | Open | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | South | 211729175 | 18/02/2025 | 20 | GP3.8601.../2421416 | Trip_Genset_Low_Voltage | Open | MS. Power Systems | Prasad Power Engineers - Hassan |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | South | 211729017 | 18/02/2025 | 10 | GP3.8301.../2420194 | Starting Issue Call By Customer Name :- Sanjava .. Mobile No :-9036068959 | Task Start | Nitte (Deemed To Be University)... | Prasad Power Engineers - Karakala | 34.9 | Starting issue due to automation panle board problem so inform the automation panel board person ,now dg manually running properly. | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211729007 | 18/02/2025 | 0 | GP3.8601.../2520087 | FUEL PRIMING PUMP NOT WORKING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspectied the site noticed the fuel priming pump not working | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211685514 | 05/02/2025 | 57 | T4.8941.../2420464 | Diesel Leakage Issue Call By Customer Name - Sonam Number - 7303092007 | Task Start | M/S AXESS ULTRASONICS PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 158 | Found No any leakage from Engine, Diesel over flow reason during fill the diesel During visit the Engineer found 79% fuel | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | South | 211727558 | 17/02/2025 | 25 | GP3.8702.../2421940 | Electrical Problems | Open | Belve Inn | Prasad Power Engineers - Udupi |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | NORTH | 211729895 | 18/02/2025 | 125.4 | 4H.8042.C4../2420792 | Amber Lamp On Alarm Call By Customer Name :- Satyam Pathak Mobile No :-7649989898 | Task Start | HOTEL GURUDEV KUNJ | Excel Diesel Private Limited - Faizabad |  | Engineer visit today | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | NORTH | 211729875 | 18/02/2025 | 125.4 | 4H.8041.../2420418 | Leakage Issue | Task Start | AP INFRA | R K Engineers - Bijnor |  | Update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | NORTH | 211729847 | 18/02/2025 | 125 | F6.9840.../2420054 | 2420054 | Task Start | ADVANTEK FUEL SYSTEMS PVT. LTD. | Paluck Technologies Ltd. - Ghaziabad | LR | Gas Engine | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | NORTH | 211729580 | 18/02/2025 | 58.5 | T4.8941.../2422419 | Starting Issue Call By Customer Name - Vikas ... Number - 8700415057 | Task Start | Dhingra Fabrics Pvt. Ltd. | Vidyut Engineers - New Delhi | 2 | Update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211725775 | 17/02/2025 | 30 | 3H.8902.../2420172 | Starting Issue Call By Customer Name :-Rajiv Mobile No :-9777575588 | Task Start | Thakur Enterprises | Gangpur Sales and Services - BHUBANESWAR |  | Visit Pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | South | 211677607 | 03/02/2025 | 250 | F6.8841.../2420045 | Starting issue Call by customer Name: Murty Number: 9606805106 | Task Start | JRC Projects | Surya Power Services - Bommasandra, Bangalore | 165 | check the engine not starting in auto mode due to phase change in lvm. Change the phase in lvm and check in auto mode running found ok | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | South | 211677647 | 03/02/2025 | 0 | GP3.8702.../2422057 | ENGINE HUNTING | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected the dg give to load 50% dg working ok but abow 50 % dg don't take load and block smok , Check the air filter and turbo ok, check the fuel filter tightness and comman rail pressure are ok , still tomorrow replaced the injeter | Task Start | Mr. NandhaGopal | [9 empty] | Air Filter | 4 | 4 | 3 | 48 | Low
13 | NORTH | 211728680 | 18/02/2025 | 160 | 6H.8475.../2420038 | REVALIDATION REQ | Completed | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | LR-1.4 | SR open for Revalidation | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | NORTH | 211727980 | 17/02/2025 | 15 | GP3.8501.../2421667 | White Smoke Issue Call By Customer Name :- Yogesh Bishnoi No :- 6375000318 | Open | BAGTESH INFRA | Rajdhani Diesels and Electricals - Jodhpur |  | Visit pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | NORTH | 211726249 | 17/02/2025 |  | 4H.8042.C4../2421158 | LINE REJECTION | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | NORTH | 211726156 | 17/02/2025 | 58.5 | T4.8941.../2421959 | Automation Issue Call By Customer Name - Mr. Ish Agarwal Number - 9868785036 | Closed | Ish Agarwal | Paluck Technologies Ltd. - Ghaziabad | 23 | Mains line issue in Customer panel side | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | South | 211677676 | 03/02/2025 | 160 | 6H.8475.../2420324 | shutdown Alaram Issue. Call By KGD Name :- Nivita Mobile No :-9434293127 | Completed | Liberty High Scans Private Limited | Madhu Engineering Sales & Service - Teynampet,Chennai | 39 | ADBLUE LOW LEVEL ALARM SHOWING SO TOPUP THE ADBLUE IN 100% THEN STARTED THE DG RUNNING NORMAL CONDITION. | Completed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | NORTH | 211725976 | 17/02/2025 |  | 4H.8042.C4../2520071 | STARTING ISSUE | Closed | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi | LR | Fan hub issue - Update pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | NORTH | 211725928 | 17/02/2025 | 20 | GP3.8604.../2420102 | INSTANCE ID:-100740911 SITE ID:- I-RJ-ALWR-ENB-G001 CALL BY CUSTOMER// DG ISSUE:- DG UNDER VOLTAGE ALARM/AUTOMATION FAULTY NAME:- KISHAN NUMBER:- 9024467214 | Under Monitoring | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - Alwar | 300 | Under voltage alarm | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | North | 211730289 | 18/02/2025 | 20 | GP3.8601.../2421051 | Starting issue | Closed | M/s BHARAT CONSTRUCTIONS (INDIA) PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Shimla | 51 | Fuel pipe found choked so clean the same & also clean the Tank , resolved the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | South | 211677689 | 03/02/2025 | 20 | GP3.8601.../2421748 | Starting Problem Call by : Customer Name :Sam Contact :9447798549 | Closed | St. MATHIAS ORTHODOX SYRIAN CHURCH | G-Care Diesels Private Limited - Thrissur | 32 | Dg starting problem rectified. Fuse failure. 2A ,M2 fuse box . 10 A fuse damage. Replace fuse. Problem clear. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211728709 | 18/02/2025 | 30 | 3H.8902.../2421211 | Protect lamp on issue Starting issue Call By Customer Name :- Urvanchal panday Mobile No:-9906408310 | Task Start | BHARAT GENERAL STORE | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | South | 211677887 | 03/02/2025 | 58.5 | T4.8941.../2423150 | Electrical Problems | Task Start | Raghamantra Jewellery | Bharath Diesel Sales and Service - Salem | 1.48 | 2791/18, 5838/1 clear the code. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | NORTH | 211728961 | 18/02/2025 | 20 | GP3.8601.../2420063 | Starting/Stopping Issue | Closed | Posh Fragrances Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 52 | Found maintenance due alarm & service required | Closed | Kapil Solanki | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
35 | North | 211723469 | 17/02/2025 | 125.4 | 4H.8041.../2420506 | Service due | Closed | VPG Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Baddi | 507 | Service has been done | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211726050 | 17/02/2025 | 2.8 | AP1.7003.../2400148 | Starting Issue Email by KGD Name - Saktimay Satpathy | Open | RANJIT TENT HOUSE | Gangpur Sales and Services - BHUBANESWAR |  | Today SE will visit site | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211722526 | 16/02/2025 | 320 | F6.8802.../2420176 | AMF Panel Power Supply Issue. Call By Customer, Name: -CHANDAN KUMAR SINGH Mobile No.:-8757084667 | Closed | RADHESHYAM INFRA | Globalline India Services Private Limited - Arrah | 4 | No issue in DG, There was an automation issue so SE visited and connected the wires properly issue resolved. | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
42 | South | 211673384 | 01/02/2025 | 160 | 6H.8475.../2420310 | Starting/Stopping Issue | Closed | Eye Foundation Ltd. | Ultimate Power Source - Vellore | 93 | No issue | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | South | 211725214 | 17/02/2025 | 125.4 | 4H.8042.C4../2420824 | Abnormal Sound Issue And Preventive Maintenance Call By Customer Name :- Murgan Mobile No :-9941009188 | Task Start | Pers Enterprises P. Ltd. | Madhu Engineering Sales & Service - Teynampet,Chennai | 315 | 1761/16,3031/14,1761/17,6875/0,4095/1, error code clear the code. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | South | 211673585 | 01/02/2025 | 15 | GP3.8501.../2421687 | DC supply switch broken Call by : Customer Name : Contact :8105211989 | Closed | KAUSHAL | Surya Power Services - Mysuru | 2 | Visited the site replaced the DC supply switch and solved the issue | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
40 | South | 211674108 | 01/02/2025 | 15 | GP3.8501.../2421320 | Excessive Smoke | Open | C. Jawahar | Net Work Diesels - Sholinganallur |  | Visit Pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | South | 211723776 | 17/02/2025 | 30 | 3H.8902.../2422111 | prementive maintaince call by : customer name : Malyadi contact : 8790197273 | Task Start | Bhargavi Engineering. | Ultimate Power Source - Nellore |  | Visit pending | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211723615 | 17/02/2025 | 25 | GP3.8702.../2520192 | LEAK OFF PIPE DAMAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspection the site noticed the fuel return hose connector damage | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | South | 211723333 | 17/02/2025 | 40 | 3H.8951.../2421520 | Spn 2791 fmi18 | Task Start | FUJI TECHNICAL SERVICES PVT. LTD. | Electro Controls - Palakkad |  | Visit pending | Task Start | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | South | 211723273 | 17/02/2025 | 40 | 3H.8951.../2421223 | Error Code Issue Call By Customer Name : Vinay No : 8123760610 | Task Start | OUR LADY OF LOURDES CHURCH | Prasad Power Engineers - Tumkur | 5 | After visited the site observed thet there is active error code. After clear the error code found ok. Finally started the engine observed on running condition working found ok | Task Start | Mr. Anil Kumar H G | Details required | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | South | 211674125 | 01/02/2025 | 125.4 | 4H.8041.../2420370 | Starting/Stopping Issue | Closed | Dot Workplace Solutions Pvt Ltd | Surya Power Services - Bommasandra, Bangalore | 53 | Adblue low topup the same. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | South | 211674462 | 01/02/2025 | 30 | 3H.8902.../2421062 | Diesel Leakage Problem Call by : Customer Name :Sajeesh Contact :9947269249 | Closed | Manappuram | G-Care Diesels Private Limited - Thrissur | 16 | Diesel leakage from fuel pipe(fuel filter to fip) due to pin hole noticed .replaced fuel pipe with new one. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | South | 211721738 | 15/02/2025 | 40 | 3H.8951.../2420896 | Error code | Task Start | Axis Bank Ltd | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 8.1 | 97/5 , 157/14,Attended the site and observed fuel in the water and pressure relief valv error codes clear after started the engine running condition is good observed no any leakages from engine side engine start and stop is good condition | Closed | Mr. MD Saleem | [9 empty] | Error Codes | 5 | 4 | 3 | 60 | Low
36 | South | 211674478 | 01/02/2025 | 200 | 6H.8435.../2420142 | REPLACING NEW CHARGING ALTERNATOR AS PER ASM APPROVAL | Task Start | KAVERI SUPER MARKET | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai |  | Visit Pending | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211711092 | 12/02/2025 | 40 | 3H.8951.../2421469 | Under Speed Alarm And Tripping Issue Call By Customer Name :- Riya Kumari Mobile No :-9341084114 | Closed | M/s. Riya Tent Light & Sound | HACS Engineering and Tech Private Limited - Daltonganj | 52 | update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
35 | South | 211674508 | 01/02/2025 | 25 | GP3.8702.../2420122 | Starting Problem Call by : Customer Name : Srinivasulu Contact : 9849554400 customer registered the complaint on 29/1/2025 ,he didn't get any call back from our Dealer side and also the complaint was cancelled SR no: 211656297 | Task Start | Prasad Trading Company | Ultimate Power Source - Kurnool |  | Visit Pending | Task Start | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | South | 211675534 | 01/02/2025 | 160 | 6H.8475.../2420286 | Error code issue Called by customer Name : Napa Radhakrishnan Number : 8939061144 | Closed | Sri Napa Kalyana Mandapam | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 18 | 1761/16 , 516166/0 .Adblue low alarm, topup the same | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | South | 211720440 | 15/02/2025 | 25 | GP3.8702.../2420995 | Starting Problem & Automatically Switching off Call by : Customer Name :SIVAKUMAR Contact :8012010006 | Closed | Aliyar Residency | Electro Controls - Pollachi | 27 | Visited the site observed that DG checked engine oil level and radiator coolent level found ok checked battery voltage is normal then checked all wiring harness are good condition started the engine running performance is normal found load test Carried out found engine not tripping checked all parameters are working properly. Found control ON OFF switch is lightly loosed so retighted the element... | Closed | Mr. Sanjaimon S | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
25 | South | 211720248 | 15/02/2025 | 20 | GP3.8601.../2421003 | Red lap problem Call by : Customer Name : Basava raju Contact : 7795769416 | Task Start | SREE BASAVA TRADERS | Vijayshree Diesel Sales and Service - Bellary | 144 | No issue, Customer side Emergency alarm pressed | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | South | 211720180 | 15/02/2025 | 5 | CP1.1003.../2400027 | Oil Leakage Issue. Call By Customer. Name:-Lingappa Mobile No.:7676848981 | Closed | CHANNAGOUDRA TRADING COMPANY | KALA Care Global LLP - Hubli | 22 | As per the customer completing the visit to the site and observing the oil leakage issue oil drain Bolt copper washer was broken and replaced copper washer and start the DG running is ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | South | 211676760 | 02/02/2025 | 125.4 | 4H.8041.../2420463 | Tripping Issue Call by customer Name: Kanan - Number: 9840638763 | Open | Sonder Groups | Bharath Diesel Sales and Service - Chennai |  | Visit Pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
29 | South | 211720109 | 15/02/2025 | 250 | F6.8841.../2420414 | Display showing alarm Call by : Customer Name : Sharath Contact : 8197581568 | Task Start | KIDS CLINIC INDIA LIMITED | Surya Power Services - J C Road, Bangalore | 52 | Adblue low alarm. Top up the same. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | South | 211676833 | 02/02/2025 | 200 | 6H.8435.../2420257 | Starting Issue Call By Customer Name- C Chethan Mobile No- 9488454067 | Task Start | Utsav | Surya Power Services - Bommasandra, Bangalore | 15 | 97/5 alarm in water in fuel and remove the diesel filter and refitting the diesel filter and rest the alarm and engine start running found ok | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | South | 211719926 | 15/02/2025 | 125.4 | 4H.8042.C4../2420294 | Automatically switching off & error code problem Call by : Customer Name : Mallan gowda Contact : 9731472579 | Task Start | Suresh Hangal | Vijayshree Diesel Sales and Service - Hospet | 88 | Adblue low alarm. Top up the same. Also fuel senor stuck | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | South | 211719787 | 15/02/2025 | 30 | 3H.8902.../2421079 | Starting Problem Call by : Customer Name :Mohammad Contact : 9391939708 | Closed | Lagan Shah Sarees | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 27.1 | Found start relay wires voltage droped tight the wiring and check the engine start and stop working ok | Closed | Mr. MD Saleem | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
35 | South | 211719511 | 15/02/2025 | 20 | GP3.8601.../2421691 | Starting/Stopping Issue | Closed | Thirupathi Gen-z Private Limited | Ultimate Power Source - Vellore | 9 | No issue | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
42 | South | 211718223 | 14/02/2025 | 58.5 | T4.8941.../2422168 | NOT START | Closed | Abdul Jaleel | G-Care Diesels Private Limited - Calicut | LR | Attended the site check the engine site visited for Genset commissioning,but unfortunately found that Genset diesel return line is in disconnected condition and tried to connect the diesel line with gauge,but it's not suitable both side ,so discussed the matter with OEM team (powercom),and as per OEM request and customer emargency situation, temporarily an another hose crimped and fitted issue solved | Closed | Mr. Sanjaimon S | GOEM issue | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | South | 211718146 | 14/02/2025 | 125.4 | 4H.8041.../2420789 | Amber Lamp Alarm Call By Customer Name : -Sukesh No:-9060158877 | Closed | Hotel Swathi. | Vijayshree Diesel Sales and Service - Hospet | 89 | 1761/16- Urea Tank Level - Bank 1 - Below Normal Range Moderately Severe, check the dg add blue low and top-up the add blue and clear the alarm start the DG running condition good and checked the all parameter found ok take on trial engine is good working | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
34 | South | 211675051 | 01/02/2025 | 250 | F6.8841.../2420324 | Starting/Stopping Issue | Task Start | KARSN Food & Beverages | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 171 | Adblue low alarm | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211721389 | 15/02/2025 | 40 | 3H.8951.../2420139 | Starting/Stopping Issue | Closed | K. Fialok Trendz | Industrial Power Solutions - LUDHIANA | 142 | Starting issue due to 3 No. wire found loose on Self Starter so re-conneceted the same & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211719606 | 15/02/2025 | 100 | 4H.8041.../2320072 | Starting/Stopping Issue | Closed | Council of Scientific and Industrial Research CSIR. Himachal Pradesh | Megatron Engineers - Amb | 125 | Flange heater was not installed due to which DG starts after 20 second,installation of Flange heater has completed with GOEM (Electro-equipment) & resolve the issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | South | 211678258 | 03/02/2025 | 58.5 | T4.8941.../2421695 | AMF panel problem Call by : Customer Name : Sanjay siddagowdru Contact : 9900975126 | Task Start | Santosh Channappa Gudas | KALA Care Global LLP - Belagavi | 38 | Contractor fault at Koel AMF panel. Replace the contractor | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | South | 211666866 | 31/01/2025 | 25 | GP3.8702.../2421579 | Door lock problem Call by : Customer Name :Jishad Contact :7902288628 | Closed | Vortex Fuels | G-Care Diesels Private Limited - Malappuram | 43 | Door hinges issue | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | North | 211733284 | 19/02/2025 | 40 | 3H.8951.../2520140 | Starting Issue Email By - KGD Name - Rohit Gupta | Task Start | TARUN DUA | Vidyut Engineers - Noida | 12 | Found starting ring move freely but check Starter found ok | open | Kapil Solanki | Plant issue | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211733269 | 19/02/2025 | 57 | T4.8941.../2320129 | Battery Issue & preventive Maintanance Call By Customer Name :- Rajesh No :-9818443221 | Task Start | Country Home Fashions Pvt. Ltd. | Vidyut Engineers - New Delhi | 22 | DG bettary terminal faulty so replace the same & service done | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211733243 | 19/02/2025 | 125 | F6.9840.../2420031 | Under Speed Alarm issue Call By Customer Name :- Durgesh Awasthi Mobile No :- 9602907049 | Closed | UNIQUE POWER SOLUTION. | Vidyut Engineers - Noida | 29 | Increase the gas pressure through ITV | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211733134 | 19/02/2025 | 750 | DV2.8501.C4../2420019 | Urea Tank Cap Issue Call By Customer Name :-Saddam Mobile No :- 9785742850 | Task Start | Homekraft Infra Pvt. Ltd. | Vidyut Engineers - Noida | 47 | found urea tank cap proper not fitted Due to urea tank cap is faulty urea tank cap to be change (3) pes | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | WEST | 211659492 | 30/01/2025 | 125.4 | 4H.8042.C4../2420162 | Leakage Issue | Completed | YMCA OASIS | Unique Techno Services Pvt Ltd. - Ahmedabad | 254 | Oil leakage from flywheel side oil seal so engineer will visit today. | closed | Amit sandlya | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
15 | North | 211733078 | 19/02/2025 | 30 | 3H.8902.../2420924 | Starting/Stopping Issue | Open | JAY SHREE KRISHNA CONSTRUCTION COMPANY | Rajdhani Diesels and Electricals - Barmer | 116 | Found in panel connection was loose tightness to be all | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | North | 211732954 | 19/02/2025 | 20 | GP3.1021.../2420328 | INSTANCE ID:-100777785 SITE ID:- I-UE-MUDH-ENB-9097 CALL BY CUSTOMER// DG ISSUE:- DG AIR ISSUE NAME:- MANVENDRA SINGH NUMBER:- 9305497598 | Task Start | Reliance Jio Infocomm Limited | Espiem Engines & Machines (P) Limited - Banda |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | North | 211732673 | 19/02/2025 | 500 | DV8.9313.../2420028 | .. | Open | Kirloskar Oil Engines Ltd | Excel Diesel Private Limited - Faizabad | LR | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | WEST | 211661535 | 30/01/2025 | 750 | DV2.8501.C4../2420174 | Electrical Problems | Closed | Gulbrandsenv | Unique Techno Services Pvt Ltd. - Dahej | 10 | SR opened for sync activity. | closed | Amit sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211732567 | 19/02/2025 | 30 | 3H.8902.../2420026 | Starting Issue Call By Customer Name :- Manish Kumar Mobile No :-9318482747 | Closed | KSS Engineers | Paluck Technologies Ltd. - Faridabad | 89 | Found Emergency alarm check the relay & Emergency found ok after reset the alarm then issue resolve | Closed | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
25 | North | 211730555 | 18/02/2025 | 58.5 | T4.8941.../2420691 | Starting/Stopping Issue | Closed | Relief Hospital. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 261 | Found emergency switch was pressed then realease the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211734041 | 19/02/2025 | 57 | T4.8941.../2320210 | Starting Issue Call By Customer Name :-Arun Rajpal Arun Rajpal Mobile No :- 9968270524 | Closed | Sunrise Towers CGHS. Ltd. | Paluck Technologies Ltd. - Faridabad | 213 | Found Emergency button on pressed condition so, realease the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | North | 211730449 | 18/02/2025 | 200 | 6H.8435.../2420226 | Load Issue Call By Customer Name :- Guru Singh Mobile No :-9870651513 | Task Start | GURU GOBIND SINGH COLD MILLS | R K Engineers - Meerut |  | Visit today SD team & Sales team | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211733112 | 19/02/2025 | 1500 | DV2.8508.C4../2420004 & 2420006 | Inspection/Maintenance | Task Start | Guru Nanak Agro Foods Pvt. Ltd. | Gen Powers - PATIALA | 11 | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | North | 211732956 | 19/02/2025 | 15 | GP3.8501.../2421245 | Starting Issue Call By Customer Name :- Pravin Mobile No:-9660540744 | Task Start | BHARAT GENERAL STORE | Suraj Motor Store - Jammu | 239.83 | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | WEST | 211664384 | 31/01/2025 | 58.5 | T4.8941.../2422537 | White Smoke Issue. Call By Customer. Name:-Amol Kumar Disen Mobile No.:-9630590389 | Closed | Amol Kumar | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 264 | No issue found | closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | WEST | 211650216 | 28/01/2025 | 58.5 | T4.8941.../2423060 | Oil Leakage Issue Call By Customer Name :-Rakesh Mobile No :-8849978537 | Closed | HANUMAN RAM S/O KHUMA RAM | Unique Techno Services Pvt Ltd. - Anand | 285 | Oil was leaking from the oil seal so SD went to the spot and checked the torque value of the bolts and found it to be OK. Replaced the oil seal and torqued the bolts properly. |  | Amit sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | North | 211732572 | 19/02/2025 | 62.5 | T4.8941.../2420119 | Fuel sensor faulty | Closed | Jain Garments | SAAN Royal Power Solutions Private Limited - Hisar | 90 | Fuel guage found faulty,showing variable paramter,will replace the same,new guage found broken | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | North | 211716296 | 14/02/2025 | 625 | DV0.8501.C4../2420094 | Under Voltage issue Call by customer Name: Prabhyot Singh Number: 9888247463 | Closed | St. Joseph Convent School. | Dynamic Engineering Services - Jalandhar | 24 | RRA Assembly changed due to not giving voltage ; RRA MOV points are shorted(both end center point) ,no such reverse power alarm found in event log(asked to dealer for data log & event log and check-sheet for RRA check) | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211714954 | 13/02/2025 | 250 | F6.8841.../2420246 | Leakage Issue | Closed | Sunflag Global Hospital. | SAAN Royal Power Solutions Private Limited - Rohtak | 75 | Customer raised complaint as oil leakage due to some fuel & oil fall-out on guage but no such issue found in DG ; Cleaned the poured oil & fuel,filters were fitted correctely & benjo bolts re-tightened,No issue found | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
45 | North | 211713584 | 13/02/2025 | 25 | GP3.8702.../2420112 | FUEL READING ISSUE | Closed | A & Z Exports International. | Dynamic Engineering Services - Jalandhar | 47 | Fuel level was not showing correct parameter(83% instead of 100%),open the guage & re-fitted the same,issue resolved | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
46 | North | 211713524 | 13/02/2025 | 160 | 6H.8475.../2420174 | Fan belt damage | Closed | STRIKER&BROTHERS | SAAN Royal Power Solutions Private Limited - Baddi | 559 | Engine over-heat alarm due to fan-belt found broken so replace the same & resolve the Issue (Update Pending) | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
47 | North | 211713387 | 13/02/2025 | 15 | GP3.8501.../2421309 | Starting/Stopping Issue | Task Start | Dynamics Solutions | Suraj Moters Stores - Leh |  | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
48 | North | 211713345 | 13/02/2025 | 20 | GP3.8601.../2421337 | Pa war supply issue Call By Customer Name :- Ajay Joshi Mobile No :- 9915501972 | Closed | Ajay Joshi | Dynamic Engineering Services - Jalandhar | 4 | Auto-change switch from customer side not working properly,no issue in DG in mannual mode | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211735069 | 19/02/2025 | 15 | GP3.8501.../2420002 | Genset Trip | Task Start | Laxman Choudhary. | Globalline India Services Private Limited - Darbhanga |  | today SE will visit site, Showing Red lamp alarm | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
31 | North | 211733281 | 19/02/2025 | 15 | GP3.8501.../2420686 | Inspection/Maintenance | Task Start | Misty mountain Retreat. | Megatron Engineers - Amb | 75.61 | Starting issue due to Fuel Filter found choked,fuel found contaminated so cleanthe Filter & tank & resolve the Issue | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211735057 | 19/02/2025 | 40 | 3H.8951.../2420639 | Earthing issue | Completed | NAV SHAKTI APARTMENT CGSH LTD. | OVN Industries Private Limited - New Delhi | 5 | found body earthing bolt is damage | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | North | 211735074 | 19/02/2025 | 15 | GP3.8501.../2420062 | Starting Issue Call By Customer Name :- Vishwendra Mobile No :-7983860121 | Task Start | Shoram Hospital | R K Engineers - Meerut | 16 | Found Emergency was pressed condition, so realease the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211735325 | 19/02/2025 | 20 | GP3.8604.../2420159 | INSTANCE ID:-100742282 CUSTOMER SITE ID ;- I-RJ-CHMU-ENB-G004 CALL BY CUSTOMER\\ DG ISSUE:-UNDER VOLATGE ISSUE ,ALRAM ISSUE NAME:-.MANISH KUMAR NUMBER:-6350491536 | Task Start | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - JAIPUR |  | under voltage alarm | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | South | 211678292 | 03/02/2025 | 125.4 | 4H.8041.../2420341 | Starting Problem Call by : Customer Name :Natarajan Contact :9715543808 | Open | Hotel Vaira Maligai | Electro Controls - Marthandam |  | Visit Pending | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211729325 | 18/02/2025 | 25 | GP3.8702.../2421218 | Automation Issue Call By KGD Name :- Kukum Number:- 9234456624 | Open | JAIN PETROL SUPPLY COMPANY | HACS Engineering and Tech Private Limited - Hazaribagh | 92 | No issue in DG customer AMF pannel side issue and also customer satisfied with it after operating in mannual mode. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211727938 | 17/02/2025 | 125.4 | 4H.8042.C4../2421093 | STARTING ISSUE | Task Start | POWERLINE GREEN | Hibreed Engineering Pvt. Ltd. - Nagaon |  | GOEM plant issue-not starting due to airlock issue after clearing the airlock issue resolved | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211730608 | 18/02/2025 | 5.5 | CC1.1013.../2400171 | Starting Issue Call By KGD Name :- Sanjeev Mobile No:-9308664303 | Open | Mahadev Advertiser | Globalline India Services Private Limited - Bhagalpur |  | The DG is install on vehicle and at present it is in Jharkhand so need to transfer Asset | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211726050 | 17/02/2025 | 2.8 | AP1.7003.../2400148 | Starting Issue Email by KGD Name - Saktimay Satpathy | Task Start | RANJIT TENT HOUSE | Gangpur Sales and Services - BHUBANESWAR | 35 | SE found Dg Starting Issue.After Clean the Carburetor Engine Running Smoothly.Advice to Customer arrange proper Ventilation for realise hot air | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | South | 211678593 | 03/02/2025 | 40 | 3H.8951.../2420713 | battery problem Call by : Customer Name :Kashinath Contact :9591215161 | Open | Star Karavali Constructions | Prasad Power Engineers - Karakala |  | Visit Pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | East | 211729533 | 18/02/2025 | 250 | F6.8841.../2420312 | STARTING ISSUE | Task Start | M/s. Planter Hotel A. Unit Of Jigden Hotel & Resort Pvt. Ltd. | K.C. Diesel Services - SILIGURI | LR | Hunting Issue (RPM Variation 1498 - 1501) | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | West | 211714957 | 13/02/2025 | 0 | F6.8802.../2420207 | Thread issue | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Vapi | LR | Header cooler thread damage. | OPEN | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | West | 211709489 |  | 5.5 | CC1.1013.../2400727 | Tripping issue Call By Customer Name :- Nikhil . Mobile No :-8286828690 | Closed | Gayatri construction | Transcreek Engineers Pvt. Ltd. - Ambernath | 1 | Spark arrestor found chocked , so cleaned it | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | West | 211713272 | 13/02/2025 | 625 | DV0.8501.C4../2420059 | Starting issue Call By Service Dealer Name :- SANJAY PATEL Mobile No :- 9377694649 | Closed | Shashvat Green Energy Private Limited | Unique Techno Services Pvt Ltd. - Mahesana | 4 | Automation issue. | Closed | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | West | 211722450 | 16/02/2025 | 58.5 | T4.8941.../2422296 | Starting issue all By Customer Name :- Harsin Mobile No :- 9263854162 | Closed | Sarveshwari Mines. | Shree Engineering Service - Singrauli | 14 | emergency switch connection found loose , tight the connection. | Closed | Jagdeep saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211732230 | 18/02/2025 | 20 | GP3.8601.../2421533 | Trip_Genset_High_Voltage | Open | KSV Fuels | Electro Controls - Pollachi |  | Visit pending | Open | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211731147 | 18/02/2025 | 5.5 | CC1.1013.../2400210 | Starting Issue Call By Customer Name :- Sahul Ameen Number:- 9035052022 | Open | SRC Infra Developers Pvt Ltd | Vijayshree Diesel Sales and Service - Bellary | 214 | Silencer chocked, clean & refitted | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | South | 211730996 | 18/02/2025 | 40 | 3H.8951.../2421498 | Preventive Maintenance Call by : Customer Name :Balu Contact :9894751192 | Open | Vel Llanji Kumaran Ventures | Madurai Electro Controls - Tenkasi |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | South | 211730525 | 18/02/2025 | 20 | GP3.8601.../2421060 | Rpm problem Call by : Customer Name : Krishna Contact : 9346950589 | Task Start | P.Nagaraju | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 5.3 | RRA wire burnt. | Task Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | South | 211665247 | 31/01/2025 | 125.4 | 4H.8042.C4../2420240 | Starting/Stopping Issue | Task Start | Puthige Muranthakodi Subraya Bhat Memorial Charitable Trust | Prasad Power Engineers - Karakala | 1 | Self Startor movment is not happening. So replaced the Self Startor. | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | South | 211730185 | 18/02/2025 | 15 | GP3.8501.../2421880 | Tripping Problem Call by : Customer Name : Mariswamy Contact : 9611843600 | Task Start | MARISWAMY | Surya Power Services - Mandya |  | Visit pending | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | South | 211733291 | 19/02/2025 | 30 | 3H.8902.../2420050 | Sound/Vibration Issue | Task Start | M/s. Srinivasa Enterprises. | Sri Manjunath Technical Services - Bhimavaram | 480 | start the engine observed abnormal noise from fan belt side then adjust the fan belt aftar start the engine observed running is ok parameters is narmal no oil leack | Task Start | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | West | 211728845 | 18/02/2025 | 160 | 6H.8475.../2320007 | Leakage Issue | Closed | BOCHASANWASI SHRI AKSHAR PURUSHOTTAM PUBLIC TRUST | Unique Techno Services Pvt Ltd. - Baroda | 169 | The oil leak was coming from the sump oil drain pipe because the drain pipe was damaged. So the pipe was removed and bolted. | Closed | Amit sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | West | 211727401 | 17/02/2025 | 40 | 3H.8951.../2421212 | Power supplay Issue Call By Customer Name :- Amjed Khan Mobile No :-9566660861 | Closed | LG ELECTRONICS INDIA LIMITED | Natraj Power Tech - Indore | 2.3 | Engineer went to site for complaint of power problem. So he checked DG power supply is going to customer's changeover. Customer side problem. | Closed | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | West | 211724879 | 17/02/2025 | 160 | 6H.8475.../2420066 | Electrical Problems | Closed | Kavisha Group Developers | Unique Techno Services Pvt Ltd. - Ahmedabad | 191.5 | The customer complained that the DG starts and runs even when the main power supply is available.Engineer visited on site and checked DG was not shutting down when mains was unhealthy. DG shut down when mains was healthy. No any issue from our side. | Closed | Amit sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | West | 211722464 | 16/02/2025 | 58.5 | T4.8941.../2422937 | High Voltage issue Call by customer Name: Mahesh . Number: 9714673838 | Closed | Mahesh Bhai Ramesh Bhai Jadhav | Unique Techno Services Pvt Ltd. - Baroda | 1 | Engineer went to site for cable heating problem. Then he found problem on customer's cable side. So 2.5mm square cable was fitted in place of 1.5mm square cable. | Closed | Amit sandlya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | West | 211734731 | 19/02/2025 | 20 | GP3.8601.../2421321 | Low Volatge Issue Email By - KGD Name -Vishal Raut | Completed | ULV Residency | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 4 | Lift is working in 1,2,3 floor but not in 4,5,6 so need a joint visit with lift engineer. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | West | 211732891 | 19/02/2025 | 750 | DV2.8501.C4../2420161 | Starting/Stopping Issue | Closed | Protech Max Private Limited | Shree Engineering Service - Raipur | 2158 | Adblue level low so top up adblue | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | West | 211709159 |  | 500 | DV8.9313.../2400002 | Starting Issue | Closed | RAIL COACH FACTORY RCF | Transcreek Engineers Pvt. Ltd. - Mumbai | 647 | error code 157/14 , Rail presssure sensor shows the value during override so change the common rail assembly. | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | West | 211727852 | 17/02/2025 | 125.4 | 4H.8042.C4../2420063 | Genset Trip | Closed | Hukumchand Shantikumar Bros. | Dicksons Engineering Co.Pvt.Ltd. - Nagpur | 17 | Adblue level low so top up adblue | Closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | South | 211666496 | 31/01/2025 | 40 | 3H.8951.../2421147 | Starting/Stopping Issue | Closed | REVAMP POWER | Surya Power Services - J C Road, Bangalore | 3.5 | Check the engine control on/off switch (cable 2B3)and(2B7) No disconnected. Switch replaced.Tighten the the control switch properly | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | NORTH | 211722451 | 16/02/2025 | 57 | T4.8941.../2320093 | Starting/Stopping Issue | Open | ROHIN STEEL INDUSTRIES | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | South | 211673393 | 01/02/2025 | 82.5 | 5H.8901.../2420493 | Excessive Smoke | Closed | SALEM MARTHOMA CHURCH | Electro Controls - Mavalikara | 16 | Found the leakage from the exhaust pipe joint. Remove pipe and reconnected tightly. Presently complaint is cleared. | Closed | Mr. Sanjaimon S | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | NORTH | 211722471 | 16/02/2025 | 200 | 6H.8435.../2420025 | Fan Belt Issue Call By Customer Name :- Gaurav Mobile No :-7976790652 | Closed | MORINGA HILL RESORT | BSES (I) Pvt. Ltd. - Udaipur | 509 | V-belt was broken, so replace the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | NORTH | 211722476 | 16/02/2025 | 20 | GP3.8601.../2420787 | Red Lamp On Alarm Issue. Call By Customer. Name:-Kiyansu Jayshwal Mobile No.:-7080207044 | Open | JAISWAL COLLECTION | Excel Diesel Private Limited - Raebareli |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | East | 211703705 | 10/02/2025 | 45 | 3H.8951.../2421641 | Starting issue Called by customer Name : Prabhakar Number : 8709322290 | Open | N D Mart | HACS Engineering and Tech Private Limited - Deoghar | 242 | There is no issue in DG at present its running properly only once DG fails to start after that no issue raise so customer,s demand is to check the health of DG. Dealer yet not able to depute the SE will depute soon. | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | East | 211713841 | 13/02/2025 | 20 | GP3.8601.../2420685 | Maintenance Due Alarm issue Call by Customer Name :-Akhilesh Prasad NO :-9778074795 | Open | VEERMAN ENTERPRISES | Gangpur Sales and Services - Sambalpur |  | visit pending | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | East | 211700712 | 10/02/2025 | 125.4 | 4H.8042.C4../2420732 | Starting/Stopping Issue | Closed | Mondal Electricals | Revenus Industries Pvt. Ltd. - Asansol | 52.11 | Error code 1761/14 due to AdBlue very low level,Top-up the AdBlue and checked all external parts found normal then start the engine running on load testing condition normal. | CLOSED | Prosanjit saha | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
27 | North | 211679723 | 03/02/2025 | 15 | GP3.8501.../2421245 | Tripping issue Called by customer Name : Vijay Number : 9596287903 | Open | BHARAT GENERAL STORE | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211691868 | 07/02/2025 | 10 | GP3.8301.../2420342 | Line Rejection | Task Start | R GANESH | Gangpur Sales and Services - Rourkela | 1 | SE removed tappet covers and found All Intake Adjusting Screw dislocated but the Lock nut were not loose.So removed the Rocker arm Shaft and Found 2 nos Bent push tubes and also found Rocker shaft mounting bolt in loose condition and observed no oil supply or oil traces on rocker shaft and near rocker arm and found Rocker shaft sheared. | OPEN | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | South | 211716264 | 14/02/2025 | 58.5 | T4.8941.../2422201 | Starting/Stopping Issue | Task Start | Sarvanandh Garu | Laxmi Diesels - Rajahmundry | 16 | visit the site as per following complaint check the engine condition and wiring connections found the relay board wiring was lose so retight the connections then start the engine running condition is ok | Closed | Mr. MD Saleem | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
3 | South | 211713709 | 13/02/2025 | 10 | GP3.8301.../2420162 | Starting Issue Call By Customer Name : Pavan No : 8747900715 | Open | SRI VINAYAKA FILLING STATION | Prasad Power Engineers - Tumkur |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | South | 211712762 | 13/02/2025 | 15 | GP3.8501.../2420254 | Automatically switching off Call by : Customer Name : Arief Contact : 9849099745 | Closed | Sayeed Brothers. | Powerlinks Infra Tech Pvt Ltd - L B Nagar | 54.28 | Attend the site checking engine is not start in auto mode checking connection Automatic glass relay loose connection glass relay loose fightment tight and checking engine is ok so started the engine starting and running condition is good load trail also done and also checked automatic working is ok | Closed | Mr. MD Saleem | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
24 | North | 211675056 | 01/02/2025 | 125.4 | 4H.8042.C4../2420472 | Starting Issue Call By Customer Name - Narendar Singh Number - 7669931331 | Closed | M P Singh | Vidyut Engineers - Noida | 4.2 | Emergency switch button was pressed realeased the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | South | 211712684 | 13/02/2025 | 200 | 6H.8435.../2420159 | AMF panel problem Call by : Customer Name : Harish Contact : 9900605134 | Closed | NP Ramesh | Surya Power Services - Bommasandra, Bangalore | 205 | Visit the site check the auto not starting due to the b phase fuse fault replace the new fuse and check in auto mode running found ok check the all parameters working engine running found ok | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | North | 211661599 | 30/01/2025 | 125.4 | 4H.8041.../2420905 | Electrical Problems | Closed | JEENA CRITICARE LOGISTICS PVT.LTD | OVN Industries Private Limited - New Delhi | 119 | Mains contactor not be hold Voltage set from VMR 270 | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | South | 211717434 | 14/02/2025 | 20 | GP3.8601.../2420539 | Starting/Stopping Issue | Task Start | Rise Hospitals. | Sri Manjunath Technical Services - Vijaywada | 60 | DG observed emergency stop switch activated alaram so checked the sensing and connected nagative wire after start the DG and I observed DG working condition is ok | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | East | 211704976 | 11/02/2025 | 20 | GP3.8604.../2420062 | INSTANCE ID:-100740972 SITE ID:-I-BR-SIMR-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-Anuj Kumar NUMBER:-8084447706 | Task Close | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah |  | update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | South | 211717354 | 14/02/2025 | 30 | 3H.8902.../2421318 | Starting/Stopping Issue | Task Start | Sreekanya Homes | Laxmi Diesels - Visakhapatnam | 1.1 | Customer, due to lack of knowledge, pushed the emergency button up, causing the DG to not start. Customer then registered a complaint that the DG was not starting. We attended the site, pushed the button down, and started the engine. Running condition found ok. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
20 | South | 211717187 | 14/02/2025 | 45 | 3H.8951.../2421626 | Starting Problem Call by : Customer Name : Dinesh Contact :9902182958 | Task Start | Perennial Technologies Pvt. Ltd | Prasad Power Engineers - Davangere |  | 2791/18 error code. | Task Start | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | South | 211716916 | 14/02/2025 | 15 | GP3.8501.../2421043 | Maintenance Due Alarm Issue & Diesel Leakage Issue Call By Customer Name : Chandrashekhar .. No : 7411968034 | Open | AXIS BANK LTD | Prasad Power Engineers - Hassan |  | Visit pending | Open | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | North | 211676987 | 02/02/2025 | 15 | GP3.8501.../2421667 | Starting Issue Call By Customer Name ;- YOGESH BISHNOI Mob No ;- 6375000318 | Closed | BAGTESH INFRA | Rajdhani Diesels and Electricals - Jodhpur | 90 | R Phase under voltage alarm due to fuse faulty in panel hence replace the same with new one, | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | South | 211716730 | 14/02/2025 | 15 | GP3.8501.../2421687 | Diesel leakage problem Call by : Customer Name :Vantash Contact :8105211989 | Task Start | KAUSHAL | Surya Power Services - Mysuru | 5 | Oil leakage from oil sump side. K - sealant is not properly applied. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | South | 211716728 | 14/02/2025 | 40 | 3H.8951.../2420896 | Red lamp Alaram problem Call by : Customer Name : Srisailam Contact : 7401631554 | Task Start | Axis Bank Ltd | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 8 | The Positive supply fuse failure so change the new fuse found ok | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211677622 | 03/02/2025 | 200 | 6H.8435.../2420025 | Fan Belt Issue And Abnormal Sound Issue Call By Customer Name :- Gaurav Mobile No :-7976790652 | Closed | MORINGA HILL RESORT | BSES (I) Pvt. Ltd. - Udaipur | 385 | Fan belt loose tightness the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211718676 | 14/02/2025 | 40 | 3H.8951.../2421443 | DG showing alarm under speed | Task Start | BHARTI AIRTEL LIMITED | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211718549 | 14/02/2025 | 58.5 | T4.8941.../2421947 | Maintenance Due alarm issue and Fuel Sensor issue Call By Customer Name :-Pawan Kumar Number:- 9811458226 | Task Start | INDER GENERATOR HOUSE.. | Vidyut Engineers - New Delhi | 313 | Maintenance due alarm reset & fuel level low | Closed | Kapil Solanki | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
4 | North | 211718308 | 14/02/2025 | 750 | DV2.8501.C4../2420026 | Starting Issue Call By Customer Name Vikram singh No : 9680457787 | Task Start | G S PHARMBUTOR PRIVATE LIMITED | Pratap Diesels Pvt. Ltd. - Alwar | 41 | Found Bank-B DM was not working so, replace the same after that issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | North | 211717810 | 14/02/2025 | 30 | 3H.8902.../2420872 | Starting Issue Call By Service Dealer Name :-Mahindra singh Mobile No :-8922816982 | Task Start | Kendriya Vidyalaya Uttar Pradesh. | Espiem Engines & Machines (P) Limited - Jhansi |  | Update pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211717727 | 14/02/2025 | 250 | F6.8841.../2420384 | Starting/Stopping Issue | Task Start | HOTEL DEV ARJUN SINGH PRIVATE LIMITED | S.S. Enterprises - Sonbhadra |  | Update pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211717114 | 14/02/2025 | 25 | GP3.8702.../2420006 | Battery issue | Completed | ENOVATE LIFESTYLES PRIVATE LIMITED(Candere Lifestyles Jewellery) | R K Engineers - Meerut |  | Update pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | South | 211717320 | 14/02/2025 | 15 | GP3.8501.../2421320 | Excessive Smoke | Open | C. Jawahar | Net Work Diesels - Sholinganallur |  | Visit pending | Open | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | East | 211710295 | 12/02/2025 | 15 | GP3.8501.../2421891 | Red Lamp On Alarm And Tripping Issue Call By Customer Name :- Virendra Kumar Mobile No :- 7488183540 | Closed | Abhisingh Kesri | Globalline India Services Private Limited - Muzaffarpur | 18 | There was red lamp issue due low fuel level and educate customer to maintain minimum 30 % fuel to get rid off from this issue and also said it next time this will held the service will be on paid basis | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | East | 211711092 | 12/02/2025 | 40 | 3H.8951.../2421469 | Under Speed Alarm And Tripping Issue Call By Customer Name :- Riya Kumari Mobile No :-9341084114 | Closed | M/s. Riya Tent Light & Sound | HACS Engineering and Tech Private Limited - Daltonganj | 52 | update pending | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | East | 211711910 | 13/02/2025 | 200 | 6H.8435.../2420109 | Radiator Leakage issue Call by KGD Name :-Sheetal Gupta NO :-6299024030 | Closed | Yogeda Satsanga Society of India | HACS Engineering and Tech Private Limited - Ranchi | 4.9 | coolant seepage was due loosen of thermostat outlet hose clamp tighten restore the issue at coolant hose pipw due loose of clamp, and door foam burn due contact with exhaust pipe so to restore the issue cutted the foam which was in contact with exhaust need some modifications | CLOSED | Prabhakar Kumar | [9 empty] | Thermostat | 5 | 4 | 3 | 60 | Low
68 | South | 211695423 | 08/02/2025 | 125.4 | 4H.8042.C4../2420258 | Starting Problem Call by : Customer Name : Shiva kumar Contact : 9553476969 | Closed | Bmm Founction Hall. | Ultimate Power Source - Kadappa | 32.58 | Engine not starting due to alarm issue (516166/0,4095/1,2) . Checked the wirring harness then Clear the code. | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | North | 211665814 | 31/01/2025 | 15 | GP3.8501.../2421242 | Starting/Stopping Issue | Open | ALIF EMPORIUM | Suraj Motor Store - Srinagar |  | Update Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
36 | North | 211666316 | 31/01/2025 | 20 | GP3.8601.../2421051 | Voltage Fluctuation | Closed | M/s BHARAT CONSTRUCTIONS (INDIA) PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Shimla | 39 | Voltage flactuation due to AVR connection found loose & fuse found faulty,Tightened & replace respectively &resolve the Issue (Update Pending) | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
76 | South | 211693425 | 07/02/2025 | 30 | 3H.8902.../2421509 | Diesel Leakage Problem Call by : Customer Name : Akshay Contact : 9538743337 | Closed | Badri Menz Fashion | Vijayshree Diesel Sales and Service - Hospet | 81 | Check the water level low top up the water level check the diesel fillter pipe lekage from benjo bolte loose retight it, engine start no leakages performance ok | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
77 | South | 211693166 | 07/02/2025 | 250 | F6.8841.../2420197 | Abnormal sound issue Call By Customer Name :- Sugan . Mobile No :-9777988138 | Closed | Brigade Enterprises Limited | Surya Power Services - Kalyan Nagar | 7.2 | find out the issue exhaust bellow Bolt loose condition then find out the nut and properly refitted the bolt and tighted then now start and checked the engine running condition ok. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
79 | South | 211693037 | 07/02/2025 | 160 | 6H.8475.../2420324 | Abnormal sound isue preventive maintenance Call By Customer Name :- Ravishankar Mobile No:-9940681110 | Closed | Liberty High Scans Private Limited | Madhu Engineering Sales & Service - Teynampet,Chennai | 44 | After checked the vbelt tension low condition so properly tight for vbelt checked the belt tension with in limit ok. | Closed | Mr. NandhaGopal | Vendor visit | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
34 | North | 211666877 | 31/01/2025 | 125.4 | 4H.8042.C4../2420158 | Starting/Stopping Issue | Closed | Oxygen Hospital | SAAN Royal Power Solutions Private Limited - Rohtak | 2 | AdBlue Level found low on site so Top-up the same & remove the code | Closed | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
83 | South | 211691875 | 07/02/2025 | 58.5 | T4.8941.../2422324 | Starting Issue Call By Customer Name Ram .. No : 7899956153 | Closed | ADISHAKTI CARS PVT LTD | Prasad Power Engineers - Shimoga | 222 | Visited the site and observed the ERROR code so connected the I Connect toll and clear the all error codes and wiring connection (XDBK4 2A) internal wiring connection was problem so currented it and agine started the engine check the sound and smoke is normal condition, engine working in good condition | Closed | Mr. Anil Kumar H G | [9 empty] | Error Codes | 5 | 4 | 3 | 60 | Low
85 | South | 211690755 | 06/02/2025 | 30 | 3H.8902.../2421382 | Starting/Stopping Issue | Closed | ATC Telecom Infrastructure Private Limited | Ultimate Power Source - Kurnool | 4 | Automation issue from customer end | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
32 | North | 211677937 | 03/02/2025 | 30 | 3H.8902.../2421650 | Maintenance Due Alarm & Preventive Maintenance Call By Customer Name :- Aman Kumar Mobile No :- 8091800775 | Open | Sumcon infraventures LLP | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
87 | South | 211690634 | 06/02/2025 | 40 | 3H.8951.../2420755 | Diesel Leakage Problem Call by : Customer Name : Palguna Contact : 9440047705 | Closed | M/s. D. N. R. Poultry Farms | Ultimate Power Source - Chittoor | 64 | Diesel lekage problem found suction side benjo bolt loose. tighten the same | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
90 | South | 211690291 | 06/02/2025 | 0 | DV0.8501.C4../2420141 | FUEL PRIMING ISSUE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Inspected the dg notice the copper wash damage for diesel tank to water separator filter hose end, change the new copper wash issue solved | Closed | Mr. NandhaGopal | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
30 | North | 211678513 | 03/02/2025 | 40 | 3H.8951.../2421644 | Inspection/Maintenance | Task Start | BLUE BELL BAKERS | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
94 | South | 211689081 | 06/02/2025 | 58.5 | T4.8941.../2421652 | Starting/Stopping Issue | Closed | M/S S P POWER TECH | Laxmi Diesels - Rajahmundry | 18 | As per the customer complaint attended the site and checked that main supply fuse in control panel got failed so replaced the same Cranked the Engine running found satisfactory. | Closed | Mr. MD Saleem | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | North | 211714368 | 13/02/2025 | 20 | GP3.1021.../2420345 | INSTANCE ID:- 100777978 SITE ID:- I-UE-KEAT-ENB-G002 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLAM NAME:- RAAMPRAKASH SIR NUMBER:-8299599379 | Open | Reliance Jio Infocomm Limited | SAM Engineering corporation - Varanasi Cantt. |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211714150 | 13/02/2025 | 20 | GP3.1021.../2420387 | INSTANCE ID:-100784741 SITE ID:-I-UE-POLR-ENB-9130 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-ATUL SIR NUMBER:-8299698439 | Task Start | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211713973 | 13/02/2025 | 25 | GP3.8702.../2420543 | STARTING ISSUE | Open | ATC Telecom Infrastructure Private Limited | Vidyut Engineers - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | North | 211713777 | 13/02/2025 | 20 | GP3.8601.../2420107 | Oil leakage | Closed | DEEPAK TRAPATHI | S. R Engines Sales And Service - Mau | 52 | Found Oil cap loose so, tightness the same | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
6 | North | 211713687 | 13/02/2025 | 58.5 | T4.8941.../2421601 | Leakage Issue | Task Start | NAZRUL | SAM Engineering corporation - Varanasi Cantt. | 142 | Found oil seapage from sump after that tightness the Oil drain Nut then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | North | 211713521 | 13/02/2025 | 25 | GP3.8702.../2420404 | Voltage Fluctuation | Closed | Public Works Department Uttar Pradesh | Espiem Engines & Machines (P) Limited - Aligarh | 70 | Check & found the avr fuse burn so change the new fuse or start the engine work ok | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211713240 | 13/02/2025 | 160 | 6H.8475.../2420031 | Belt broken and I-bolt damage Email By - GOEM Name -Product Support | Task Start | TRAIN HIGH | OVN Industries Private Limited - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211713010 | 13/02/2025 | 160 | 6H.8475.../2320030 | Starting issue and abnormal sound issue Called by customer Name : Rabbani Number : 9015201975 | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 197 | Found V-belt loose tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
13 | North | 211712968 | 13/02/2025 | 15 | GP3.8501.../2420622 | Voltage fluctuation issue Call by KGD Name :-Pradeep Bhati NO :-9911316001 | Closed | Noida Diesel & Electrical Works. | Paluck Technologies Ltd. - Ghaziabad | 19 | Engineer visit on site found no any issue DG running well | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
16 | North | 211712587 | 13/02/2025 | 125.4 | 4H.8042.C4../2420760 | Starting Issue Call By Customer Name : Sachin No : 8802730007 | Closed | Ghaziabad Diesel Service. | Vidyut Engineers - Noida | 15.17 | Wrong report SR- Engineer visit the site found no any issue | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211715149 | 13/02/2025 | 35 | 3H.8902.../2422102 | Power supply issue Call by customer Name:Amit Number:8092455731 | Open | M/S NAVAKRITI ENTERPRISES | Globalline India Services Private Limited - Patna | 1.1 | visit Pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | North | 211678886 | 03/02/2025 | 40 | 3H.8951.../2320109 | Starting Issue Call By Customer Name :- Satish Kumar Mobile No :- 8803349159 | Task Start | Jammu Kashmir Cricket Association | Suraj Motor Store - Jammu |  | Visit Pending | Open | Ved Prakash Gupta | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | East | 211713492 | 13/02/2025 | 20 | GP3.8601.../2421651 | Automation Issue | Closed | Girish chanachur &snacks pvt. ltd | HACS Engineering and Tech Private Limited - Jamshedpur | 7.5 | customer complaint was that DG automatically switch auto to mannual mode and he want DG should not start at night without switch to mannual mode so SE installed an Switch in auto sensing wire. But the first issue is suspected as per SE that one another DG 15 KVA is there so may be someone else switch to mannual mode | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | North | 211717095 | 14/02/2025 | 125 | F6.9840.../2420045 | Automation Issue Call By Customer Name :- Manoj Kumar Mobile No :-9350058139 | Closed | IGS APPARELS | Paluck Technologies Ltd. - Ghaziabad | 5.6 | Update pending | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | WEST | 211666092 | 31/01/2025 | 500 | DV8.8501.C4../2420169 | Starting Issue Email By - Customer Name -Bhajanlal Sahu | Closed | Aspire Pharmaceuticals Pvt. Ltd. | Shree Engineering Service - Raipur | 56.27 | Engine was not cranking so checked the interface box connector and found that the XC1 male connecter 5No. wire pin was backout from its position. |  | Vijay patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | North | 211717025 | 14/02/2025 | 10 | GP3.8301.../2420131 | DG PROBLEM | Closed | ICICI Bank Limited | Pratap Diesels Pvt. Ltd. - JAIPUR | 166 | Found Emergency switch alarm after that check & found wire was loose then tightness the same then issue resolve | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
19 | North | 211716982 | 14/02/2025 | 10 | GP3.8301.../2420422 | KRM Issue and Abnormal sound issue Call by customer Name:Shashikant Agarwal . Number:8755130013 | Open | Shashi Kant Agarwal | Espiem Engines & Machines (P) Limited - Etawah |  | Visit pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | WEST | 211698929 |  | 40 | 3H.8951.../2421000 | Oil leakage Issue. Call By Customer. Name:- Santosh Mobile No.:9370050004 | Task Start | Santosh Kicheegoda Ailekopal ,C/o Banglore | KALA Care Global LLP - Nanded | 51 | oil leakage from flywheel side , change the oil seal | closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
8 | WEST | 211692136 |  | d+A227:H249 | 3H.8951.../2421000 | Oil leakage Issue. Call By Customer. Name:- Santosh Mobile No.:9834011158 | Closed | Santosh Kicheegoda Ailekopal ,C/o Banglore | KALA Care Global LLP - Nanded | 51 | oil leakage from flywheel side , change the oil seal | closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
49 | South | 211672975 | 01/02/2025 | 125.4 | 4H.8042.C4../2420460 | Starting Problem Call by : Customer Name : Badmanaban Contact : 9486985201 | Closed | V. P. Synergic Weld Solutions Pvt. Ltd. | Madhu Engineering Sales & Service - Kavaraipettai, Chennai | 6 | Found engine fuel system air lock,so check the suction pipe found Banjo side one copper washer missing,so added the copper washer, also suction tube hose clamp broken, changed the new hose clip, run the engine found one alarm showing 3364 urea tank level quality sensor signal not working, ad blue tank temperature high,so check the tank sensor found ok,one file updated then. Starting the engine load test found ok | Closed | Mr. NandhaGopal | GOEM issue | [8 empty] | Load Test | 5 | 4 | 3 | 60 | Low
13 | WEST | 211719396 | 15/02/2025 | 40 | 3H.8951.../2421121 | Starting Issue Call By Customer Name:-Raj Agarwal No:-9201629436 | Closed | Vakman Ventures | Natraj Power Tech - Indore | 27.7 | Emergency button was pressed by customer side, hence released the emergency button and started the DG. For this the customer was educated. | closed | Vijay Patil | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | WEST | 211718255 | 14/02/2025 | 500 | DV8.8501.C4../2420153 | DG NOT START Email by GOEM Name - HARSHADBHAI | Task Start | Parekh Power Systems | Unique Techno Services Pvt Ltd. - Dahej | 3 | No any issue found at site. | closed | Amit Shandilya | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | WEST | 211711057 | 12/02/2025 | 5.5 | CC1.1013.../2400486 | Silencer broken | Closed | Shree associates Infraventures Pvt Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 320 | Exhaust silencer found broken so need to replace the silencer. | OPEN | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | WEST | 211687654 | 06/02/2025 | 2.8 | AP1.7003.../2400109 | start issue Email by KGD Name - Surekha Auti | Task Close | CLARIDGES SEZ DEVELOPERS PRIVATE LIMITED | Transcreek Engineers Pvt. Ltd. - Panvel | 130 | Starter get proper supply but pinnon not working so change the starter. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | WEST | 211720044 | 15/02/2025 | 250 | F6.8841.../2420105 | Urea tank Laveal blow Ise Call By KGD Name: Priyanka Number: 9823036697 | Closed | Dr. Vaidya | Transcreek Engineers Pvt. Ltd. - Ambernath | 139 | Adblue level low so top up adblue. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
25 | WEST | 211723735 | 17/02/2025 | 125.4 | 4H.8042.C4../2420613 | Genset Trip | Task Start | ECONATURALS | Shree Engineering Service - Bilaspur | 7 | Mains R phase connection found loose so properly connect the wire. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
26 | WEST | 211716349 | 14/02/2025 | 125.4 | 4H.8042.C4../2420613 | Starting/Stopping Issue | Closed | ECONATURALS | Shree Engineering Service - Bilaspur | 3.2 | Dg not start due to dg auto sensing wire found open so connect the auto sensing wire. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
28 | WEST | 211700709 | 10/02/2025 | 20 | GP3.1021.../2420206 | INSTANCE ID:-100750213 SITE ID:- I-MH-VLPI-ENB-9004 CALL BY CUSTOMER// DG ISSUE:- DG AUTOMATION/ALARM ISSUE NAME:- RAHUL NUMBER:- 7083816723 | Closed | Reliance Jio Infocomm Limited | Mahalaxmi Diesels - Goa | 20 | No issue with dg | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
30 | WEST | 211719905 | 15/02/2025 | 25 | GP3.8702.../2420198 | Starting Issue Call By Service Dealer Name :- Saurabh No :- 7385403851 | Closed | Prapti Associates | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 14 | Emergency switch was pressed, Realease the same. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | WEST | 211714110 | 13/02/2025 | 400 | DV8.8542.C4../2420033 | Leakage Issue | Task Start | Magna Automotive India Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 97 | Cheaekd oil lekage from breather pipe. Then crank dg set .find abnormal noise Eng side. Then remove rocker cover checked rocker lever and bridge condition and aliment is ok. After move Eng on flywheel but Engine moving is hard. Then cheaked oil find silver particles . After remove oil filter find copper particles in oil filter . Find Eng enternaly friction parts . Need to check engine from inside. | closed | Jagdeep Saini | [9 empty] | Flywheel | 6 | 3 | 4 | 72 | Low
47 | South | 211673077 | 01/02/2025 | 250 | F6.8841.../2420216 | ECU amber lamp alarm issue Call by customer Name - Girish Kumar Number - 7678192216 | Closed | SLN coffee curing Pvt. Ltd | Surya Power Services - Kushalanagara | 79.5 | Adblue low topup the same. | Closed | Mr. Anil Kumar H G | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
38 | WEST | 211722774 | 16/02/2025 | 25 | GP3.8702.../2421430 | Trip_Genset_Low_Voltage | Task Start | PARTH CONSTRUCTION | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC |  | wrong reported by customer. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | WEST | 211721317 | 15/02/2025 | 25 | GP3.8702.../2421426 | Starting/Stopping Issue | Closed | P. C. Plastic | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 3 | XDBK 1, 2C wire connection found loose so tight the connection issue solved. | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
41 | WEST | 211725883 | 17/02/2025 | 15 | GP3.8501.../2420973 | Alternator issue Called by customer Name : AMIT BABAR Number : 9503874844 | Closed | M/s. Puja Petroleum. | Mahalaxmi Diesels - Sangli | 79 | wrong reporting by customer | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | NORTH | 211724900 | 17/02/2025 | 25 | GP3.8702.../2420424 | Tripping issue and low fuel level alarm issue Call By Customer Name :- Indrajeet Mobile No:-7838385811 | Task Start | A. S. A. Riders LLP. | Paluck Technologies Ltd. - Ghaziabad | 75 | Customer side panel issue & found no any leakage Customer topup the diesel over | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | NORTH | 211724044 | 17/02/2025 | 20 | GP3.1021.../2420470 | INSTANCE ID:-100784739 SITE ID:-I-UE-GKPR-ENB-G013 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME:-ASHWANI KUMAR NUMBER:-8299599398 | Open | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
5 | NORTH | 211723988 | 17/02/2025 | 750 | DV2.8501.C4../2420165 | DG ISSUE | Task Start | Vodafone | R K Engineers - Meerut | 49 | Dg trip with 633/3 Error code showing after that check & found Bank 1 Lifting pump not working - EDO of the Lifting pump | open | Sudhir Awasthi | Failed part | [8 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | NORTH | 211723891 | 17/02/2025 | 200 | 6H.8435.../2420205 | Starting/Stopping Issue | Task Start | Aisshpra Gems & Jewels. | S. R Engines Sales And Service - LUCKNOW | 901 | Found V-belt was loose so, tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
8 | NORTH | 211723560 | 17/02/2025 | 25 | GP3.8702.../2320003 | Battery Charging Issue call by customer name - Satyavir Sharma no - 9799207333 | Open | Pawan Tanay Chem Plast Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar |  | Visit pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | NORTH | 211723532 | 17/02/2025 | 20 | GP3.1021.../2420343 | VOC - Under voltage Alarm Problem Customer Name -Narsaram Customer Number -9667016198 Mode- SR Generated through CDI calling. | Open | Reliance Jio Infocomm Limited | Pratap Diesels Pvt. Ltd. - Nagaur |  | Visit pending | open | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | NORTH | 211723266 | 17/02/2025 | 20 | GP3.1021.../2420387 | INSATANCE ID:-100784741 SITE ID:-I-UE-POLR-ENB-9130 CALL BY CUSTOMER:- DG ISSUE :-DG UNDER ALRAM ISSUE NAME:-Atul NUMBER :- 8299698439 | Task Start | Reliance Jio Infocomm Limited | S.S. Enterprises - Allahabad |  | update pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | NORTH | 211722584 | 16/02/2025 | 30 | 3H.8902.../2420439 | Inspection/Maintenance | Task Start | Sachin Kumar Gupta | S. R Engines Sales And Service - Mau |  | Visit pending | open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | NORTH | 211722547 | 16/02/2025 | 58.5 | T4.8941.../2420787 | Battery Replacement Issue. Call By Customer Name :- Ram Saran Mobile No :-7982975198 | Open | SETHI BUILDCON | Vidyut Engineers - New Delhi |  | Visit pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
34 | WEST | 211701641 | 10/02/2025 | 160 | 6H.8475.../2420293 | DG Refurbishment | Task Close | B D Patil Sons Cold Storage | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 2 | Engine got damage due to accident , fitted new part in chargeble basis | closed | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | WEST | 211718184 | 14/02/2025 | 400 | DV8.8542.C4../2420150 | Leakage Issue | Task Start | Magna Automotive India Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 97 | Attend site with koel team Removed oil & oil sump observed 3rd & 7th no cylinder connecting rod bearing seized & bearing particuls observed in sump so need to change engine. | OPEN | Jagdeep Saini | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | East | 211713841 | 13/02/2025 | 20 | GP3.8601.../2420685 | Maintenance Due Alarm issue Call by Customer Name :-Akhilesh Prasad NO :-9778074795 | Open | VEERMAN ENTERPRISES | Gangpur Sales and Services - Sambalpur | 51 | NO Issue in DG Customer required service | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
17 | East | 211716451 | 14/02/2025 | 500 | DV8.8501.C4../2320020 | Starting Issue Call By Customer Name :- Vishwjeet Mobile No :-9778798930 | Closed | Action Ispat & Power. | Gangpur Sales and Services - Jharsuguda | 34 | Low adblue level,SE will visit to educate the customer and filling up the adblue,Issue resolved. | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
21 | North | 211716593 | 14/02/2025 | 20 | GP3.8601.../2420861 | Starting/Stopping Issue | Completed | Public Works Department Uttar Pradesh | Espiem Engines & Machines (P) Limited - Etawah | 48 | Update pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211756602 | 25/02/2025 | 10 | GP3.8301.../2420058 | Red lamp Alarm issue Call By Customer Name :- Saurabh Rai Mobile No :-7008755713 | Closed | SAINIK MINING AND ALLIED SERVICES LIMITED | Gangpur Sales and Services - Jharsuguda | 1749 | Customer Pressed the emergency switch after that released the switch ,Issue resolved | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
23 | North | 211716325 | 14/02/2025 | 40 | 3H.8951.../2420021 | DG mains contractor faulty | Closed | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Faridabad | 12 | Found mains contactor was foulty so, need to be replace | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
24 | North | 211716255 | 14/02/2025 | 320 | F6.8802.../2420330 | Starting/Stopping Issue | Closed | Hirohama India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 99 | DG not start in Auto, but check & found Customer do not complete sysnc the DG, Educate the customer for Sync | Closed | Gourav Sharma | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
14 | North | 211678097 | 03/02/2025 | 40 | 3H.8951.../2320070 | Starting Issue Call By Customer Name :-Atul Baranwal Mobile No :- 8960458371 | Task Start | KANSAI NEROLAC PAINTS LIMITED. | Paluck Technologies Ltd. - Ghaziabad |  | update pending | open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
27 | North | 211721312 | 15/02/2025 | 15 | GP3.8501.../2420469 | Starting/Stopping Issue | Open | Doon Associates | GLOBALVISION POWER SOLUTIONS PVT LTD - Srinagar |  | Update pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
30 | North | 211720890 | 15/02/2025 | 625 | DV0.8501.C4../2420014 | Sound/Vibration Issue | Open | T. C. Health Care Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 245 | Found V-belt teeth broken so, replace the V-belt then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
12 | North | 211678160 | 03/02/2025 | 20 | GP3.8601.../2420779 | Leakage Issue | Closed | AKSHAYPATRA EQUIPMENTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 12 | Oil leakage from oil drain pipe clamp was loose tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
33 | North | 211720334 | 15/02/2025 | 40 | 3H.8951.../2420661 | Leakage Issue | Closed | Shiv Engree | Deep Jyoti Electricals and Services - Shahjahanpur | 200 | Update pending | Open | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | North | 211678255 | 03/02/2025 | 57 | T4.8941.../2320093 | Starting Issue Call By Customer Name :- Rishabh Gupta Mobile No :- 9810539132 | Closed | ROHIN STEEL INDUSTRIES | OVN Industries Private Limited - New Delhi | 154.19 | Found the panel wiring loose in Distribution box tightness the same then issue resolve | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
36 | North | 211720085 | 15/02/2025 | 57 | T4.8941.../2320025 | Starting Issue Call By Customer Name :- Vivek Mobile No :-7011508129 | Closed | PSG ELECTRICALS | OVN Industries Private Limited - New Delhi | 62.17 | Update pending | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
37 | North | 211719895 | 15/02/2025 | 750 | DV2.8501.C4../2320007 | Trip_Genset_Low_Voltage | Open | Merino Industries Ltd. | Paluck Technologies Ltd. - Ghaziabad |  | Visit pending | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
10 | North | 211678288 | 03/02/2025 | 58.5 | T4.8941.../2421885 | Starting issue Call by customer Name - Tiwari Number - 9559191222 | Task Start | Lucknow Generator Wala | S. R Engines Sales And Service - LUCKNOW | 30 | Customer raise the complaint for starting issue, but when Engineer visit the site check the Dg found Under speed alarm but now DG in running condition found no any other issue | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
39 | North | 211719856 | 15/02/2025 | 125.4 | 4H.8041.../2420508 | Over voltage issue | Closed | Bharat Saka Gokai | Vidyut Engineers - New Delhi | 62 | Voltage set from AVR 230 found before 242 | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
9 | North | 211678302 | 03/02/2025 | 15 | GP3.8501.../2420683 | Leakage Issue | Task Close | Pradeep General Store | Espiem Engines & Machines (P) Limited - Aligarh | 432 | Found the oil leakage from oil gallery nut was loose tightness the same then issue resolve | Closed | Sudhir Awasthi | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
43 | North | 211719527 | 15/02/2025 | 40 | 3H.8951.../2420123 | Engine service due | Closed | Aryan Singh | Paluck Technologies Ltd. - Faridabad | 306 | Service done & Audio relay alarm reset the alarm then issue resolve | Closed | Kapil Solanki | [9 empty] | Relay | 5 | 4 | 3 | 60 | Low
8 | North | 211678665 | 03/02/2025 | 30 | 3H.8902.../2320045 | Smoke Issue & Silencer Faulty Call By Customer Name :- Punit Mobile No :-9643768190 | Closed | Born Max Gyane Clinic B. M. C. | Paluck Technologies Ltd. - Ghaziabad | 126 | Engineer visit the site check the DG set found no any problem in DG- Customer report the Wrong report | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
1 | East | 211722526 | 16/02/2025 | 320 | F6.8802.../2420176 | AMF Panel Power Supply Issue. Call By Customer, Name: -CHANDAN KUMAR SINGH Mobile No.:-8757084667 | Open | RADHESHYAM INFRA | Globalline India Services Private Limited - Arrah | 4 | Visit pending | OPEN | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
2 | East | 211721089 | 15/02/2025 | 15 | GP3.8501.../2420565 | Maintenance Due Alarm Issue And Red Lamp On ALrm Issue Call By Customer Name :-MR AMIT KUMAR Mobile No :- 9431822674 | Closed | Suprab Enterprises | Globalline India Services Private Limited - Begusarai | 65 | Maintenance alarm was showing so reset it and fuel level showing on mechanical gauge approx. 100 and on display showing 95% but as per customer it should be 70-80,So SE cheked for loose connection found no loose connection and then removed fuel senor from tank and checked for stuckness found ok then refitted and then saw found ok (85%) customer satisfied. | CLOSED | Prabhakar Kumar | [9 empty] | Maintenance | 4 | 3 | 2 | 24 | Low
4 | East | 211718455 | 14/02/2025 | 20 | GP3.8604.../2420174 | DG Air locking | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Muzaffarpur | 98 | DG was not starting showing under speed alarm as per customer complaint but SE tried to checked same issue DG was running helathy without alarm so he tried 4-5 time found no issue but he absorb that fuel suction pipe from fuel gauge to feed pump was not properly aligned he alinged and ensure tightening of all wiring connection of feed pump and panel. | CLOSED | Prabhakar Kumar | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
7 | East | 211717848 | 14/02/2025 | 40 | 3H.8951.../2420738 | Diesel not showing | Closed | JYOTISHMAN HARDWARE & GRILL | Hibreed Engineering Pvt. Ltd. - Nagaon | 511 | UPdate pending | CLOSED | Ujjwal Das | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
4 | North | 211678878 | 03/02/2025 | 125.4 | 4H.8041.../2420660 | Genset Tabit cover leakage Call By Customer. Name:-Lalit Tyagi Mobile No.:-9810138700 | Task Start | Sgs Diesel Power And Heavy Electrical. | Vidyut Engineers - Noida | 30.23 | Found the minor leakage from Rocker cover O' ring required need to be replace | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
3 | North | 211679406 | 03/02/2025 | 125.4 | 4H.8042.C4../2420912 | AMF Panel Issue Call By Customer Name :- Rajesh Mobile No :- 8445334200 | Task Start | VIVEKANAND CO-OP GROUP HOUSING SOCIETY LTD. | OVN Industries Private Limited - New Delhi |  | Customer panel - VMR setting change | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
11 | East | 211715149 | 13/02/2025 | 35 | 3H.8902.../2422102 | Power supply issue Call by customer Name:Amit Number:8092455731 | Closed | M/S NAVAKRITI ENTERPRISES | Globalline India Services Private Limited - Patna | 1.1 | NO issue in DG SE tried to resolved on call but customer was not ready for it,he was demanding for visit . SE visited site and found Emergency switch was pressed and found DC MCB was off. | CLOSED | Prabhakar Kumar | [9 empty] | MCB | 5 | 4 | 3 | 60 | Low
12 | East | 211721163 | 15/02/2025 | 125.4 | 4H.8041.../2420840 | Starting/Stopping Issue | Closed | AMPL Resources Pvt Ltd | Revenus Industries Pvt. Ltd. - Asansol | 62.4 | Error code 1761/14 due to AdBlue very low level,Top-up the AdBlue and checked all external parts found normal then start the engine running on load testing condition normal. | CLOSED | Prosanjit saha | [9 empty] | Load Test | 5 | 4 | 3 | 60 | Low
13 | East | 211719681 | 15/02/2025 | 30 | 3H.8902.../2420582 | Leakage Issue | Task Start | Maa Kali Bhandar | Revenus Industries Pvt. Ltd. - Contai | 32 | Visit Pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
15 | East | 211718792 | 14/02/2025 | 0 | 3H.8902.../2421621 | Low oil pressure | Task Start | ELMECH ENGINEERS | Revenus Industries Pvt. Ltd. - Howrah |  | UPdate pending | OPEN | Prosanjit saha | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
18 | North | 211717033 | 14/02/2025 | 500 | DV8.8501.C4../2320046 | Under voltage issue Callby OEM Name:Arjendra Singh Number:8146866339 | Task Start | SHUBH INDUSTRIES | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Update pending | Open | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low
22 | North | 211716360 | 14/02/2025 | 30 | 3H.8902.../2421225 | Starting Issue Call By Customer Name - Bushpreet singh Number - 8076271828 | Closed | DIVYANSHI POWER SOLUTION. | Paluck Technologies Ltd. - Ghaziabad | 60.65 | Found No any issue in DG | Closed | Kapil Solanki | [9 empty] | Unknown | 1 | 1 | 10 | 10 | Low