## Sorted
Sr. No | Incident Id | Creation Date | Kva Rating | Engine No | Customer Voc | Sr Status | Account Name | Service Dealer Name | Running Hrs | Observation | Incident Status | Asm Name | Rrt Remark | Priority
1 | 210381958 | 2024-02-08 10:48 | 125.4 | 4H.8041.../2320160 | Fuel leakage Issue Call By Customer Name:Mukesh Bansal No:9255891000 | Open | CNC. Solutions... | Paluck Technologies Ltd. - Faridabad | 12 | Fuel leakage from Return Line (Loose Connector) Tighten the same, Issue resolved. | Closed | Kapil Solanki |  | Low
2 | 210382661 | 2024-02-08 14:01 | 25 | GP3.8702.../2320015 | STARTING PROBLEM | Task Start | VISHAL POWER SYSTEMS | Vishal Power Systems - Karnal |  | Engine RPM not reflecting on GCU resulting DG trip with under speed alarm, Checked ECM CAN resistance & found 200 Ohms, replaced ECM from Float stock, issue resolved. | Closed | Kapil Solanki |  | Low
3 | 210382691 | 2024-02-08 14:14 | 125.4 | 4H.8041.../2320015 | Starting Issue & Battery Issue Call By Customer Name :Nitin Jain Mobile No :9958745874 | Task Start | Parswa Exports Pvt. Ltd. | Vidyut Engineers - Noida | 21 | Battery discharged at faster rate (Seems internal cell week) Replaced Battery issue resolved also need to install e-feed Pump as Engine starting in first crank with Hand Priming only | Closed | Kapil Solanki |  | Moderate
4 | 210382879 | 2024-02-08 14:59 | 57 | T4.8941.../2320010 | Panel Issue Email By - Service Dealer Name -Kartikey Rajput | Open | Rajeev Jetly | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 103 | As per complaint, SD team perform Load trail but any voltage related issue observed. | Closed | Kapil Solanki |  | Low
5 | 210383036 | 2024-02-08 15:25 | 200 | 6H.8435.../2320013 | hose clamp faulty. Email By - Service Dealer Name -Madan Chhimpa | Task Start | Zeniya Electech Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 3 | Coolant leakage from the water pump hose(hose clamp loose)change the clamp ,issue resolved. | Closed | Kapil Solanki |  | Moderate
6 | 210386639 | 2024-02-09 11:58 | 500 | DV8.8501.C4../2320038 | fuel pipe Leakage Email By - Service Dealer Name -VINIT KUMAR JAIN | Open | TRANS ACNR SOLUTIONS PRIVATE LIMITED | Power Trading Company - Bhiwadi ( Alwar) | 14 | Attend the DG Set check and find fuel pipe leakage( primary filter to water separator)Replace the fuel pipe. After than start the DG set check and found OK | Closed | Gourav Sharma |  | Low
7 | 210386848 | 2024-02-09 12:31 | 62.5 | T4.8941.../2320098 | Power Supply Issue Call By Customer Name :Trimohan Kumar Mobile No :9205829296 | Task Start | S K Generators | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 29 | Loose connection from changeover switch, dealer engineer suggested to customer correct the changeover. | Closed | Kapil Solanki |  | Low
8 | 210387236 | 2024-02-09 13:57 | 125.4 | 4H.8041.../2320134 | Error Code Issue Call By Customer Name:Mohmmad Asif Ahmad Number:8445820675 | Open | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 225 | SPN no-516166 FMI -0 Clear the DTC and top up the urea, issue resolved. | Closed | Sudhir Awasthi |  | Low
15 | 210390416 | 2024-02-10 12:27 | 125.4 | 4H.8041.../2320140 | DG issue | Task Start | AIRPLAZA RETAIL HOLDINGS PRIVATE LIMITED | Diesel Engineers Sales & Service - Ghaziabad | 65 | Urea level low issue, educate the customer the same. | Closed | Kapil Solanki |  | Low
2 | 210397140 | 2024-02-12 15:54 | 125.4 | 4H.8041.../2320186 | Black Smoke Issue Call By Customer Name :- Niraj Number :- 9837768335 | Open | Goldripe International Pvt. Ltd. | R K Engineers - Meerut | 39 | DG running in Auto mode and customer putting 60 to 70 % initial load( jerk load) also capturing the smoke video of engine throttle time, suggested to Put step load on DG (40 to 45%). | Closed | Sudhir Awasthi |  | Low
3 | 210396792 | 2024-02-12 14:47 | 200 | 6H.8435.../2320010 | Maintenance Due Alarm and Fuel Leakage Issue Call By Customer Name :-Sonilal Number :-9599382335 | Open | AGRAWAL METALS | Paluck Technologies Ltd. - Gurgaon | 3 | engine starting issue due to air lock problem in fuel line. | Closed | kapil solanki |  | Low
4 | 210396613 | 2024-02-12 13:46 | 160 | 6H.8475.../2320028 | Coolant Leakage Issue Call By Customer Name : Rabbani Sir Number : 9015201975 | Task Start | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 15.6 | Radiator hose leakage , tighten the clamp, issue resolved. | Closed | kapil solanki |  | Moderate
5 | 210396468 | 2024-02-12 13:15 | 500 | DV8.8501.C4../2320038 | Engine Starting Issue. Email By - Service Dealer Name -VINIT KUMAR JAIN | Task Start | TRANS ACNR SOLUTIONS PRIVATE LIMITED | Power Trading Company - Bhiwadi ( Alwar) | 17.39 | Starting issue due to 30 amps fuse blown, engine start command given but not cranked and show start to fail ,changed the fuse(under campaign),issue resolved. | Closed | Gourav sharma |  | Low
9 | 210395496 | 2024-02-12 09:42 | 500 | DV8.8501.C4../2320083 | Starting Issue Call By Customer Name:Manoj Kumar No:9996545880 | Open | Friction Metal Fibers (I) Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 5.2 | starting issue in 500, kva,flashed ECU with Slow Ramp up file DV8- 1234, Issuse resolved | Closed | kapil solanki |  | High
10 | 210395385 | 2024-02-12 08:52 |  | 5H.5301.../2300001 | 94 PIN wiring harness replacement required Email By Koel Person Name -Saurav Kumar | Open | Manitou Equipment India Pvt. Ltd. | Vidyut Engineers - Noida |  | BSV Line rejection issue | Closed | kapil solanki |  | Low
2 | 210400852 | 2024-02-13 17:00 | 30 | 3H.8902.../2320194 | Trial Taken | Task Start | HS. Enterprises | H.S Enterprises - Leh | 1 | Cold starting trial by CRE at Low ambient Temp & High altitude. | Closed | Ved Gupta |  | Low
3 | 210400794 | 2024-02-13 16:55 | 125.4 | 4H.8041.../2320096 | Starting issue Call by Customer Name :-Dishant . Number :- 9571603080 | Open | Dr. Manoj Kumari Yadav | Power Trading Company - ALWAR | 12.2 | Engine starting issue due to week battery (Battery charger MCB in trip/off condition), after charging the battery issue resolved. | Closed | Gaurav Sharma |  | Moderate
4 | 210400808 | 2024-02-13 16:52 | 40 | 3H.8951.../2320113 | Trial Taken | Task Start | HS. Enterprises | H.S Enterprises - Leh | 1 | Cold starting trial by CRE at Low ambient Temp & High altitude. | Closed | Ved Gupta |  | Low
5 | 210400676 | 2024-02-13 16:30 | 160 | 6H.8475.../2320025 | Oil Leakage Issue Call by service Dealer Name : Neha No : 9306961004 | Task Start | Striker Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 2 | fuel leakage from e-Feed Pump NRV benzo, Replaced washer issue resolved. | closed | Kapil Solanki |  | Low
7 | 210399657 | 2024-02-13 14:09 | 125.4 | 4H.8041.../2320036 | R Phase Voltage down issue Call By Customer Name:Shivender Kaushik No:8368265246 | Task Start | Trend Setters International | Paluck Technologies Ltd. - Gurgaon | 23 | DG reverse power shut down found in event log. capacitor bank was running on load educated customer about same also urea level is not showing in controller | closed | Kapil Solanki | Update required | Low
8 | 210399374 | 2024-02-13 12:54 | 40 | 3H.8951.../2320010 | Starting Issue Call By Customer Name :-Ravindra Kumar Number :-9350444479 | Task Start | Ganpati Enterprises | Vishal Power Systems - Karnal | 8 | Air lock issue due to fuel leakage at benzo set the benzo issue resolved. | closed | Kapil Solanki |  | Low
9 | 210399319 | 2024-02-13 12:39 | 125.4 | 4H.8041.../2420017 | Starting Issue Call By Customer Name :-Mahesh Mittal Number :-9226513807 | Open | Modern Process House | R K Engineers - Meerut | 4.13 | E-feed Pump not starting due to negative missing from Circuit (1C2 Wite connected at 102) Corrected the same, Issue resolved. | closed | Sudhir Awasthi |  | Low
11 | 210399106 | 2024-02-13 12:08 | 125.4 | 4H.8041.../2320200 | Starting issue Call By Customer Name :-Vinay Gupta Number :-8707336707 | Task Start | Nagarjuna Construction Company Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 13 | DEF tank level sensor stuck in range at 0%, Physicallt DEF available in Tank, Cleaned Level sensor, issue resolved. | closed | Kapil Solanki |  | Low
12 | 210399023 | 2024-02-13 11:41 | 250 | F6.8841.../2320019 | Voltage issue Call by Customer Name :-Narendra Nagar Number :- 9811818373 | Task Start | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 31 | Jerk load at site due to which (195 Amp) ,voltage was fluctuating same advised customer for load issue. | closed | Kapil Solanki |  | Low
13 | 210398999 | 2024-02-13 11:40 | 320 | F6.9051.../2300002 | Starting Issue Email By Service Dealer Name :-Sonu Rai | Open | PERENNIAL TECHNOLOGY PVT LTD | Paluck Technologies Ltd. - Gurgaon | 584 | SPN-5461, FMI-0(SCR monitoring alarm) after connecting tool and clear the DTC issue resolved. | closed | Kapil Solanki |  | Low
14 | 210398974 | 2024-02-13 11:35 | 82.5 | 5H.8901.../2320015 | GCU Flashing Issue Email By Service Dealer Name :-Amitabh Kushwaha | Task Start | EVEREST STEEL FABRICATOR | Paluck Technologies Ltd. - Faridabad | 70 | Urea level was not displaying in GCU ,after flashing ECU issue resolved. | closed | Kapil Solanki | Need updates | High
15 | 210398941 | 2024-02-13 11:29 | 160 | 6H.8475.../2320035 | Oil Leakage Issue Call By Customer Name :Jyoti .. Mobile No :7503944746 | Open | BEETA CONVEYORS PVT LTD | OVN Industries Private Limited - New Delhi | 5.21 | Coolant leakage from (Thermosat to radiator hose), tighten hose clamps issue resolved. | closed | Kapil Solanki |  | Moderate
1 | 210404677 | 2024-02-14 16:59 | 160 | 6H.8475.../2320011 | Starting Issue Call By Customer Name :-Anip Harbajan Number :-9555927287 | Open | Kashish Plastic Industries | Diesel Engineers Sales & Service - Ghaziabad | 26 | Due to loose Fan belt abnormal sound produced,after tighten the fan belt issue resolved. | Closed | Kapil Solanki |  | Low
2 | 210403785 | 2024-02-14 15:13 | 30 | 3H.8902.../2320159 | Electrical Wiring Issue | Task Start | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 1.38 | AMF panel connection issue after connecting a negative wire for sensing from AMF panel issue resolved. | Closed | Kapil Solanki |  | Low
3 | 210403565 | 2024-02-14 14:15 | 125.4 | 4H.8041.../2320105 | Automation Issue Call By Service Dealer Name :- Sohit Number :- 8287515158 | Task Start | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 363 | loose cranking relay wire and low Ad blue level, after tighten the relay wire and top Ad blue issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210403490 | 2024-02-14 13:56 | 250 | F6.8841.../2320005 | Red Lamp on alarm Issue Call By Customer Name:Vinod Kumar No:9728005448 | Open | ALFA FLEXITUBES ( P ) LTD | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 26 | Red lamp alarm due to SPN-516166 After connecting the ikonnect tool,and clear the DTC issue resolved. | Closed | Kapil Solanki |  | Low
8 | 210402542 | 2024-02-14 10:46 | 250 | F6.8841.../2320017 | Tripping Issue Call By: Customer Name :Rajinder Saini No :9716627693 | Open | Power Control System | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 32 | Low urea level (spn -1761) alarm displayed in controller.DEF top up done. Engineer advised the customer for DG service. | Closed | Kapil Solanki |  | Low
10 | 210402443 | 2024-02-14 10:29 | 500 | DV8.8501.C4../2320038 | Starting Issue Call By Service Dealer Name :Devendra Yadav Mobile No :9813602580 | Task Start | TRANS ACNR SOLUTIONS PRIVATE LIMITED | Power Trading Company - Bhiwadi ( Alwar) | 18.4 | Air lock issue in fuel line due to kink in Fuel line, after changing the cu washer issue resolved. | Closed | Gourav Sharma |  | Low
1 | 210413394 | 2024-02-16 17:54 | 250 | F6.8841.../2320047 | Ureya Issue Call By Customer Name :Laxmi Narayan Number :9899515513 | Open | Rai Industrial Power Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Customer just call for enquiry at Heldesk (DEF topup process), resolved telephonically. | Closed | Kapil Solanki |  | Low
2 | 210410747 | 2024-02-16 12:13 | 160 | 6H.8475.../2320028 | Fuel sensor Issue Email By Service dealer Name:-Rakesh Singh | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 16.4 | Fuel gauge wire loose. Just detach & reconnect the connector, Issue resolved. | Closed | Kapil Solanki | efsr check for photo | Low
3 | 210410700 | 2024-02-16 12:00 | 320 | F6.8802.../2320080 | Voltage issue Call By Customer Name:Rhul kumar Singh Number:9971966432 | Closed | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 31.28 | Customer not allowed to check the DG set , he said to planned it for tomorrow when Electrician For AMF to come | Closed | Kapil Solanki |  | Low
4 | 210410335 | 2024-02-16 10:56 | 125.4 | 4H.8041.../2320026 | Low oil pressure alarm issue And Voltage fluctuation issue Call by customer Name: Yash Pal Number:9599117169 | Closed | SAMPARK Global Logistics Private Limited | Paluck Technologies Ltd. - Faridabad | 31 | Due to loose neutral wire in changeover voltage fluctuates after tighten the neutral connection issue resolved (Customer says that engine have starting problem in morning) | Closed | Kapil Solanki |  | Low
6 | 210409598 | 2024-02-15 18:35 | 160 | 6H.8475.../2320035 | Starting issue Call by customer Name: Jyoti Number:7503944746 | Closed | PUSHPANJALI HOSPITAL | OVN Industries Private Limited - New Delhi | 5.38 | Starting issue due to air in fuel line after checked found that Electric feed pump thimble broken, after connected and tighten thimble issue resolved | Closed | Kapil Solanki | efsr check for photo | Low
7 | 210407612 | 2024-02-15 14:15 | 125.4 | 4H.8041.../2320056 | Starting Issue Call By Customer Name:Devendar Sharma Number:8950256020 | Closed | Srihans Technologies Exports Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 8 | Safety monitor on delay show in controller without actual starting of DG, after flashing ECU issue resolved | Closed | Kapil Solanki |  | High
8 | 210407607 | 2024-02-15 14:05 | 125.4 | 4H.8041.../2320065 | Starting Issue Call By Customer Name:Devendar Sharma Number:8950256020 | Closed | Srihans Technologies Exports Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 14 | Safety monitor on delay show in controller without actual starting of DG , after flashing ECU issue resolved | Closed | Kapil Solanki |  | High
9 | 210407590 | 2024-02-15 13:56 | 160 | 6H.8475.../2320030 | Fuel sensor Issue Call By Customer Name:Rabbani Number:9015201975 | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 23.1 | Fuel level showing in EMS is not proper After retightening connector issue resolved | Closed | Kapil Solanki | Need details | Low
10 | 210407079 | 2024-02-15 12:05 | 82.5 | 5H.8901.../2320091 | Starting Issue Call BY Customer Name : Rajesh No : 8851139581 | Closed | OP KHAITAN & CO | Vidyut Engineers - New Delhi | 9.52 | Mains Battery Charger not connected, Connected the same, Issue resolved. | Closed | Kapil Solanki | Commisioing need to check | Moderate
11 | 210406831 | 2024-02-15 11:17 | 125.4 | 4H.8041.../2320174 | Starting Issue Call By Customer Name :-Umesh Mehra Number :- 9958393148 | Closed | Kalka Krishna Engineering | Vidyut Engineers - New Delhi | 12 | E-feed Pump NRV valve chocked after cleaning the NRV valve issue resolved. | Closed | Kapil Solanki | Photo to share and one pager | Low
13 | 210406413 | 2024-02-15 09:46 | 125.4 | 4H.8041.../2420018 | OIL LEAKAGE | Closed | Sharkline Appliances | M/s OM Diesels Pvt. Ltd. - HISAR | 4 | Engineer attend the Site and found that oil leakage at drain plug after cleaning and tightening drain plug issue resolved | Closed | Kapil Solanki |  | Low
3 | 210415113 | 2024-02-17 14:43 | 82.5 | 5H.8901.../2320042 | Starting Issue Call By Customer Name :Mohmmad Asif Mobile No :8445820675 | Closed | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 22 | Battery Terminal loose. Tighten the same, Issue resolved. | Closed | Sudhir Awasthi | CC check | Moderate
6 | 210414828 | 2024-02-17 13:11 | 500 | DV8.8501.C4../2320014 | Starting Issue Call By: Customer Name :Saurabh Goyal No :9456264710 | Closed | RPS CHEMICAL INDUSTRIES PRIVATE LIMITED | R K Engineers - Muzaffarnagar | 71 | Air lock issue, bleed the system, issue resolved. | Closed | Sudhir Awasthi |  | Low
7 | 210414768 | 2024-02-17 13:06 | 125.4 | 4H.8041.../2320171 | Starting Issue And Display Issue Call By Customer Name :Rajvir Saini Mobile No :9873318777 | Closed | New United Enterprises | Paluck Technologies Ltd. - Faridabad | 7.1 | Fuel gauge float unit stuck hence showing '0' Reading. Detached unit & make its movement free, Issue resolved. | Closed | Kapil Solanki | efsr check for photo | Low
8 | 210414663 | 2024-02-17 12:38 | 57 | T4.8941.../2320040 | Load ISsue And Tripping issue Call By Customer Name : Umesh Dhavan Mobile No :9213428845 | Closed | Hariom Tools | Paluck Technologies Ltd. - Faridabad | 32 | customer equipment grinder was not working as it was there panel connection issue same is done by customer also CNC was tripping this also is related to panel same has been conveyed to customer. | Closed | Kapil Solanki |  | Low
9 | 210414447 | 2024-02-17 11:48 | 320 | F6.8802.../2320044 | Starting Issue Call By Customer Name :- Anand Prakash Number :-8449011760 | Closed | K. K. Fabs | R K Engineers - Meerut | 2.42 | As per Customer request, Installed Remote start switch in Customer office (Taken output from 49 Pin of Deepsea), SD team mentioned DG Ventillation issue, Issue closed. | Closed | Sudhir Awasthi | CC check for space constraints | Low
10 | 210414106 | 2024-02-17 10:37 | 82.5 | 5H.8901.../2320063 | Starting Issue Call By Customer Name :-Dinesh Kumar Number :-7240482041 | Task Start | JMCC. Infra Project Pvt. Ltd. | Power Trading Company - ALWAR |  | Mail dropped for cancellation. | Closed | Gourav Sharma | Need update. Shifting activity | Low
1 | 210420691 | 2024-02-19 22:20 | 250 | F6.8841.../2420009 | Line Rejection | Task Start | The National Media Centre Cooperative House | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2 | ECU malfunctioning alarm (SPN/FMI : 3031/14) shown in controller, connect the ikonnet tool and clear the DTC issue resolved. | Closed | Gourav Sharma | Data to be share with AME of trail with 125 kva | High
2 | 210419938 | 2024-02-19 16:29 | 125.4 | 4H.8041.../2320059 | Diesel leakage issue Call By: Customer Name :Chandrdev .. No :9643819750 | Task Start | Sudh Investments Private Limited | Vidyut Engineers - Noida | 98.35 | fuel leakage issue due to loose fuel pipe, tighten the same issue resolved. And also SPN- 516166/0 shown in controller, connect the ikonnet tool and clear the DTC | Closed | Kapil Solanki |  | Low
3 | 210419401 | 2024-02-19 15:36 | 30 | 3H.8902.../2320028 | Oil Leakage issue Call by Customer Name:- Mahendra Number:- 9599463164 | Task Start | High Tech Profile Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 20.56 | Oil leakage issue due to loose oil filter, tighten the same, issue resolved. | Closed | Sudhir Awasthi |  | Moderate
4 | 210418868 | 2024-02-19 13:18 | 125.4 | 4H.8041.../2320105 | Automation Issue Call By Service Dealer Name :- Sohit Number :- 8287515158 | Closed | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 412 | SPN 157/14,SPN 51/0,SPN 516166/0 code in DM 2 genset tripping after sometime no fixed pattern. Engineer visited the site and found no abnormility | Closed | Kapil Solanki | KRM data check Service history | Low
5 | 210418013 | 2024-02-19 10:08 | 82.5 | 5H.8901.../2320069 | Mobil leakage Issue Call By Customer Name : Rakesh Yadav Mobile No :8010612178 | Closed | FASHION MAKERS INDUSTRIES PRIVATE LIMITED | Vidyut Engineers - Noida | 80 | Coolant leakage due to over flow from recovery bottle, as customer misunderstood leakage but as visited tighten all the clamp of hoses. | Closed | Sudhir Awasthi |  | Low
1 | 210420691 | 2024-02-19 22:20 | 250 | F6.8841.../2420009 | Line Rejection | Task Start | The National Media Centre Cooperative House | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2 | ECU malfunctioning alarm (SPN/FMI : 3031/14) shown in controller, connect the ikonnet tool and clear the DTC issue resolved. | Closed | Gourav Sharma | Data to be share with AME of trail with 125 kva | High
2 | 210419938 | 2024-02-19 16:29 | 125.4 | 4H.8041.../2320059 | Diesel leakage issue Call By: Customer Name :Chandrdev .. No :9643819750 | Task Start | Sudh Investments Private Limited | Vidyut Engineers - Noida | 98.35 | fuel leakage issue due to loose fuel pipe, tighten the same issue resolved. And also SPN- 516166/0 shown in controller, connect the ikonnet tool and clear the DTC | Closed | Kapil Solanki |  | Low
3 | 210419401 | 2024-02-19 15:36 | 30 | 3H.8902.../2320028 | Oil Leakage issue Call by Customer Name:- Mahendra Number:- 9599463164 | Task Start | High Tech Profile Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 20.56 | Oil leakage issue due to loose oil filter, tighten the same, issue resolved. | Closed | Sudhir Awasthi |  | Moderate
4 | 210418868 | 2024-02-19 13:18 | 125.4 | 4H.8041.../2320105 | Automation Issue Call By Service Dealer Name :- Sohit Number :- 8287515158 | Closed | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 412 | SPN 157/14,SPN 51/0,SPN 516166/0 code in DM 2 genset tripping after sometime no fixed pattern. Engineer visited the site and found no abnormility | Closed | Kapil Solanki | KRM data check Service history | Low
5 | 210418013 | 2024-02-19 10:08 | 82.5 | 5H.8901.../2320069 | Mobil leakage Issue Call By Customer Name : Rakesh Yadav Mobile No :8010612178 | Closed | FASHION MAKERS INDUSTRIES PRIVATE LIMITED | Vidyut Engineers - Noida | 80 | Coolant leakage due to over flow from recovery bottle, as customer misunderstood leakage but as visited tighten all the clamp of hoses. | Closed | Sudhir Awasthi |  | Low
1 | 210422939 | 2024-02-20 15:17 | 125.4 | 4H.8041.../2320194 | Error Code issue Email By Service dealer Name:-Devender Yadav | Task Start | Shri Ashwini Saxena Hospital | Power Trading Company - Rewari | 14.33 | Fuel leakage from Main Fuel pipe due to loose banjo, Tighten the same also replaced Copper washer issue resolved. | Closed | Gourav Sharma |  | Low
3 | 210422693 | 2024-02-20 14:46 | 82.5 | 5H.8901.../2320043 | Automation Issue Call By Customer Name :- Vijendra .. Mobile No :- 9416517717 | Task Start | Mr. Ravinder Kumar | M/s OM Diesels Pvt. Ltd. - Rohtak | 4 | DG auto starting enabled 'Remote start' setting in controller, Issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210422499 | 2024-02-20 14:12 | 125.4 | 4H.8041.../2320018 | Starting Issue Call By Customer Name-Papu Singh Mobile No-9718863311 | Task Start | SR. Power Engineers | Vidyut Engineers - Noida | 16.5 | Commissioned on 06-Dec-23, Battery in discharged condition as mains Charger not connected, Connedcted the same, Issue resolved. | Closed | Kapil Solanki |  | Moderate
6 | 210421356 | 2024-02-20 10:58 | 125.4 | 4H.8041.../2320036 | Voltage Â Issue Call By Customer Name :Shivender Kaushik Mobile No :8368265246 | Closed | Trend Setters International | Paluck Technologies Ltd. - Gurgaon | 29 | R-Phase GCU Input wire connection loose at Fuse junction, Tighten all Connections, Issue resolved. | Closed | Kapil Solanki |  | Low
8 | 210421142 | 2024-02-20 10:18 | 160 | 6H.8475.../2320025 | Battery Charging Issue Call By: Customer Name :Ankush . No :9990250454 | Task Start | Striker Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 2.55 | Commissioned on 14-Jan-24, Battery Charger not connected, Connedcted the same, Issue resolved. | Closed | Kapil Solanki |  | Moderate
1 | 210427651 | 2024-02-21 16:30 | 57 | T4.8941.../2320085 | Starting Issue Call By Customer Name : Sachin Khare Mobile No : 9999436017 | Task Start | Sunder Mavi Hospital | Diesel Engineers Sales & Service - Ghaziabad | 45 | DG starting issue due to Air Lock in Fuel line, Top up Diesel & Bleed Fuel line , Issue resolved. | Closed | Kapil Solanki | Merge issue. KRM data check | Low
2 | 210427233 | 2024-02-21 15:29 | 320 | F6.8802.../2420001 | Radiator Hose Pipe Coolant Leakage | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 1 | Line rejection case, Coolant leakage issue from 'Radiator Bottom tank to Engine Hose' due to Loose clip, Tighten the same, Issue resolved. | Closed | Kapil Solanki |  | Moderate
3 | 210427015 | 2024-02-21 14:50 | 40 | 3H.8951.../2320016 | Starting Issue Call By Customer Name :Gaurav Gupta Mobile No :9582116957 | Closed | A. & G. Hospitality | Vidyut Engineers - Noida | 7.41 | Under speed alarm due to loose Battery connections, tighten the same, Issue resolved. | Closed | Kapil Solanki | Need to check | Moderate
4 | 210426590 | 2024-02-21 13:06 | 62.5 | T4.8941.../2420011 | Tripping Â Issue Call By Customer Name :Vikas Mobile No :9810500690 | Closed | Castor Wheels India | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | Non KOEL AMF panel auto, no Issue with DG just educated Customer, Issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210426345 | 2024-02-21 12:08 | 320 | F6.8802.../2320024 | Starting issue Call By Customer Name :- Kalishankar Varma No :- 9811082359 | Task Start | KLK. Venture Pvt. Ltd. | Vidyut Engineers - Noida | 29.21 | SPN/FMI : 1761/16, Low DEF level in tank, Top Up the same, Issue resolved. | Closed | Kapil Solanki |  | Low
8 | 210425606 | 2024-02-21 09:45 | 320 | F6.8802.../2320038 | Tripping Â Issue Call By Customer Name :Dehal Pandey Mobile No :9812497330 | Task Start | Pl Footwear P. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | SPN/FMI : 1761/16, Low DEF level in tank, Top Up the same, Issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210431538 | 2024-02-22 17:17 | 160 | 6H.8475.../2320014 | Ad Blue Level Issue Call By Customer Name : Ram Das Mobile No :9012533754 | Task Start | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 3.28 | SPN/FMI-3031/14, 522120/19,522122/19 ,FMI-(DM 1) Code shown in controller, DEF Top up & ECU flashing done, issue resolved. | Closed | Sudhir Awasthi |  | High
7 | 210430440 | 2024-02-22 15:33 | 320 | F6.8802.../2320080 | ECU Mall Facing Alarm Issue Call By Customer Name : Rahul kumar Mobile No :9593182067 | Task Start | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 45.29 | SPN/FMI -3031/14,1761/16,5461516/0 Code shown in controller, after that connect the ikonnect tool and clear all DTC issues resolved. | Closed | Kapil Solanki |  | Low
9 | 210430409 | 2024-02-22 15:29 | 125.4 | 4H.8041.../2320037 | Starting Issue Email By Service Dealer Name-Shiv | Closed | MAHNA LEATHERS PVT. LTD. | Vidyut Engineers - Noida | 13.19 | SPN/FMI-516166/0 connect the ikonnect tool, clear the DTC issue resolved. | Closed | Kapil Solanki |  | Low
10 | 210430220 | 2024-02-22 14:51 | 62.5 | T4.8941.../2320098 | Tripping Issue And Control Panel Issue Call By Customer Name : Sanjay Lothara Mobile No : 9811292515 | Closed | S K Generators | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 134 | Tripping issue due to loose engine panel wiring connector ,also NO & NC not displayed in controller. After that, tighten the connector and the NO , NC switch, issue resolved. | Closed | Kapil Solanki | Need details | Low
11 | 210429663 | 2024-02-22 12:52 | 125.4 | 4H.8041.../2320128 | Red Light Alarm Issue Call By Customer Name : Sahil Rana No : 7300651325 | Closed | KALYAN JEWELLERS INDIA LTD. | OVN Industries Private Limited - New Delhi | 16.7 | Issue from customer panel side engine is running ok . | Closed | Kapil Solanki | Efsr need to check | Low
12 | 210429479 | 2024-02-22 12:13 | 125.4 | 4H.8041.../2320015 | Starting Issue Call By Customer Name :- Krishna Number :- 9718578511 | Task Start | Parswa Exports Pvt. Ltd. | Vidyut Engineers - Noida | 26 | Starting issue due to Air lock after Fitment electric feed pump kit, issue resolved. | Closed | Kapil Solanki |  | Low
14 | 210429084 | 2024-02-22 10:56 | 125.4 | 4H.8041.../2320194 | Error Code Issue. Email By - Service Dealer Name -Devender Yadav | Task Start | Shri Ashwini Saxena Hospital | Power Trading Company - Rewari | 14.55 | Wrong DEF transfer line connection made by GOEM (Tank to SM Inlet & Return interchganged), Corrected the same, Issue resolved | Closed | Gourav Sharma | Commisioing need to check. And check points | Low
15 | 210428709 | 2024-02-22 09:44 | 125.4 | 4H.8041.../2320090 | Starting Issue Call By Customer Name :-Rajesh Kumar Number :- 7042659373 | Task Start | TAURUS READY MIXED CONCRETES | OVN Industries Private Limited - New Delhi | 409.5 | Engine starting issue due to air lock in fuel line , replaced the all cu washer issue resolved. | Closed | Kapil Solanki |  | Low
1 | 210445134 | 2024-02-25 14:17 | 125.4 | 4H.8041.../2320202 | Oil leakage issue Call By Customer Name :- Vinit Singal No :- 6284737475 | Open | Eden Garden | M/s OM Diesels Pvt. Ltd. - Rohtak | 22 | oil leakage due to loose flywheel oil seal plate after that clean and tighten the oil seal plate issue resolved | Closed | Kapil solanki | Oil seal and surface photos | High
2 | 210445110 | 2024-02-25 13:51 | 40 | 3H.8951.../2320078 | Starting Issue Call By: Customer Name :Ashu No :9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 45.5 | Starting issue due to ECM switched supply missing as relay card defective after that change the same, issue resolved | Closed | Kapil solanki | Part need to dispatch | Low
3 | 210445100 | 2024-02-25 12:58 | 57 | T4.8941.../2320261 | Under speed alarm issue Call By Customer Name :- Ashok ... No :- 7678512026 | Task Start | Kalina Overseas Pvt. Ltd. | Vidyut Engineers - Noida | 14.55 | SPN 97/5 water in fuel alarm, Physically no water available. after that connect the ikonnect tool and clear the DTC issue resolved | Closed | Kapil solanki | Tommorow discussion | Low
5 | 210442436 | 2024-02-24 16:19 | 250 | F6.8841.../2420010 | Starting issue Call by customer Name: Mohan lal Yadav Number:9717616023 | Task Start | The National Media Centre Cooperative House Building Society Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 3 | ECU Protection lamp on, Just Reset GCU alarm that, issue resolved | Closed | Kapil solanki | Tommorow discussion | High
6 | 210440441 | 2024-02-24 13:27 | 125.4 | 4H.8041.../2320169 | White Smoke Issue Call By Customer Name :rajnikant Sharma Mobile No :9312404079 | Closed | DIHAAN ENTERPRISES | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 13 | White smoke issue due to water mixed in fuel, SD team suggested Customer need replace fuel filter as well as Fuel tank cleaning, decision pending from Customer side & insisting for Warranty support. | Closed | Kapil solanki | Tommorow discussion | Moderate
7 | 210439926 | 2024-02-24 12:22 | 125.4 | 4H.8041.../2420038 | Diesel leakage Issue Call By Customer Name :- Sanjay Varma No :- 9278336162 | Closed | SR. Power Engineers | Vidyut Engineers - Noida | 5 | Fuel leakage from Electric feed pump T socket(Multiple Points) after tighten all Connections socket and start the engine issue resolved | Closed | Kapil solanki | GOEM issue | Low
8 | 210439910 | 2024-02-24 12:19 | 320 | F6.8802.../2320055 | FUEL SENSOR NOT WORKING Email By - Service Dealer Name -VINIT KUMAR JAIN | Closed | AJANTA CHEMICAL INDUSTRIES | Power Trading Company - Bhiwadi ( Alwar) | 8.58 | Low fuel level alarm shown issue due to loose connector . | Closed | Gourav sharma | Photo required. Tommorow will discuss | Low
9 | 210439367 | 2024-02-24 11:24 | 82.5 | 5H.8901.../2320045 | Starting Issue Call By Customer Name :-Dilip Kumar Number :-9958134859 | Closed | Concept Engineers I. Pvt. Ltd. | Vidyut Engineers - Noida | 17.44 | Battery discharge due to loose battery connection after tighten the battery connection issue resolved | Closed | Kapil solanki | Tomorrow will discuss | Moderate
10 | 210438663 | 2024-02-24 10:28 | 320 | F6.8802.../2320029 | Error Code Issue Email By - Service Dealer Name -Shiv | Closed | Mangla Design Lab U/O MAIPL | Vidyut Engineers - Noida | 62.16 | SPN 5461/8 code shown in controller after that connect the ikonnect tool and clear the DTC issue resolved | Closed | Kapil solanki | Details from Gunjan | Low
11 | 210438486 | 2024-02-24 09:57 | 40 | 3H.8951.../2320024 | Starting Issue Call By Customer Name :-Bhaskar .. Number :-8218112739 | Task Start | GENESIS ENTERPRISES PVT. LTD. | Espiem Engines & Machines (P) Limited - Aligarh | 110 | SPN 157/14 code shown in controller after that connect the ikonnect tool and clear the DTC but sometimes does not start. | Closed | Sudhir Awasthi | PIR | Low
13 | 210438043 | 2024-02-23 19:25 | 57 | T4.8941.../2320090 | Starting Issue Call By Customer Name :- Anil . No :- 9818545301 | Task Start | SGH Enterprises | OVN Industries Private Limited - New Delhi |  | 13 RB1 (RL2) relay could not get 12 volt and checked 2A6 (X2) fuse is damaged , replaced the fuse issue resolved | Closed | Kapil Solanki | Need reispection for electric load | Low
15 | 210435027 | 2024-02-23 12:19 | 500 | DV8.8501.C4../2420005 | Oil Leakage Email By - Service Dealer Name -Sonu Rai | Closed | Auto International India Ltd. | Paluck Technologies Ltd. - Gurgaon | 15 | Oil leakage from header cooler adapter after that change the adapter issue resolved | Closed | kapil solanki | GOEM | Low
16 | 210433857 | 2024-02-23 10:08 |  | GP3.8301.../2320003 | Engine Starting Issue | Closed | Jakson & Company | Power Trading Company - Bhiwadi ( Alwar) | 2 | Starting issue due to control panel relay card negative supply missing and loose after that tighten the same issue resolved | Closed | Gourav sharma | GOEM | Low
1 | 210456085 | 2024-02-27 18:29 | 320 | F6.8802.../2320002 | Amber Lamp Alarm Issue Call By Customer Name :-Irfan ... Mobile No :-7889711040 | Open | Akbar Agro Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar | 702 | SPN/FMI- 4375/11 code showing, and amber lamp on, clear the same issue resolved. | Closed | Ved Gupta | Need to discuss | Low
4 | 210454141 | 2024-02-27 14:20 | 57 | T4.8941.../2420042 | Power supply Issue Call By Customer Name :-Rakesh Kumar Number :-8585945501 | Closed | The Maharaja Aggarsain CGHS. Ltd. | Paluck Technologies Ltd. - Faridabad | 1.8 | customer panel issue load not connected in their panel…same has been informed to customer and DG running OK. | Closed | Kapil Solanki |  | Low
6 | 210453853 | 2024-02-27 13:50 | 200 | 6H.8435.../2320016 | Electric feed pump Email By Service dealer Name:-Sahil Khan | Closed | AVS. Brake Linings Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 43 | SR open for 6R electric feed pump kit. Installed the feed pump kit issue resolved. | Closed | Kapil Solanki |  | Low
8 | 210452045 | 2024-02-27 10:26 | 320 | F6.8802.../2320045 | Starting Issue And Abnormal Sound Issue And Red Lamp Alarm Issue Call By Service Dealer Name :-Vikas Mobile No :-7027820033 | Closed | AVH HEALTHCARE INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Rohtak | 24 | DEF Level sensor stuck at 0%, cleared the same, issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210458452 | 2024-02-28 12:56 | 57 | T4.8941.../2320197 | AMF Panel Issue Call By Customer Name :-Harjeet Singh Number :-9717028542 | Closed | Sikka Group | Vidyut Engineers - New Delhi | 2.42 | GCU Auto starting Setting Changed from Mains sensing to Negative sensing, Issue resolved. | Closed | Kapil Solanki | Compile data of auto panel or sync panel | Low
5 | 210458130 | 2024-02-28 12:13 | 250 | F6.8841.../2420010 | Starting Issue Call By Customer Name :Mohan lal Yadav Mobile No :9717616023 | Closed | The National Media Centre Cooperative House Building Society Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 6.1 | SPN/FMI-3031/14 (Adblue Tank tep High), Just reset the alarm and & done ECM flashing, issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210457935 | 2024-02-28 11:51 | 320 | F6.8802.../2320013 | Genset Reverse Power Alarm Issue Call By Customer Name:Roshanlal Mobile No: - 9672175373 | Task Start | TINA ORGANICS PVT LTD | Power Trading Company - ALWAR | 43 | Reverse Power alarm on GCU as Customer using the Solar Panel also, Just Educated Customer to use one Power source at a single time or Opt of Sync option. | Closed | Gourav Sharma |  | Low
8 | 210457073 | 2024-02-28 10:19 | 57 | T4.8941.../2320063 | Fan Belt Broken Issue Call By Customer Name :-Joganver Singh Mobile No :-9911146716 | Closed | NEW GAGAN GENERATOR | Vidyut Engineers - New Delhi | 24 | Counter purchase 4 V-belt Unit, no Failure. | Closed | Kapil Solanki |  | Low
9 | 210457071 | 2024-02-28 10:19 | 125.4 | 4H.8041.../2320103 | Low Urea Level Alarm Call By Customer Name:-Shubham Goyal Number:-9255555939 | Closed | SHRI BALAJI POLYMERS | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 19.63 | Low DEF level alarm @ 36%, Top up the same also educated to Customer to keep the DEF level maintained b/w 50-100 % for trouble free Operation. | Closed | Kapil Solanki | commisioing | Low
1 | 210467300 | 2024-02-29 17:58 | 30 | 3H.8902.../2320054 | Low Speed Alarm Issue Call By Customer Name :-Annuj Number :-9718741652 | Open | Asha Sharma | Diesel Engineers Sales & Service - Ghaziabad | 16 | Relay in Auto Panel Faulty (Under Voltage), Suggested Customer to take up with Auto Panel team. | Closed | Sudhir Awasthi |  | Low
2 | 210467140 | 2024-02-29 17:43 | 62.5 | T4.8941.../2320034 | V Belt Loose Email By-Service Dealer Name:-Kartikey Rajput | Closed | Yaduvanshi Generators Services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 864 | V-belt loose, tighten the same, Issue resolved. | Closed | Kapil Solanki | Details from sites. Belt change period need to confirm. | Low
4 | 210465313 | 2024-02-29 15:22 | 750 | DV2.8501.C4../2320029 | Genset Lockout issue Message By Customer Name:- Koushal Kishore Yadav Number:- 7033035764 | Task Start | Carlsburg India Pvt ltd | Power Trading Company - ALWAR | 14 | Emergency switch lock out due to Loose connection in Panel, Tighten the same, Issue resolved. | Closed | Gourav Sharma | Need details | Low
5 | 210465169 | 2024-02-29 15:03 | 125.4 | 4H.8041.../2320105 | Error Code Issue Call By Service Dealer Name :Umesh Number :9716440220 | Task Start | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 429 | SPN/FMI: 157/14, PRV open Count '50' in a single crank & Engine failed to start, Replaced Common Rail, Issue resolved. | Closed | Kapil Solanki | One pager. Under observation | Low
6 | 210464991 | 2024-02-29 14:38 | 30 | 3H.8902.../2320082 | Starting Issue Call By Service Dealer Name :-Sohit Number :- 8287515158 | Closed | EDS. Construction Private Limited | OVN Industries Private Limited - New Delhi | 106 | Lacquering/Carbonisation inside the EGR Valve, Cleaned the same, Issue resolved also Educated Customer to operate the DG on min 30% Load. | Closed | Gourav Sharma | Duty cycle for KRM data | High
8 | 210463817 | 2024-02-29 11:46 | 125.4 | 4H.8041.../2320145 | Air Lock Issue Call By: Customer Name :Datta Mishra No :9599637302 | Closed | V. M. Technocoatings | Vidyut Engineers - Noida | 13.2 | Air Lock issue, bleed system Issue resolved. | Closed | Kapil Solanki | Electric feed pump not present. Commisioing date 14/12/2023 | Low
10 | 210463471 | 2024-02-29 11:11 | 250 | F6.8841.../2320019 | Starting issue & Mobil Leakage Issue Call By Customer Name :- Narendra Nagar No :- 9811818373 | Closed | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 44 | GCU 754 Unit malfunction (Bootloading again & again), Replaced the same under Warranty, Issue resolved. | Closed | Kapil Solanki | Replaced and part send for furher investigation. Under observation | Low
11 | 210463176 | 2024-02-29 10:28 | 125.4 | 4H.8041.../2320187 | Automation Issue Call by Customer Name: Dharmendra . Number :7409417094 | Closed | Rush Enterprises | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | Loose Battery Terminal connections, tighten the same, Issue resolved. | Closed | Kapil Solanki | Cooldown time enquiry by customer. Educated and clsoed | Moderate
12 | 210462951 | 2024-02-29 09:55 | 160 | 6H.8475.../2320033 | Urea Issue Call By Customer Name:-Harishchandra Chauhan Number:-9999572417 | Closed | OM SAI RAM PCB SOLUTION LLP | Vidyut Engineers - Noida | 12.4 | SPN/FMI 516166/0, Just reset the DTC, issue resolved. | Closed | Kapil Solanki | KRM data. Urea level low 1761/16 | Low
13 | 210462845 | 2024-02-29 09:37 | 160 | 6H.8475.../2320014 | Diesel Leakage Issue Call By Customer Name : Ram Das Mobile No :9012533754 | Closed | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 15 | Fuel leakage from Return line (connector at tank), Tighten the same, Issue resolved. | Closed | Sudhir Awasthi | Efsr check | Low
1 | 210486241 | 2024-03-03 10:42 | 320 | F6.8802.../2320026 | Urea and GPS Issue Call By Customer Name : Aniket . Mobile No :8009818110 | Open | JAYCEE CASTALLOYS (P) LTD. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 40.1 | Low DEF level alarm @ 43% top up the same also educated to customer to keep the DEF level maintained b/w 50 to 100% for trouble free operation. | Closed | Kapil Solanki |  | Low
3 | 210484918 | 2024-03-02 17:42 | 125 | 4H.8041.../2320056 | Display display Issue Call By: Service Dealer Name :Ramesh No :9911266168 | Closed | Srihans Technologies Exports Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 8.6 | DEF level was not showing in controller check level sensor found ok. after that discussed with RRT HO team and change the controller issue resolved. | Closed | Kapil Solanki | PIR need to raise. Issue creation | Low
4 | 210480938 | 2024-03-02 13:01 | 750 | DV2.8501.C4../2320005 | Control Panel Issue Call By Customer Name :Gupta Mobile No9429459334 | Closed | Bharat Rasayan Limited | M/s OM Diesels Pvt. Ltd. - Rohtak | 101.1 | SPN/FMI:516305/0 code was showing , after that connect the tool and clear the DTC issue resolved also Customer was using the DG in Over ride switch 'off' condition. | Closed | Kapil Solanki | KRM check | Low
5 | 210480935 | 2024-03-02 13:01 | 750 | DV2.8501.C4../2320033 | Control Panel Issue Call By Customer Name :Gupta Mobile No9429459334 | Closed | Bharat Rasayan Limited | M/s OM Diesels Pvt. Ltd. - Rohtak | 24.51 | SPN/FMI:516166/0 code and Ambar lamp on alarm was showing after that connect the tool clear the DTC issue resolved. also Customer was using the DG in Over ride switch 'off' condition. | Closed | Kapil Solanki | 5 min talk of override switch | Low
6 | 210480745 | 2024-03-02 12:23 | 160 | 6H.8475.../2320028 | Abnormal Sound Issue Call By Customer Name :- Rabbani .. Mobile No :- 9015201975 | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 20.35 | Abnormal sound from V belt, check V belt found loose, adjust the belt tension, issue resolved. | Closed | Kapil Solanki | Part number need to confirm from field. And need to check cut off. | Low
8 | 210480197 | 2024-03-02 11:24 | 40 | 3H.8951.../2320049 | voltage issue | Task Start | Ruchika Service Station | Vidyut Engineers - New Delhi | 12 | Customer using DG with Unbalance load, Educated Customer to put the load in balance manner. | Closed | Kapil Solanki | KRM data check Service history | Low
9 | 210480143 | 2024-03-02 11:19 | 25 | GP3.8702.../2320005 | Starting Issue Call By Customer Name :-Rohit Kumar Mobile No :-9540132439 | Closed | Goodluck Buildtech Pvt. Ltd.. | OVN Industries Private Limited - New Delhi | 12.6 | SPN/FMI: 157/14 code was showing and found battery was discharged, after that same corrective action was taken issue resolved. Started the DG on load and found DG shut down after 15 minutes Then check all connections found XBDK2 connector wire loose tighten the same issue resolved. | Closed | Kapil Solanki |  | Moderate
11 | 210479551 | 2024-03-02 10:22 | 125 | 4H.8041.../2320092 | Phase issue Call by Customer Name :- Laxman Number :- 9050839880 | Closed | Prabha Eye Hospital | Paluck Technologies Ltd. - Faridabad | 39 | SPN/FMI: 3031/14 code was showing , flashing with 4K.125_V1 cal. ECU issue resolved. | Closed | Kapil Solanki |  | High
13 | 210475190 | 2024-03-01 17:35 | 160 | 6H.8475.../2320002 | Starting Issue Call By Customer Name :Om Bir Singh Mobile No :9717279844 | Closed | HNA. Contracting & Trading LLP. | Vidyut Engineers - Noida | 3 | SPN/FMI: 97/5 (water in fuel) check the sensor found ok and physically no water present in fuel, clear the DTC issue resolved. | Closed | Kapil Solanki | Need data for other variednt. KRM data | Low
14 | 210470751 | 2024-03-01 14:38 | 750 | DV2.8501.C4../2320006 | Hunting issue Call By Customer Name :- Shambhu Kumar Sharma No :- 7982794922 | Closed | PREM INDUSTRIES | Vidyut Engineers - Noida | 252 | DG over-heating issue due to V-belt slip as all Belt in loose condition, SD technician visited & Tighten all Belts, Issue resolved. | Closed | Kapil Solanki |  | Low
16 | 210470037 | 2024-03-01 12:49 | 320 | F6.8802.../2320057 | Display Issue Call By Customer Name :-Jogindar Mobile No :-9873867764 | Closed | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 10 | Incorrect Date & Time in Deepsea 745 unit, Just updated correct Date & time, Issue resolved. | Closed | Kapil Solanki | GOEM check. And need to check at commisioning | Low
17 | 210469408 | 2024-03-01 11:09 | 250 | F6.8841.../2320050 | Oil Leakage Issue Call By Customer Name :- Pradeep Yadav Number :-8368321282 | Closed | H. P. Power Solution | Diesel Engineers Sales & Service - Ghaziabad | 8 | Engine Oil leakage from Allen key Screw (Oil Cooler Header assy), Tighten the same, Issue resolved. | Closed | Kapil Solanki | Reworked at GOEM for pressure adjustment | Moderate
18 | 210469329 | 2024-03-01 10:57 | 160 | 6H.8475.../2320014 | High consumption issue And Ambar lamp alarm issue Call By Customer Name :-Ram Das Number :-9012533754 | Closed | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 18 | Low DEF level alarm @ 47% top up the same also educated to customer to keep the DEF level maintained b/w 50 to 100% for trouble free operation. | Closed | Sudhir Awasthi |  | Low
19 | 210469322 | 2024-03-01 10:57 | 625 | DV0.8501.C4../2320027 | KRM App Issue Call By Customer Name: Subhash Mukharjee Number:8607866300 | Closed | FORECH INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 9.34 | KRM was not activated, issue resolved with the help KRM HO team. | Closed | Kapil Solanki | KRM activation process. No number pupdated in pulse. | Low
20 | 210468940 | 2024-03-01 09:56 | 125 | 4H.8041.../2320108 | Starting Issue Email By Service Dealer Name:-Madhu Sudan Sharma | Closed | SSSP. Speciality Packagings Pvt. Ltd. | Power Trading Company - ALWAR | 28 | Starting issue due to air lock in fuel line , install the electric feed pump kit issue resolved. | Closed | Gourav Sharma |  | Low
1 | 210491783 | 2024-03-04 17:33 | 160 | 6H.8475.../2320024 | Red Light Lamp Alarm Issue And Abnormal Sound Issue Call By Customer Name : Sunder Singh No : 9672973802 | Task Start | CHRYSO INDIA PRIVATE LIMITED | Power Trading Company - ALWAR | 28 | SPN/FMI: 105/4 (Boost pressure sensor) , 516160/0 &97/5 code was showing ,clear the DTC issue resolved. | Closed | Gourav Sharma |  | High
2 | 210491561 | 2024-03-04 17:03 | 200 | 6H.8435.../2420001 | Battery issue Call By: Customer Name :Pradeep Kumar No :9350849220 | Task Start | Avibha Industries Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 3.57 | main current fuse burnt in X1 connector (AC supply) due to the main wire short. Tighten the main wire and issue resolved | Closed | Kapil Solanki |  | Low
5 | 210491078 | 2024-03-04 16:05 | 250 | F6.8841.../2320005 | Starting Issue Call By: Customer Name :Vinod Kumar No :9728005448 | Closed | ALFA FLEXITUBES ( P ) LTD | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 39.3 | Low DEF level @ 32%, Just topup the DEF & educated Customer, issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210490765 | 2024-03-04 15:54 | 500 | DV8.8501.C4../2320029 | Coolant Leakage Issue Call By Customer Name :- Jahangir Ahmed Mobile No :- 9797750480 | Task Start | Sheen Agri Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar | 52.27 | Coolant leakage From loose radiator hose clip , tighten the hose clip issue resolved. | Closed | Ved Gupta | Consolidated data. | Moderate
7 | 210490562 | 2024-03-04 15:28 | 125.4 | 4H.8041.../2420005 | Starting issue Call By: Service Dealer Name :Ritik No :7027820034 | Closed | Strategic Alliance Management Service Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Rohtak | 10 | Overload upto 108 kw & observed jerk load on DG, educated the customer to use DG @ 80% load. | Closed | Kapil Solanki |  | Low
8 | 210489670 | 2024-03-04 13:32 | 160 | 6H.8475.../2420003 | Synchronisation Issue Call By Customer Name : Subhash Mukharjee Number :8607866300 | Closed | FORECH INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 2.4 | SR open for synchronization with 625 and 500 kva DG | Closed | Kapil Solanki |  | Low
9 | 210489131 | 2024-03-04 12:08 | 125.4 | 4H.8041.../2320186 | ENGINE FUEL LEAKAGE ISSUE DUE Email By - Service Dealer Name -SUNITA | Closed | Goldripe International Pvt. Ltd. | R K Engineers - Meerut | 55 | fuel was leaking due to over fill tank. | Closed | Sudhir Awasthi | Details required | Low
10 | 210488906 | 2024-03-04 11:37 | 250 | F6.8841.../2320019 | Starting Issue & Canopy Emg Stop Issue Call By Customer Name :-Narendra Nagar Number :-9811818373 | Closed | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 49 | Emergency switch ON, just corrected the same, Issue resolved. Also Rain water accumulated in Canopy. | Closed | Kapil Solanki | Rain guard check | Low
11 | 210488780 | 2024-03-04 11:07 | 125.4 | 4H.8041.../2420041 | Starting issue Call by Customer Name : Prashant . Number : 9911093925 | Closed | Godrej Projects Development Limited | Paluck Technologies Ltd. - Gurgaon | 58 | Low Def level @38% just top up the DEF & educated customer issue resolved. | Closed | Kapil Solanki |  | Low
12 | 210488551 | 2024-03-04 10:30 | 57 | T4.8941.../2320124 | Starting Issue Email By Service Dealer Name:-Power Trading Company, BM | Closed | Yash Abrasive | Power Trading Company - Bhiwadi ( Alwar) | 14.42 | There was R phase wire burned , after that, replace the new wire issue resolved. | Closed | Gourav Sharma |  | Low
13 | 210488495 | 2024-03-04 10:18 | 125.4 | 4H.8041.../2320191 | FUEL LEAKAGE Email By - Service Dealer Name -VINIT KUMAR JAIN | Closed | Neer Industries | Power Trading Company - Bhiwadi ( Alwar) | 12 | Fuel leakage from leak off pipe, tighten the same issue resolved and also add the washer. | Closed | Gourav Sharma |  | Low
14 | 210488434 | 2024-03-04 10:10 | 57 | T4.8941.../2320051 | Load issue Call by customer Name: Ramesh Number:9999538698 | Closed | Falcon Vacuum Pumps & Systems | Paluck Technologies Ltd. - Faridabad | 19.29 | Running Load 12-15 KW additional Jerk load on DG (14-15 KW) , suggested to the customer for step loading. | Closed | Kapil Solanki |  | Low
1 | 210515777 | 2024-03-10 16:58 | 82.5 | 5H.8901.../2320102 | Phase issue Call by customer Name: Kishan . Number: 7409096174 | Open | Vuenow Marketing Services Pvt. Ltd. | Diesel Engineers Sales & Service - Ghaziabad |  | Customer requirement to reduce the cooling time 300 sec to 0 sec … guided the customer it is not possible as it is a Product requirement. SR to be cancelled. | Closed | Kapil Solanki |  | Low
2 | 210515776 | 2024-03-10 16:55 | 82.5 | 5H.8901.../2320103 | Control panel issue Call by customer Name: Kishan . Number: 7409096174 | Open | Vuenow Marketing Services Pvt. Ltd. | Diesel Engineers Sales & Service - Ghaziabad |  | Customer requirement to reduce the cooling time 300 sec to 0 sec … guided the customer it is not possible as it is a Product requirement. SR to be cancelled. | Closed | Kapil Solanki |  | Low
4 | 210515690 | 2024-03-10 15:15 | 400 | DV8.8542.C4../2320006 | Coolant leakage Issue Call By Customer Name : Iqbal . Number : 9034549209 | Open | PUSH UP TOOLS UDYOG (P) LIMITED | M/s OM Diesels Pvt. Ltd. - Rohtak | 48.22 | Customer complained for abnormal sound but after checking the DG there was no abnormal sound. | Closed | Kapil Solanki |  | Low
5 | 210515647 | 2024-03-10 12:45 | 57 | T4.8941.../2320238 | Canopy paint issue & return pipe issue Email By KGD Name:-Pooja Sharma | Open | Golden Sparrow Industries | Power Trading Company - Bhiwadi ( Alwar) | 2.55 | Fuel leakage due to injector return pipe lock was missing, fited the same issue resolved. | Closed | Gourav Sharma |  | High
6 | 210515252 | 2024-03-09 19:15 | 125.4 | 4H.8041.../2320128 | Starting Issue Call By: Customer Name :Yogesh No :8200900653 | Closed | KALYAN JEWELLERS INDIA LTD. | OVN Industries Private Limited - New Delhi | 17 | Battery charger connection was loose in auto panel.( non KOEL auto panel ) | Closed | Kapil Solanki |  | Moderate
7 | 210513708 | 2024-03-09 16:09 | 40 | 3H.8951.../2320004 | Starting Issue Call By Customer Name :- Arvind . Mobile No :- 9871903398 | Closed | Waves Enterprises. | Vidyut Engineers - Noida | 2.8 | Starting issue due to air lock in fuel line after that cleared the fuel line by hand priming issue resolved. | Closed | Kapil Solanki |  | Low
8 | 210513399 | 2024-03-09 15:49 | 320 | F6.8802.../2420005 | Trip_Genset_Low_Voltage | Task Start | Alko Plus Technosafe Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 21 | Customer put overload on DG suggested to the customer to maintain balanced load. | Closed | Kapil Solanki |  | Low
9 | 210512830 | 2024-03-09 14:36 | 62.5 | T4.8941.../2320173 | Starting Issue Call By Customer Name :-Abhishek Garg Mobile No :-7015280772 | Task Start | Shri Shyam Sweets | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 27 | Programming mode On also SPN/FMI: 97/5 ( DM 2) water in fuel alarm shown, check the sensor found ok, just clear the DTC issue resolved. | Closed | Kapil Solanki |  | Low
10 | 210512608 | 2024-03-09 14:01 | 30 | 3H.8902.../2320175 | Acidic & Toxic Fumes And Earthing Issue Call By Customer Name :Nilaksh Sharma Mobile No :9310408163 | Task Start | Rajender Nagar Nursing Home | Diesel Engineers Sales & Service - Ghaziabad | 3 | Customer has issue with KGD for wrong place installation of DG Communicating the same to GOEM and ask customer to contact GOEM. | Closed | Kapil Solanki |  | Low
11 | 210511018 | 2024-03-09 10:45 | 62.5 | T4.8941.../2320144 | Starting Issue Email By - Service Dealer Name -Devender Yadav | Closed | Dr. Kaushal Surgical Hospital & Maternity Home | Power Trading Company - Rewari | 31 | Starting issue due to loose CAN H wire in controller, tighten the same issue resolved. | Closed | Gourav Sharma |  | Low
13 | 210510356 | 2024-03-09 09:14 | 250 | F6.8841.../2420010 | Starting Issue Call By Customer Name :Mohan lal Yadav Mobile No :9717616023 | Closed | The National Media Centre Cooperative House Building Society Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 8 | Oil Prssure changing erratically, SPN /FMI 100/3 Oil Pressure sensor fault further check the connection and supply found ok clear the alarm, Kept under observation. | Closed | Kapil Solanki |  | Low
14 | 210508729 | 2024-03-08 15:50 | 125.4 | 4H.8041.../2320035 | V Belt Issue Call By Customer Name:Surendar Singh Number :7838955363 | Closed | VINKAY TEXTILES [P] LTD | Paluck Technologies Ltd. - Faridabad | 92 | Abnormal sound due to damaged V belt, replace the same and also SPN/FMI : 5461/0 code was shown clear the DTC issue resolved. | Closed | Kapil Solanki |  | Low
15 | 210508067 | 2024-03-08 14:03 | 400 | DV8.8542.C4../2320007 | coolant leakage | Closed | BPCL Jaipur | A.S.Motors - Kota | 6.48 | Coolant leakage from dosing module coolant circuit (oil coolant header assy ) due to cu washer missing at B bank. fited the cu washer issue resolved. | Closed | Gourav Sharma |  | Low
16 | 210506962 | 2024-03-08 10:57 | 125.4 | 4H.8041.../2320041 | Low uria Alarm issue And Starting issue Call By Customer Name : Giby Jackob Mobile No : 9891123347 | Closed | Bala Ji. Exports | Paluck Technologies Ltd. - Faridabad | 20.44 | Fuel leakage at benzo bolt in fuel line due to damaged cu washer change the cu washer issue resolved. | Closed | Kapil Solanki |  | Low
17 | 210506513 | 2024-03-08 09:41 | 320 | F6.8802.../2420001 | RR Assembly Defective | Closed | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 4.6 | Under voltage alarm shown,because of RRA burnt due to reverse mains power (1143 Amp also Engine Run @ 1000 RPM) on DG, due to absence of changeover at customer end after that replace the RRA on Paid bases , and suggested to the customer for installation of changeover. | Closed | Kapil Solanki |  | Low
1 | 210523044 | 2024-03-12 15:07 | 750 | DV2.8501.C4../2320033 | Fuel Leakage issue ' Call By Customer Name :-Ram Mohan Mobile No :-9050555117 | Closed | Bharat Rasayan Limited | M/s OM Diesels Pvt. Ltd. - Rohtak | 34.49 | Fuel tank leakage, KGD had agreed to give a new tank with site installation but Customer not given Down time to replace New tank so they installed New External tank. | Closed | Kapil Solanki |  | Moderate
4 | 210522215 | 2024-03-12 11:55 | 750 | DV2.8501.C4../2320005 | Trip_Genset_Low_Voltage | Task Start | Bharat Rasayan Limited | M/s OM Diesels Pvt. Ltd. - Rohtak | 111.52 | There was a jerk load at the site due to which the over current alarm & under voltage alarm was coming and due to which the genset was tripping also updated (Cooling & idle cooling time) | Closed | Kapil Solanki |  | Low
5 | 210521991 | 2024-03-12 11:11 | 125.4 | 4H.8041.../2320202 | Tripping Issue Call By Customer Name :- Vinit Singal No :- 6284737475 | Task Start | Eden Garden | M/s OM Diesels Pvt. Ltd. - Rohtak | 45 | Multiple error codes shown in controller related to Ad blue level , check physically tank found 0% ad blue in DEF tank , just top the DEF and educate the customer pls maintain DEF Between 50 % to 90 % for trouble free operation. | Closed | Kapil Solanki |  | Low
6 | 210521732 | 2024-03-12 10:06 | 125.4 | 4H.8041.../2420059 | Starting Issue Call By Customer Name :- Rajnesh Kumar Mobile No :- 9649880643 | Closed | Sath Guru Engineering | Power Trading Company - ALWAR | 2.3 | starting issue due to under speed alarm, open the electrical feed pump kit and refitted it properly and also update the programming file, issue resolved. | Closed | Gourav Sharma |  | Low
2 | 210525869 | 2024-03-13 11:22 | 40 | 3H.8951.../2320033 | Automation Issue Call By Customer Name :- Bajrang Singh Mobile No :- 9868356329 | Closed | Bajrang Singh | Vidyut Engineers - Noida | 60.48 | Starting issue due to loose wiring at ignition relay (3C wire loose) tighten the same issue resolved. | Closed | Kapil Solanki |  | Low
1 | 210530447 | 2024-03-14 15:15 | 500 | DV8.8501.C4../2320069 | Door Lock issue Call By: Service Dealer Name :Sachin No :7428791137 | Closed | QH. Talbros Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 7 | Canopy door lock alignment issue, same corrective action was taken issue resolved. | Closed | Kapil Solanki |  | Low
3 | 210530174 | 2024-03-14 14:18 | 500 | DV8.8501.C4../2320061 | Amber Lamp Alarm Issue Call By Customer Name :- Vinay ... Mobile No :- 9958706403 | Task Start | PG. Electroplast Ltd. | Vidyut Engineers - Noida | 14.45 | SPN/FMI :3465/1 'B Bank' Throttle valve open circuit DTC, Remove ITV male connector protection cap & refix the same, Issue resolved. | Closed | Kapil Solanki |  | Moderate
5 | 210529677 | 2024-03-14 12:12 | 40 | 3H.8951.../2320006 | Terrping Issue Call By Customer Name :- Ajay Batra No :- 9837410538 | Closed | Krosfit Sports | R K Engineers - Meerut | 51.5 | Discharged Battery cause Engine starting issue as 2B3 Connection damaged, corrected the same, Issue resolved. | Closed | Sudhir Awasthi |  | Moderate
7 | 210529394 | 2024-03-14 11:25 | 57 | T4.8941.../2320126 | Starting Issue Call By Customer Name :- Usman . Mobile No :- 6399391461 | Closed | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 386.38 | Starting issue as loose Main fuel filter, retighten the same issue resolved. | Closed | Kapil Solanki | Vibration check. | Low
2 | 210543721 | 2024-03-17 13:38 | 57 | T4.8941.../2320152 | Canopy Door Lock issue Call By: Customer Name :Ashu No :9718850143 | Open | PSG ELECTRICALS | Vidyut Engineers - Noida | 188 | Rear left Canopy Door Locking problem found Canopy beeding space in bend condition, Corrected the same, Issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210539505 | 2024-03-16 12:10 | 82.5 | 5H.8901.../2320076 | Starting Issue. Call By Customer Name:- Chandu ... No:-8930449119 | Closed | Sandhu Construction | Vishal Power Systems - Karnal | 419 | DG was not taking load due to choked fuel filters , Replace the same issue resolved. | Closed | Kapil Solanki | SR history check. Filter photo | Low
6 | 210538041 | 2024-03-16 07:53 | 30 | 3H.8902.../2320082 | Engine Stop Alarm Issue And Starting Issue Call By Customer Name :-Surakan . Mobile No :-9899576164 | Closed | EDS. Construction Private Limited | OVN Industries Private Limited - New Delhi | 258.26 | Starting issue due to canopy emergency switch pressed,and also air lock issue due to loose fuel filter,clear the same issue resolved. | Closed | Kapil Solanki | Details required | Low
7 | 210535009 | 2024-03-15 13:40 | 62.5 | T4.8941.../2320056 | Starting Issue Call By: Customer Name :Joganver Singh No :9911146716 | Closed | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 339 | SPN/FMI: 633/3 code and emergency stop alarm shown,clear the DTC issue resolved. | Closed | Kapil Solanki | KRM dat check | Low
9 | 210534763 | 2024-03-15 13:04 | 250 | F6.8841.../2320019 | Oil leakage problem Email By - OEM Name -JYOTI BHADURIA | Closed | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 60 | Lube oil leakage from oil filter, replace the same issue resolved. | Closed | Kapil Solanki | CSP check | Low
10 | 210534109 | 2024-03-15 11:15 | 125.4 | 4H.8041.../2320041 | Loading issue Call By Customer Name : Giby Jackob Mobile No : 9891123347 | Closed | Drivewell Auto Industries. | Paluck Technologies Ltd. - Faridabad | 27 | External fuse box is installed by customer for load shifting of mains and DG but fuse specifications are not matched with load capacity, install the fuse according to the same issue resolved. | Closed | Kapil Solanki | Details required | Low
11 | 210534107 | 2024-03-15 11:15 | 62.5 | T4.8941.../2320034 | Fan Belt Broken Issue Call By Customer Name : Subhash Yadav Number : 9891282853 | Closed | Yaduvanshi Generators Services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1026 | Fan belt broken and Water in fuel alarm shown in controller, replace the same and reset the alarm issue resolved. | Closed | Kapil Solanki | Belt part number photo | Low
12 | 210533901 | 2024-03-15 10:32 | 160 | 6H.8475.../2320004 | Oil Leakage Issue Email By Service Dealer Name:-Priya Dogra | Task Start | JK. Constructions | Suraj Motor Store - kathua | 96 | Inlet and outlet pipe DEF tank to SM is interchanged and also Ad blue leakage from loose outlet pipe , tighten with teflon tap issue resolved . | Closed | Ved Gupta | Need to discuss with Suraj | Low
1 | 210545043 | 2024-03-18 09:03 | 320 | F6.8802.../2320054 | PUC alarm issue and oil leakage issue Call By: Customer Name :-Krishna Gopal No :7388874982 | Closed | Newtech Vinyl | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 51 | SPN/FMI : 6595/0 code (Aftertreatment 1 Diesel Exhaust Fluid Actual Dosing Quantity (High Range), after that cleaned the Ad blue filters and checked any blockage in the def line found ok. refited the same issue resolved. | Closed | Kapil Solanki | More details required from field and monitoring | Low
2 | 210545205 | 2024-03-18 09:44 | 20 | GP3.8601.../2320002 | Starting Issue Call By Customer Name :-Ajay Bhagat Mobile No :-9312746111 | Closed | PHOTON COMPUTERS INDIA PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 31 | Electric feed pump kit wire loose , just retighten the same issue resolved. | Closed | Kapil Solanki | Past history to be checked | Low
3 | 210545241 | 2024-03-18 09:48 | 500 | DV8.8501.C4../2320017 | starting Issue call by Customer Name ; Sanjiv Kumar Number ; 8814828270 | Closed | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat | 82.2 | Starting issue due to interface card fuse (30A ) burnt to replace the same issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210545434 | 2024-03-18 10:28 | 125.4 | 4H.8041.../2320088 | Starting Issue Call By Customer Name :- Bhopal Kishan Mobile No :- 9650991118 | Closed | Shramdeep Appartments | Vidyut Engineers - Noida | 51.56 | Starting issue due to Emergency switch in depressed condition, Correct the same, issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210546163 | 2024-03-18 12:13 | 160 | 6H.8475.../2320036 | Starting Issue Call By Customer Name :- Nikhil Gupta No :- 9871151722 | Closed | Subhash Light House | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 4.5 | GCU not Starting as 2D fuse blown out replaced the same issue resolved. | Closed | Kapil Solanki |  | Low
7 | 210546559 | 2024-03-18 13:16 | 250 | F6.8841.../2320026 | Load Issue Call By Customer Name:Pravez Singh No:9312907425 | Closed | Ajanta Cold Storage and General Mills | Diesel Engineers Sales & Service - Ghaziabad | 264100322 | Earthing was connected on CT by customer due to which DG reverse phase alarm was generated after that earthing wire connected to panel issue resolved. | Closed | Kapil Solanki | More details required from field and monitoring | Low
9 | 210546862 | 2024-03-18 14:30 | 750 | DV2.8501.C4../2320035 | ECU lock Email By - Service Dealer Name -VINIT KUMAR JAIN | Task Start | Shree Cement Ltd. | Power Trading Company - Bhiwadi ( Alwar) | 14.14 | ECU & DCU Communication error (Multiple DTC), Updated ECU and DCU Callibration issue resolved. | Closed | Gourav Sharma | More details required from field and monitoring | High
10 | 210547134 | 2024-03-18 15:23 | 62.5 | T4.8941.../2320246 | Starting Issue Email By Service Dealer Name:- Devender Yadav | Closed | Arora Nursing Home | Power Trading Company - Rewari | 36 | Starting issue due to GCU digital output connector loose, refited the same issue resolved. | Closed | Gourav Sharma |  | Low
1 | 210553831 | 2024-03-20 09:49 | 30 | 3H.8902.../2320126 | Voltage Fluctuation Issue Call By Customer Name :-Sazid Ali Mobile No :-9953056786 | Open | Sazid Spare Parts | Vidyut Engineers - New Delhi | 20 | Customer complained for voltage fluctuation.. Engineer visited the site and checked DG manually and also checked on load.. But no issue was found and informed to the customer. same. | Closed | Kapil Solanki |  | Low
4 | 210552420 | 2024-03-19 17:22 | 57 | T4.8941.../2320183 | Trip_Genset_Low_Voltage | Task Start | Technocrat Moudlings Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 28 | Main Alternator Red Wire (connected to AVR) in burnt condition, Repair the same, Issue resolved. | Closed | Kapil Solanki |  | High
5 | 210551587 | 2024-03-19 15:33 | 750 | DV2.8501.C4../2320028 | faced issues in HMI Email By - Customer Name - Deepak Singh | Open | Merino Industries Ltd. | Diesel Engineers Sales & Service - Ghaziabad |  | Customer requirement to remove deep sleep mode from controller,and requirement for displaying of fuel in percentage reprogram the same.issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210551548 | 2024-03-19 15:28 | 250 | F6.8841.../2320015 | Tripping Â Issue Call By Customer Name :- Abhishek Kumar Mobile No :- 7903795913 | Task Close | HIND TERMINALS [P] LTD | Paluck Technologies Ltd. - Faridabad | 150 | Emergency stop activate itself witout depressing while DG running, Emergency switch malfunction. replace the same issue resolved also updated deepsea Parameters input G from never to always & in LCD display 'Canopy Emergency Stop) | Closed | Kapil Solanki |  | Low
9 | 210550574 | 2024-03-19 12:19 | 250 | F6.8841.../2320049 | Engine GCU Amber Alarm Issue Due Email By Service Dealer Name:- Sunita | Closed | VSV. Polymers | R K Engineers - Meerut | 6.58 | Customer doing Hot shutdown, SPN/FMI : 516166/0 Code was shown, clear the DTC issue resolved. | Closed | Sudhir Awasthi |  | Low
1 | 210556914 | 2024-03-20 17:58 |  | F6.8841.../2320034 | oil pressure problem | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 1.1 | High oil pressure issue ( 10 bar) adjust Pressure Relief valve, Issue resolved. | Closed | Sudhir Awasthi |  | Moderate
2 | 210556906 | 2024-03-20 17:55 |  | F6.8841.../2320036 | oil pressure problem | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 2 | High oil pressure issue ( 10 bar) adjust Pressure Relief valve, Issue resolved. | Closed | Sudhir Awasthi |  | Moderate
4 | 210554515 | 2024-03-20 11:39 | 125.4 | 4H.8041.../2320104 | Red lamp alarm issue Call By Customer Name :Rakesh Yadav Mobile No :8744041285 | Closed | Unicel Autotech India Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 42 | SPN/FMI: 1761/16 ( Low DEF level @ 47% ) clear the DTC and also suggested to the customer purchase the DEF and top up for trouble free operation. | Closed | Kapil Solanki |  | Low
5 | 210554359 | 2024-03-20 11:11 | 40 | 3H.8951.../2320078 | Starting Issue Email By Service Dealer Name:- Shiv | Closed | PSG ELECTRICALS | Vidyut Engineers - Noida | 57 | SR open due to Claim purpose of relay board 12RB1, earlier SR cancelled due to dealer account merger. | Closed | Kapil Solanki |  | Low
7 | 210553831 | 2024-03-20 09:49 | 30 | 3H.8902.../2320126 | Voltage Fluctuation Issue Call By Customer Name :-Sazid Ali Mobile No :-9953056786 | Closed | Sazid Spare Parts | Vidyut Engineers - New Delhi | 20 | Customer complained for voltage fluctuation.. Engineer visited the site and checked DG manually and also checked on load.. But no issue was found and informed to the customer same. | Closed | Kapil Solanki |  | Low
2 | 210559366 | 2024-03-21 14:53 | 30 | 3H.8902.../2320190 | Automation issue call by customer name;Manhohar no;9871891191 | Task Start | ONEWORLD SECURITIES | OVN Industries Private Limited - New Delhi | 5.4 | Customer complained for automation & error code issue , Engineer visited the site and checked DG manually and also checked on load.. But no issue was found and informed to the customer about the same. | Closed | Kapil Solanki |  | Low
4 | 210558584 | 2024-03-21 12:08 | 62.5 | T4.8941.../2320015 | Starting Issue Email By - Service Dealer Name -VINIT KUMAR JAIN | Closed | OM MULTISPECIALITY HOSPITAL | Power Trading Company - Bhiwadi ( Alwar) | 16.33 | SPN/FMI :157/14 ( Exceeding of the maximum rail pressure sensor ) checked and found that some time ECU did not get 12 V supply properly then checked relay 12RB1 ( RL2 ) and found Voltage drop at RL2 relay. change relay (RL2) issue resolved. | Closed | Gourav Sharma |  | High
6 | 210557644 | 2024-03-21 09:40 | 125.4 | 4H.8041.../2320037 | Starting Issue Email By Service Dealer Name-Shiv | Closed | MAHNA LEATHERS PVT. LTD. | Vidyut Engineers - Noida | 17.13 | SPN/FMI : 1761/14 ( Low ad blue level @ 1% ) top up the ad blue,clear the DTC and educate the customer about the same and also ( 3031/14) code was shown, updated dummy cal issue resolved. | Closed | Kapil Solanki |  | Low
7 | 210557551 | 2024-03-21 08:46 | 125.4 | 4H.8041.../2320170 | Control issue Call By: Customer Name :Anirudh Singh No : 8534803481 | Closed | Gharonda Sahakari Awas Samiti Limited | Vidyut Engineers - Noida | 4.11 | SPN/FMI: 2802/4 ( battery low voltage ) check battery terminal connections found ok . Clear the DTC issue resolved. | Closed | Kapil Solanki |  | Moderate
9 | 210387244 | 2024-02-09 14:01 | 250 | F6.8841.../2320030 | AMF Panel Issue Call By Customer Name : Prashant Number :9899113161 | Task Start | Asian Engineering Co. | Vidyut Engineers - New Delhi |  | AMF panel issue, SR cancelled |  | Kapil Solanki | Need updates | Low
10 | 210387424 | 2024-02-09 14:44 | 57 | T4.8941.../2320091 | Automation Issue Call By Customer Name : Sachin Solanki Number : 9999677898 | Task Start | Mohit | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2 | Problem in auto panel. | Open | Kapil Solanki |  | Low
12 | 210387720 | 2024-02-09 15:18 | 82.5 | 5H.8901.../2320100 | Amber Lamp Alarm Issue Call By Customer Name : Dinesh . Number :9997189180 | Open | Brocin Textile Ltd. | Espiem Engines & Machines (P) Limited - Aligarh |  | Update yet to receive. | Open | Sudhir Awasthi |  | Low
13 | 210388716 | 2024-02-09 17:23 | 320 | F6.9051.../2300002 | Starting Issue Email By Service Dealer Name:- Madan Chhimpa | Task Start | PERENNIAL TECHNOLOGY PVT LTD | Paluck Technologies Ltd. - Gurgaon | 573 | SPN no-5461,FMI-0 Already data provided to RRT HO. Team will revisit the site to collect Data log in order to monitor the Inlect & Outlet Nox value | Open | Kapil Solanki |  | Low
14 | 210389634 | 2024-02-10 09:37 | 57 | T4.8941.../2320258 | Starting Issue Call By Customer Name:Sushint Kumar Number:9717720025 | Task Start | Swastik Components Private Limited | Paluck Technologies Ltd. - Faridabad | 5 | High Oil Pressure Alarm (SPN/FMI: 100/3) also Service tool connector 'D' Pin Push Back, Correcth the same but Oil Pressure issue still pending. | Open | Kapil Solanki |  | Low
1 | 210398048 | 2024-02-12 18:17 | 125.4 | 4H.8041.../2320098 | Starting issue Call by Customer Name:Soom Deep No:9992100991 | Open | Rathi Pumps Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 10 | Electric feed pump kit requirement at site as not installed from GEOM end. | Open | kapil solanki |  | Low
6 | 210396130 | 2024-02-12 12:00 | 125.4 | 4H.8041.../2320104 | Starting problem .Email By - Service Dealer Name -Madan Chhimpa | Task Start | Unicel Autotech India Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 39 | Electric feed pump kit requirement at site as not installed from GEOM end. | Open | kapil solanki |  | Low
7 | 210395624 | 2024-02-12 10:17 | 320 | F6.8802.../2320061 | Starting Issue Call By Customer Name :-Sushil .. Number :-8860089233 | Task Start | Rai Indutrial Power Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 6 | 320 kva (1)abnormal sound from alternator, (2) leakage from DG HP Pump (3)water leakage & crack in exhaust, Planned JV with all Vendors. | Open | kapil solanki |  | High
8 | 210395551 | 2024-02-12 10:01 | 125.4 | 4H.8041.../2320026 | Starting Issue Call By Customer Name :-Yash Pal Number :-9599117169 | Task Start | SAMPARK Global Logistics Private Limited | Paluck Technologies Ltd. - Faridabad | 29 | Ad blue temp high alarm(3031/14), clean header of the urea tank and refitted the connection. | Open | kapil solanki |  | Low
1 | 210400998 | 2024-02-13 17:23 | 625 | DV0.8501.C4../2320027 | Voltage issue Call By Customer Name :- Subhash Mukharjee Number :-8607866300 | Open | FORECH INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat |  | Customer purchased new DG & Registered SR for synchronization of 2 DGs | Open | Kapil Solanki |  | Low
6 | 210400540 | 2024-02-13 16:07 | 400 | DV8.8542.C4../2320006 | Coolant leakage Issue Email By Customer Name:-Nitin Jain | Open | PUSH UP TOOLS UDYOG (P) LIMITED | M/s OM Diesels Pvt. Ltd. - Rohtak | 31.39 | Coolant leakage from radiator bottom. Today our ASE will visit the site | Open | Kapil Solanki |  | Moderate
10 | 210399231 | 2024-02-13 12:29 | 320 | F6.8802.../2320044 | ENGINE WIRING AND STARTING ISSUE Email By Service dealer Name:-Kaushik | Open | K. K. Fabs | R K Engineers - Meerut | 2.4 | Battery disconnted also KRM not active, intiated KRM activation process. |  | Sudhir Awasthi |  | Moderate
16 | 210398827 | 2024-02-13 10:58 | 160 | 6H.8475.../2320002 | Starting Issue Call By Customer Name :Om Bir Singh Mobile No :9717279844 | Open | HNA. Contracting & Trading LLP. | Vidyut Engineers - Noida | 1.47 |  | Open
5 | 210403057 | 2024-02-14 12:15 | 125.4 | 4H.8041.../2320121 | Automation Issue Call By Service Dealer Name : Sohit Number : 8287515158 | Task Start | XPERT POWERGEN PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | 733 |  | Open | Kapil Solanki
6 | 210402805 | 2024-02-14 11:36 | 82.5 | 5H.8901.../2320086 | Audio Relay | Task Start | PSG. International | Paluck Technologies Ltd. - Faridabad |  | visit will be planned for tomorrow. | Closed | Kapil Solanki |  | Low
7 | 210402800 | 2024-02-14 11:32 | 125.4 | 4H.8041.../2420034 | Electrical Problem | Task Start | S. G. Wires | Paluck Technologies Ltd. - Faridabad | 3 | ECU malfunctioning alarm shown in controller, after flashing ECU issue resolved. | Open | Kapil Solanki |  | High
9 | 210402495 | 2024-02-14 10:35 | 320 | F6.8802.../2320025 | Load Issue Call By Customer Name :-Raju Sharma Number :-9050303897 | Open | MANGLA APPARELS INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 33.1 | coolant leakage from hose after tightening the clamp issue resolved and also under voltage and under frequency alarm showing in controller. Our ASE will be visiting the site tomorrow. | Open | Kapil Solanki |  | Low
5 | 210410124 | 2024-02-16 10:19 | 320 | F6.8802.../2320025 | Load Issue Call By Service Dealer Name :Mohit Mobile No :7027820044 | Task Start | MANGLA APPARELS INDIA PVT. LTD. | M/s OM Diesels Pvt. Ltd. - Sonipat | 34.1 | Sometimes DG tripping with 'Low Voltage alarm' suspected Overload sometimes, Discussed with HO team & got instructions to perform Load analyses. | Open | Kapil Solanki | Load data and KRM data | Low
12 | 210406518 | 2024-02-15 09:58 | 500 | DV8.8501.C4../2320004 | Coolant temp light issue Call By Customer Name :- Virendra Kumar Number :-7633873576 | Cancelled | Indian Potash Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | SR pertains to Bihar state, Transferred to concern SD. | Open | Kapil Solanki |  | Low
1 | 210416927 | 2024-02-18 11:52 | 125.4 | 4H.8041.../2320108 | starting also and high engine noise at the load Email By - KGD Name - Shamim Ahmed | Open | SSSP. Speciality Packagings Pvt. Ltd. | Power Trading Company - ALWAR | 18.28 | Engine starting issue due to Air Lock, Electric feed pump kit required. | Open | Gourav Sharma | To be check | Low
2 | 210416724 | 2024-02-17 21:34 | 125.4 | 4H.8041.../2320145 | Air Lock Issue Call By: Customer Name :Datta Mishra No :9599637302 | Open | V. M. Technocoatings | Vidyut Engineers - Noida |  | Electric feed pump not installed from GOEM side. | Open | Kapil Solanki | To be check | Low
4 | 210415040 | 2024-02-17 14:17 | 125.4 | 4H.8041.../2420009 | Red Lamp Alam Issue Call By: Customer Name :Rahul No :9909018923 | Task Start | Panipat Elevated Corridor Limited. | Vishal Power Systems - PANIPAT | 12 | No DEF Consumption issue (as on now DG clocked 12 Hrs but DEF level is 100%) | Open | Kapil Solanki |  | Low
5 | 210414875 | 2024-02-17 13:26 | 320 | F6.8802.../2320080 | Voltage issue Call By Customer Name : Rhul kumar Singh Mobile No :9593182067 | Closed | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 32.15 | Customer having 90 KW Motor (Star delta), Jerk Load upto 400 Amp, customer motor was not working & Panel breaker tripping due to under Voltage. educated to customer to modify in panel if any issue related to voltage. | Open | Kapil Solanki |  | Low
6 | 210417985 | 2024-02-19 09:52 | 125.4 | 4H.8041.../2320174 | Under Speed Alarm Issue And Power Supply Issue Call By Customer Name :Vidhan Mandal Number :8384070276 | Closed | Kalka Krishna Engineering | Vidyut Engineers - New Delhi | 12.1 | NRV issue, as NRV the air is flowing in both direction.. Kept under observation | Open | Kapil Solanki | NRV failed part dispatch check | Low
7 | 210417977 | 2024-02-19 09:46 | 200 | 6H.8435.../2320010 | Abnormal Sound Issue Call By Customer Name :Sonilal Mobile No :9599382335 | Closed | BITS N BYTES SOFT PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 5 | Abnormal sound due to DC alternator clip broken, welded the plate and bolts replaced. | Open | Kapil Solanki | Field communication | High
8 | 210416927 | 2024-02-18 11:52 | 125.4 | 4H.8041.../2320108 | starting also and high engine noise at the load Email By - KGD Name - Shamim Ahmed | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Power Trading Company - ALWAR | 18.28 | Engine Starting issue due to air lock, Electric feed pump kit required. | Open | Sudhir Awasthi |  | Low
6 | 210417985 | 2024-02-19 09:52 | 125.4 | 4H.8041.../2320174 | Under Speed Alarm Issue And Power Supply Issue Call By Customer Name :Vidhan Mandal Number :8384070276 | Closed | Kalka Krishna Engineering | Vidyut Engineers - New Delhi | 12.1 | NRV issue, as NRV the air is flowing in both direction.. Kept under observation | Open | Kapil Solanki |  | Low
7 | 210417977 | 2024-02-19 09:46 | 200 | 6H.8435.../2320010 | Abnormal Sound Issue Call By Customer Name :Sonilal Mobile No :9599382335 | Closed | BITS N BYTES SOFT PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 5 | Abnormal sound due to DC alternator clip broken, welded the plate and bolts replaced. | Open | Kapil Solanki |  | High
8 | 210416927 | 2024-02-18 11:52 | 125.4 | 4H.8041.../2320108 | starting also and high engine noise at the load Email By - KGD Name - Shamim Ahmed | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Power Trading Company - ALWAR | 18.28 | Engine Starting issue due to air lock, Electric feed pump kit required. | Open | Sudhir Awasthi |  | Low
2 | 210422736 | 2024-02-20 14:52 | 500 | DV8.8501.C4../2320063 | Starting Issue Call By Customer Name :- 9797078588 Number :-9797078588 | Open | Himalaya Cold Chain Pvt. Ltd. | Suraj Motor Store - Srinagar | 3 | Engine Starting issue, updated Slow ramp up file DV8.1234 & Kept under observation untill Tomorrow morning. | Open | Sudhir Awasthi | Need to confirm CAL file app code | Low
5 | 210421447 | 2024-02-20 11:15 | 500 | DV8.8501.C4../2320033 | Load Issue And Voltage Issue Call By Customer Name : M.I Khan Mobile No :9306952708 | Task Start | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | Over-Current alarm, Decided to Analyse the Load. | Open | Kapil Solanki |  | Low
7 | 210421258 | 2024-02-20 10:42 | 250 | F6.8841.../2320019 | ECU mail funtion warning canopy door issue Call By Customer : Name :Narendra Nagar Number :9811818373 | Closed | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 32 | Rain Water entry into Canopy due to No Door Visor fixed on canopy (mail done GOEM team 'Jakson') | Open | Kapil Solanki |  | Low
9 | 210421036 | 2024-02-20 09:51 | 320 | F6.8802.../2320080 | Canopy broke issue from battery side Call By Customer Name : Rahul kumar Mobile No :9593182067 | Closed | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 39.28 | Rain water entry into Canopy due to excessive gap b/w Doors, Adjusted door Gap, Issue resolved. | Open | Kapil Solanki | Rain guard to check in commisioning sheet | Low
10 | 210421010 | 2024-02-20 09:43 | 57 | T4.8941.../2320137 | Fuel Meter & Vacume indicator to be Change | Task Start | R. Rajpoot Generator | Vidyut Engineers - Noida | 62 | Customer runs DG before Commissioning (DG clocked 61 Hrs on dated 19-Feb-24 during CC), Air Filter restriction indicator missing & Fuel gauge faulty, Fuel gauge replaced by SD team but Vaccum gauge yet to fit by GOEM (Jakson), Mail done by SD team. | Open | Kapil Solanki | Fuel gauge dispatch check | Moderate
11 | 210421008 | 2024-02-20 09:42 | 57 | T4.8941.../2320236 | GCU Update | Task Start | Air Water India Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 0.38 | Line rejection case, Low Fuel level alarm/Warning not appearing on GCU (even Fuel at 0% level), Provided GCU programming file to SD team but they are unable to update due to Software issue. | Open | Kapil Solanki |  | Low
5 | 210426426 | 2024-02-21 12:31 | 82.5 | 5H.8901.../2320034 | Display Issue Call By Customer Name :Suhas ... Mobile No :8225052174 | Closed | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 53.31 | DEF level % not showing in GCU, SD team will update GCU programming & confirm. | Open | Kapil Solanki |  | Low
7 | 210425665 | 2024-02-21 09:55 | 750 | DV2.8501.C4../2320024 | Tripping Â Issue Call By Service Dealer Name :Deepak Kumar Mobile No :7027820048 | Task Start | Bharat Rasayan Limited | M/s OM Diesels Pvt. Ltd. - Rohtak |  | Update not received | Open | Kapil Solanki |  | Low
1 | 210432995 | 2024-02-22 21:13 | 62.5 | T4.8941.../2320056 | Tripping & Emergency Stop Alarm Issue Call By Customer Name :- Joganver Singh No :- 9911146716 | Open | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 330 | Emergency switch depressed, Resolved Telephonically, SR will be cancelled. | Open | Kapil Solanki |  | Low
2 | 210432669 | 2024-02-22 18:09 |  | 4H.8041.../2320077 | FIP HUB CHANGE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Need to Replace FIP HUB, Visit scheduled for Monday. | Open | Sudhir Awasthi |  | Low
3 | 210432686 | 2024-02-22 18:06 |  | 4H.8041.../2320076 | FIP HUB REPLACE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Need to Replace FIP HUB, Visit scheduled for Monday. | Open | Sudhir Awasthi |  | Low
4 | 210432658 | 2024-02-22 18:06 |  | 4H.8041.../2320074 | FIP HUB CHANGE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Need to Replace FIP HUB, Visit scheduled for Monday. | Open | Sudhir Awasthi |  | Low
5 | 210432631 | 2024-02-22 18:02 |  | 4H.8041.../2320072 | FIP HUB CHANGE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Need to Replace FIP HUB, Visit scheduled for Monday. | Open | Sudhir Awasthi |  | Low
8 | 210430421 | 2024-02-22 15:31 | 57 | T4.8941.../2320165 | Tripping issue Call By Customer Name :-Pramod Kumar . Number :-9991185581 | Closed | Frank Metal Recyclers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 111 | SPN 100/3 High Oil Pressure detecetd, data log collected, No Solution for HO |  | Kapil Solanki | KRM data check | Low
13 | 210429187 | 2024-02-22 11:13 | 125.4 | 4H.8041.../2320134 | Display issue Call By Customer Name :Mohmmad Asif Ahmad Number :8445820675 | Task Start | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 225 | SPN/FMI : 5461/8, No solution from HO | Open | Sudhir Awasthi |  | Low
4 | 210444722 | 2024-02-24 20:21 | 57 | T4.8941.../2320262 | Battery Charger replace issue Call by Customer Name:Sunil Number: c | Open | KPC FLEXI TUBES PVT LTD | Vidyut Engineers - New Delhi |  | Confirmed with Customer no visit required, SR cancelled. | Open | Kapil solanki |  | Low
12 | 210438330 | 2024-02-24 09:24 | 500 | DV8.8501.C4../2320065 | Load Issue Call By Customer Name:-Sushil Sani No:-9643313744 | Open | KW. Security & Services Pvt. Ltd. | Diesel Engineers Sales & Service - Ghaziabad |  | Engineer will visit site Today. | Open | Kapil solanki |  | Low
14 | 210436851 | 2024-02-23 16:28 | 320 | F6.8802.../2320061 | Starting Issue Email By-Service Dealer Name:Kartikey Rajput | Task Start | Rai Indutrial Power Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 13 | SPN 4376/5 reverting value below low voltage code shown in controller issue not resolved but engine running ok | Open | kapil solanki |  | Low
2 | 210454316 | 2024-02-27 14:48 | 125.4 | 4H.8041.../2320169 | Diseal Tank clean Issue Call By Customer Name :Pradeep Verma Mobile No :9582199953 | Open | DIHAAN ENTERPRISES | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 13 | White smoke issue due to water mixed in fuel, SD team suggested Customer need replace fuel filter as well as Fuel tank cleaning, decision pending from Customer side & insisting for Warranty support. | Open | Kapil Solanki |  | Moderate
3 | 210454271 | 2024-02-27 14:46 | 160 | 6H.8475.../2320003 | Fan belt broken Email By Service dealer Name:-Sonu Rai | Closed | A.P.GENERATORS | Paluck Technologies Ltd. - Gurgaon | 363 | Fan belt broken Due to I bolt and alternator mounting bolt broken,after that the same issue resolved. | Open | Kapil Solanki | Need to check campaign | High
5 | 210453981 | 2024-02-27 14:01 | 125.4 | 4H.8041.../2320134 | Error Code Issue Call By Customer Name:- Mohmmad Asif Ahmad No:- 8445820675 | Task Start | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar |  | 5461/8 | Open |  | KRM data need check | Low
7 | 210453196 | 2024-02-27 12:40 | 160 | 6H.8475.../2320015 | Starting Issue Email By Service Dealer Name:-VISHAL POWER Systems | Task Start | Ambadi Enterprise | Vishal Power Systems - PANIPAT | 9 | Fuel leakage from e-Feed Pump T Joint, Order placed for Part. | Open | Kapil Solanki | Commisioning date need to check | Low
1 | 210461868 | 2024-02-28 17:51 | 125.4 | 4H.8041.../2420016 | ENGINE STARTING ISSUE DUE Email By - Service Dealer Name -SUNITA | Task Start | Juneja Construction (P) Ltd. | R K Engineers - Meerut | 702 | SPN/FMI : 51/5 & 51/0, ITV malfunction internally, Under EDO. | Open | Sudhir Awasthi | Same SR | Low
2 | 210460493 | 2024-02-28 17:26 | 40 | 3H.8951.../2320078 | Starting Issue Call By: Customer Name :Ashu No :9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 13 | ECM Cummunication error, found Unswitched Power Supply missing at ECM, Just open all connectors & reifitted the same, Issue resolved Kept under obserevation for 2 Days. | Open | Kapil Solanki |  | Low
3 | 210459119 | 2024-02-28 14:48 | 57 | T4.8941.../2320067 | Fan Belt Replacement Issue Call By: Customer Name :Joganver Singh No :9911146716 | Closed | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 363 | Counter purchase 4 V-belt Unit, no Failure. | Open | Kapil Solanki |  | Low
7 | 210457324 | 2024-02-28 10:48 | 125.4 | 4H.8041.../2320170 | Starting Issue Call By Customer Name :-Anirudh Singh Number :- 8534803481 | Closed | Gharonda Sahakari Awas Samiti Limited | Vidyut Engineers - Noida | 9 | DG commissioned on 14/2/2024,Customer facing Morning starting issuem not equipped with e-Feed Pump, need to install. | Open | Kapil Solanki |  | Low
10 | 210457070 | 2024-02-28 10:19 | 250 | F6.8841.../2420011 | Automation Issue Call by customer Name: Mohan lal Yadav Number:9717616023 | Open | The National Media Centre Cooperative House Building Society Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Total 4 DG at site, SR registered on wrong Asset mistakenly, need to cancel. | Open | Kapil Solanki |  | Low
11 | 210456900 | 2024-02-28 09:53 | 57 | T4.8941.../2320262 | Battery Charger replace issue Call by Customer Name:Sunil Number: 9810076170 | Closed | KPC FLEXI TUBES PVT LTD | Vidyut Engineers - New Delhi | 5 | Battery Chrager defective no Output team visited site to replace Battery Charger but when switched On GCU found burning odor in 640C seems short internally (when disconnected Power supply no smoke), | Open | Kapil Solanki |  | Moderate
3 | 210465471 | 2024-02-29 15:40 | 160 | 6H.8475.../2320031 | Urea Issue Call By Customer Name : Mohammad Amjad Mobile No : 8865019331 | Open | INFRA 13 PVT LTD | Diesel Engineers Sales & Service - Ghaziabad |  | Update not received yet | Closed | Kapil Solanki |  | Low
7 | 210463900 | 2024-02-29 11:57 |  | 5H.5301.../2300001 | Error Code issue Email By - Service Dealer Name -Shiv | Closed | Manitou Equipment India Pvt. Ltd. | Vidyut Engineers - Noida |  | SPN/FMI: 5419/1 just reset the DTC (BS V proto Engine) | Open | Kapil Solanki |  | Low
9 | 210463781 | 2024-02-29 11:43 | 625 | DV0.8501.C4../2320001 | Fuel Meter Issue Call By Customer Name : Pradip Kumar Mobile No : 8178306138 | Task Start | Tata Tele services | Vidyut Engineers - New Delhi |  | Confirmed with Customer, no issue in DG. | Closed | Kapil Solanki |  | Low
2 | 210486016 | 2024-03-03 09:11 | 125 | 4H.8041.../2320170 | Starting Issue Call By Customer Name :-Anirudh Singh Number :-8534803481 | Open | Gharonda Sahakari Awas Samiti Limited | Vidyut Engineers - Noida |  | DG commissioned on 14/2/2024,Customer facing Morning starting issue not equipped with e-Feed Pump, need to install. Also Battery charger disconnected by Customer, instructed SD team ask for Visit Charges from Customer. | Closed | Kapil Solanki |  | Moderate
7 | 210480425 | 2024-03-02 11:45 | 250 | F6.8841.../2320040 | Starting issue Call by customer Name: A.P Jain Number:9911142234 | Task Start | Anand lok CGHS.Mayur Vihar Phase 1 | Vidyut Engineers - New Delhi | 6 | No DEF Consumption as Dosing Pressure not stable (sudden drop), Team will revisit the site with carrying New Dosing module. | Closed | Gourav Sharma | Field visit planned today. | Low
10 | 210480066 | 2024-03-02 11:12 | 57 | T4.8941.../2320262 | Battery Charger replace issue Call by Service Dealer Name :- Vijay Number :-8510925432 | Closed | KPC FLEXI TUBES PVT LTD | Vidyut Engineers - New Delhi | 5.1 | Controller(KG 640C) short internally under EDO. | Closed | Kapil Solanki |  | Low
12 | 210479463 | 2024-03-02 10:12 |  | 5H.8901.../2320081 | Engine Starting issue | Task Start | Jakson & Company | Power Trading Company - Bhiwadi ( Alwar) |  | Update not received yet | Open | Kapil Solanki | Need details | Low
15 | 210470405 | 2024-03-01 13:48 | 200 | 6H.8435.../2320005 | Tripping issue Call By Customer:- Name:-Rakesh Number:-8383095890 | Task Start | Perfect Packaging | Diesel Engineers Sales & Service - Ghaziabad | 18.14 | Engine Starting issue as HPP/LPP Not delivering High Pressure fuel, suspected HPP faulty & same need to be replace, Instructed SD team place EDO for new HPP. | Closed | Gourav Sharma |  | Low
3 | 210491461 | 2024-03-04 16:49 | 125.4 | 4H.8041.../2420002 | Starting Issue Call By: Customer Name :Pradeep Kumar No :9350849220 | Task Start | Avibha Industries Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | E-Pump already installed from GOEM side, Sometimes an under speed alarm is coming , and the engine is tripping . Issue not resolved keep under observation | Closed | Kapil Solanki |  | Low
4 | 210491168 | 2024-03-04 16:17 | 160 | 6H.8475.../2320022 | Radiator Leakage Issue Call By Customer Name :- Arun Singh Mobile No :- 9001094434 | Task Start | Orient Coated Pvt Ltd | Power Trading Company - Bhiwadi ( Alwar) | 16 | Alternator Mounting bolt broken (other than iBolt) consequentially Radiator also got damaged PIR submitted, Need to replace affected parts | Closed | Kapil Solanki |  | High
15 | 210488417 | 2024-03-04 10:03 | 320 | F6.8802.../2420005 | Red Lamp Alarm Issue Call By Customer Name :-Manish Kumar Number :-9350174697 | Closed | Alko Plus Technosafe Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 13.46 | Low Def level @48% just top up the DEF & educated customer issue resolved. | Closed | Kapil Solanki |  | Low
16 | 210488168 | 2024-03-04 09:20 | 125.4 | 4H.8041.../2320176 | Urea to be topup Email By - Service Dealer Name -Shiv | Task Start | PMO. Cooperative Housing Society Limited | Vidyut Engineers - Noida | 30 | DEF level @56%, just top the DEF | Closed | Kapil Solanki |  | Low
1 | 210503874 | 2024-03-07 15:18 | 500 | DV8.8501.C4../2320044 | Oil Leakage Issue Call By Customer Name :-Jogender Number :-7015980672 | Task Start | Karan Power System | Vishal Power Systems - Karnal | 34 | Oil leakage due to loose oil filter, retighten the filter issue resolved. | Open | Sudhir Awasthi |  | Moderate
2 | 210503722 | 2024-03-07 14:56 | 15 | GP3.8501.../2320003 | Fuel Level Senor Voltage Low Issue Call By Customer Name:- Akash Pande No:- 7355543488 | Closed | Raj Cooling Systems Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 150 | fuel sensor float was stuck due to which there was a wrong indication of fuel level….Rectified the same issue resolved. | Open | Kapil Solanki |  | Low
3 | 210503374 | 2024-03-07 14:01 | 500 | DV8.8501.C4../2320060 | Trip_Genset_Low_Voltage | Closed | LNM. Auto Industries Private Ltd.. | Paluck Technologies Ltd. - Faridabad | 30.41 | Genset low voltage issue…further visited the site but no such issue found …..engine running ok…..will try to update the 500 kva starting issue file given. | Open | Sudhir Awasthi |  | Low
4 | 210503112 | 2024-03-07 13:15 | 125.4 | 4H.8041.../2320172 | High Adblue Consumption Issue Call By Customer Name :- Ram Singh Number :-9716488845 | Closed | Petty Petal Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 15.11 | High Adblue consumption due to jerk load of air compressor and also black smoke produced at the time of the jerk, educated the customer about the same. | Open | Sudhir Awasthi | Need details. | Low
5 | 210502816 | 2024-03-07 12:19 | 160 | 6H.8475.../2320014 | Error Code Issue Call By Customer Name :- Surendra . Mobile No :- 9536875744 | Task Start | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 29 | SPN/FMI: 516166/0 code was shown, reset the same also 40 Amp charging alternator fuse corroded, Clean the same, Issue resolved. | Open |  |  | High
6 | 210502674 | 2024-03-07 12:01 | 25 | GP3.8702.../2420004 | Black Smoke Issue Call By Customer Name :Tilak Raj Mobile No :9416334078 | Task Start | Shiv Urmila Bajaj Filling Station | Vishal Power Systems - PANIPAT | 30 | black smoke issue due to unbalance phase load( R,Y,B -23,4,0 respectively) ….educated the customer to balance load and operate the engine. | Open | Kapil Solanki | KRM check. | Low
7 | 210501997 | 2024-03-07 10:10 | 250 | F6.8841.../2320049 | Hunting Issue Email By Service Dealer Name:-Sunil Tomar | Closed | VSV. Polymers | R K Engineers - Meerut | 6.2 | Hunting issue due to jerk load of compressor while DG running ok without load, educated the customer to put step load. | Open | Kapil Solanki |  | Low
3 | 210515692 | 2024-03-10 15:24 | 160 | 6H.8475.../2320014 | Amber lamp alarm issue Call By Customer Name :-Ram Das Number :-9012533754 | Open | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 36 | SPN/FMI: 546166/0 code was shown again and again just to clear the DTC but appearing again & again. | Open | Kapil Solanki |  | Low
12 | 210510751 | 2024-03-09 10:17 | 500 | DV8.8501.C4../2320004 | Sensor issue Call By Customer Name :- Bijendra Kumar No :- 7633873576 | Cancelled | Indian Potash Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Asset out of territory, Wrong SR open from help desk, so that SR to be cancelled. | Open | Kapil Solanki |  | Low
1 | 210520796 | 2024-03-11 17:41 | 40 | 3H.8951.../2320106 | Starting Issue Call By Customer Name :-Ramendra Jha Number :-9958178702 | Task Start | Nuhydro | Vidyut Engineers - Noida | 10 | Engine starting issue due to Air lock as Fuel level @ 18% , Bleed system, Issue resolved. | Open | Kapil Solanki | Auto trip with low level need to check. Dead stock verification | Low
2 | 210519200 | 2024-03-11 16:00 | 320 | F6.8802.../2320066 | Starting Issue Call By Customer Name :- Chitrajan Mahapatra Number :-9717801603 | Task Start | IK. Power Solutions | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2.1 | Starting issue as Battery discharged (19 Volt) also GCU not Power up as wrong connection done by Panel team to Battery. | Open | Sudhir Awasthi |  | Moderate
3 | 210518878 | 2024-03-11 14:56 | 40 | 3H.8951.../2320051 | Coolent Leakage Issue Email By - Service Dealer Name -Deepjyoti Electricals & Services, CRM | Closed | BP. Home Pvt Ltd | Deep Jyoti Electricals and Services - Haldwani | 485 | Coolant leakage from Hose, Tighten Clamp & Top Up Coolant, Issue resolved. | Open | Sudhir Awasthi | Details required | Low
4 | 210518408 | 2024-03-11 13:29 | 625 | DV0.8501.C4../2320005 | Display Issue Call By Service Dealer Name :-Kapil Mobile No :-9953742728 | Closed | ST. Josephs Hospital | Diesel Engineers Sales & Service - Ghaziabad | 102 | SR generated just to update Deepsea Parameters (Cooling : 03 Min & Cooling at idle : 1 Min) | Open | Kapil Solanki |  | Low
5 | 210518138 | 2024-03-11 12:25 | 57 | T4.8941.../2320122 | Starting Issue Call By Customer Name :Omveer Singh Number :9999786175 | Closed | Chaudhary Generator Service | Vidyut Engineers - Noida | 20 | Low Fuel level alarm also Charging Alternator Voltage not appearing on GCU, Just tighten the negative wire, Issue resolved. | Open | Kapil Solanki |  | High
6 | 210517997 | 2024-03-11 12:00 | 125.4 | 4H.8041.../2320170 | Starting Problem Email By - Service Dealer Name -Shiv | Closed | Gharonda Sahakari Awas Samiti Limited | Vidyut Engineers - Noida | 3.59 | Earlier SR Cancelled due to Account merger. Battery Charger Connection unplugged from Mains supply, just connected the same, Issue resolved. | Open | Kapil Solanki |  | Moderate
7 | 210517301 | 2024-03-11 10:00 | 125.4 | 4H.8041.../2320056 | Starting Issue Call By: Customer Name :-Devendar Sharma No :-8950256020 | Closed | Srihans Technologies Exports Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 9.2 | Customer reported sometimes DG not start in 1st crank, e-Feed Pump fitted from GOEM side, SD team Check Fuel line thoroughly & found NRV connector in minor loose condition, Just tighten the same & Kept under observation. | Open | Kapil Solanki | Under observation | Low
2 | 210522975 | 2024-03-12 14:51 | 125.4 | 4H.8041.../2320134 | Error Code Issue Call By: Customer Name : Kasidh Ahmad No : 8445820675 | Open | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 38.46 | SPN/FMI : 5461/0 code was shown ,after that clear the DTC issue resolved but kept under observation. Waiting for new file. | Incident status | Kapil Solanki |  | Low
3 | 210522375 | 2024-03-12 12:29 | 125.4 | 4H.8041.../2320082 | Red Lamp Alam Call By Customer Name :Amit Mobile No :9557365953 | Closed | Christu Jyoti Convent Sr. Sec. School | R K Engineers - Meerut | 24 | SPN/FMI : 516166/0 code was shown ,after that clear the DTC issue resolved but kept under observation. | Open | Kapil Solanki | KRM data | Low
1 | 210528228 | 2024-03-13 18:13 | 57 | T4.8941.../2320258 | Emergency Stop Alarm issue Message By Customer Name:- Goldee Kumar Number:- 8700470505 | Task Start | Swastik Components Private Limited | Paluck Technologies Ltd. - Faridabad | 20.2 | Emergency alarm is displaying in controller, engineer visited site late night, today electrical engineer will visit the site. | Closed | Kapil Solanki |  | Low
2 | 210530347 | 2024-03-14 14:56 | 200 | 6H.8435.../2320015 | Stopping Issue Call by customer Name:-Aakash Mobile :-8979229856 | Open | Indo World Space | Diesel Engineers Sales & Service - Ghaziabad |  | Customer not responding to Phone calls, No Visit done yet. | Closed | Kapil Solanki |  | Low
4 | 210529760 | 2024-03-14 12:27 | 320 | F6.8802.../2320006 | Trip_Genset_Low_Voltage | Open | Super Seal India Ltd. | Paluck Technologies Ltd. - Faridabad |  | SR Open due to KRM, SD team contact with customer, there is no issue as per customer voice, SR cancelled. | Closed | Kapil Solanki | KRM data check. | Low
6 | 210529481 | 2024-03-14 11:38 | 250 | F6.8841.../2420015 | Line Rejection | Task Start | Nestle Cooprative Appartment Group Housing | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 2 | Engineer visited the site for commissioning found only 2 earthing at site, also foundation are not proper and one side canopy rain guard is not fitted. | Closed | Kapil Solanki |  | Low
8 | 210529359 | 2024-03-14 11:13 | 125.4 | 4H.8041.../2420084 | Trip_Genset_Low_Voltage | Task Start | Aggaarwal Art & Pattern Pvt. Ltd. | Diesel Engineers Sales & Service - Ghaziabad |  | Engine starting issue, only starting in Over-ride mode, need to update GCU programming, SD team will visit today. | Open | Kapil Solanki |  | Low
1 | 210543761 | 2024-03-17 15:07 | 125.4 | 4H.8041.../2320058 | . | Task Start | AMPS Power India Pvt Ltd. | Paluck Technologies Ltd. - Gurgaon | 2 | Ad blue level is not showing in display and also the canopy roof was damaged on both sides, and electrical feed pump kit relay card is not present in panel, work in progress, Escalated to HO | Closed | Kapil Solanki |  | Moderate
3 | 210542632 | 2024-03-16 17:44 | 125.4 | 4H.8041.../2320147 | Starting Issue Call By Customer Name :-kalra Mobile No :-9810017664 | Open | SHAKTI PROPERTIES | Vidyut Engineers - New Delhi |  | Customer have two DG sets, one is CPCB 2 and one is CPCB 4 customer complaint is regarding CPCB 2 but SR open for CPCB 4 by misunderstanding, mail drop for SR cancellation. | Closed | Kapil Solanki |  | Low
5 | 210538752 | 2024-03-16 10:40 | 750 | DV2.8501.C4../2320005 | Trip_Genset_Low_Voltage | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 113.5 | DG not taking load (Tripping with Low Genset Voltage on 200 KW load) also Excessive black smoke issue, Exhaust Piping issue. | Closed | Gourav Sharma |  | Low
8 | 210534990 | 2024-03-15 13:38 | 320 | F6.8802.../2320018 | Trip_Genset_Low_Voltage | Open | Geeta Metal | Power Trading Company - Bhiwadi ( Alwar) |  | SR Open due to KRM, SD team contact with customer, there is no issue as per customer voice, SR cancelled. | Open | Sudhir Awasthi | KRM data check | Low
5 | 210545440 | 2024-03-18 10:28 | 40 | 3H.8951.../2320105 | Low Speed Alam Issue Call By Customer Name:RAJAT AGARWAL No:9811508302 | Open | Hitech Led Fixtures And Lightings | Diesel Engineers Sales & Service - Ghaziabad |  | Visit not done yet | Closed | Kapil Solanki |  | Low
8 | 210546818 | 2024-03-18 14:17 | 160 | 6H.8475.../2320011 | VOC-ENGINE NOT STARTING Customer Name-Amit Customer Number-9811792368 Mode- SR Generated through CDI calling. | Task Start | Kashish Plastic Industries | Diesel Engineers Sales & Service - Ghaziabad |  | Visit not done yet | Open | Kapil Solanki |  | Low
11 | 210549148 | 2024-03-18 19:00 | 750 | DV2.8501.C4../2320024 | Starting Issue Call By Customer Name :-Anup Kumar Yadav Number :- 9466728946 | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 112.1 | Exhaust Piping not correct, Black smoke issue. | Closed | ASM Name |  | Low
12 | 210549166 | 2024-03-18 19:24 | 125.4 | 4H.8041.../2420036 | AdBlu issue Call By Customer Name :Hari Dutt Mobile No :9520854571 | Open | NEERAJ GENERATOR WORKS | M/s OM Diesels Pvt. Ltd. - Sonipat |  | Visit not done yet | Open | Kapil Solanki |  | Low
2 | 210553478 | 2024-03-19 19:36 | 320 | F6.8802.../2320030 | Trip_Genset_Low_Voltage | Open | Atma Autotech Engineers Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | SR Open due to KRM, SD team visited but DG was in running condition so unable to check, Customer confirmed DG shows under Voltage alarm during Jerk Load, Ask SD team to collect Deepsea event log, Data Log & KRM data. |  | Kapil Solanki | KRM data check | Low
3 | 210553241 | 2024-03-19 17:57 | 40 | 3H.8951.../2320039 | Main panel issue | Task Start | AMPS Power India Pvt Ltd. | Paluck Technologies Ltd. - Gurgaon | 5 | Customer complained for main panel issue…further engineer visited site checked all parameter and engine found running ok and concluded issue is from customer panel as DG don’t have any issue. |  | Kapil Solanki |  | Low
7 | 210551002 | 2024-03-19 13:34 | 125.4 | 4H.8041.../2420056 | Starting Issue Email By - KGD Name -Pooja Sharma | Closed | Shri Vishnu Refractories Ltd. | Power Trading Company - ALWAR | 4 | SPN/FMI : 516166/0 Code was shown, clear the DTC issue resolved.kept under observation | Closed | Kapil Solanki |  | Low
8 | 210550642 | 2024-03-19 12:33 | 320 | F6.8802.../2320039 | Auto Problem & Synchronization Email By Service Dealer Name:- Janmejay Kumar Rajput | Task Start | EXPRESS TOWERS PVT LTD | Espiem Engines & Machines (P) Limited - Agra | 6.27 | DG Synchronization issue, discussed with HO RRT team & decided to replace ECU .. | Open | Kapil Solanki |  | High
3 | 210556105 | 2024-03-20 16:27 | 125.4 | 4H.8041.../2320118 | Alarm Complaint Email By - OEM Name -Pardeep Khetarpal | Open | Rao Tent House | OVN Industries Private Limited - New Delhi |  | Asset transferred to Rewari Location. SR transferred to Plauck Technology. | Closed | Kapil Solanki | Issue need to check. | Low
6 | 210554092 | 2024-03-20 10:42 | 125.4 | 4H.8041.../2420090 | Starting Issue Call By: Customer Name :Divakur Thakur No :9818683289 | Closed | Metro Electric Services | Vidyut Engineers - Noida | 1.58 | SPN/FMI : 3031/14 code was shown, clear the DTC, instructed SD team to update dummy cal. | Closed | Kapil Solanki |  | Low
1 | 210560108 | 2024-03-21 16:31 | 1000 | DV8.8501.C4../2320074 & 2320086 | Engine Starting Issue | Task Start | Neelkanth Star Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 46.1 | Optiprime line rejection case, Engine 1 ECU communication error, Today team visiting to replace the ECU. | Open | Kapil Solanki |  | High
3 | 210559224 | 2024-03-21 14:14 | 30 | 3H.8902.../2320107 | Maintenance Due Alarm Issue Call By Customer Name :Archna Mobile No :8800399931 | Closed | Ajay Goel Textiles Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 46 | Maintenance due alarm also G1 CSP due on 30th Jan 24, Quotation submitted to Customer but no response, Asked SD team to send Warning Letter to Customer. | Closed | Kapil Solanki |  | Low
5 | 210558133 | 2024-03-21 11:14 | 82.5 | 5H.8901.../2320104 | Fuel meter to be change | Task Start | Max Power Solution | Vidyut Engineers - Noida |  | Fuel level always shows 0% just disconnect & reconnect the connector, Issue resolved during Commissioning. | Closed | Ved Gupta |  | Low
1 | 210561559 | 2024-03-22 09:30 | 82.5 | 5H.8901.../2320053 | Starting issue Call by Customer Name :-Amit Jain Number :- 9350782691 | Closed | Rock Rubber Industries | Diesel Engineers Sales & Service - Ghaziabad | 10 | Emergency Switch Physically broken, Bypass Emergency switch, Needs replacement on paid bases. | Open | Gourav Sharma |  | Low
2 | 210561602 | 2024-03-22 09:47 | 160 | 6H.8475.../2320002 | Electrical Feed pump to be Change Email By Service dealer Name :-Shiv | Closed | HNA. Contracting & Trading LLP. | Vidyut Engineers - Noida | 7.34 | Engine starting trouble, Installed e-Feed Pump, issue resolved. | Closed | Kapil Solanki |  | Low
3 | 210561875 | 2024-03-22 10:39 | 125.4 | 4H.8041.../2320013 | fuel filter issue Call By: Customer Name :Pravin Singh No8529405105 : | Closed | JAYCEE CASTALLOYS (P) LTD. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 20.7 | Engineer visited the site and found 0% DEF level in controller .. Checked physically but DEF was available checked the header unit of DEF tank and found float was moving also.. Cleaned the same and checked the DEF level at 64% issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210561915 | 2024-03-22 10:43 | 125.4 | 4H.8041.../2320145 | Electrical Feed pump to be Change Email By - Service Dealer Name - Shiv Vidyut Engineers | Closed | V. M. Technocoatings | Vidyut Engineers - Noida | 22 | SR open for Electric feed pump kit installation also found low def level top up the same issue resolved, and educated to the customer about same. | Closed | Kapil Solanki |  | Low
5 | 210561975 | 2024-03-22 10:52 | 125.4 | 4H.8041.../2320087 | Starting Issue Call by customer Name : Zakir Hussain Number : 8376811789 | Closed | CIPL. Corporate Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 55.27 | Multiple DTC related to DEF level also def level & concentration not showing, checked DEF tank header connections found ok, then checked panel found (2A1 to 2A8 ) fuse internally malfunctioning replace the same issue resolved.( All mention in PIR) and for( 3031/14) flashing dummy file issue resolved. | Closed | Kapil Solanki |  | Low
6 | 210562032 | 2024-03-22 11:03 | 30 | 3H.8902.../2320011 | Automation Issue Call By Customer Name :- Parmeet Singh Mobile No :- 9899282225 | Closed | Parmeet Singh Nayar | Vidyut Engineers - New Delhi | 5.55 | Customer complained for automation issue engineer visited site and found customer auto panel wire loose, no issue in DG. | Closed | Kapil Solanki |  | Low
7 | 210562104 | 2024-03-22 11:16 | 750 | DV2.8501.C4../2420006 | Fuel Tenk Cap Issue Call By Customer Name :Sachin Kumar Mobile No 9931028639 | Closed | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida | 4.34 | As per Customer Fuel tank cap was not locking but it was ok.. Trained the customer about the same issue resolved. | Open | Kapil Solanki |  | Moderate
8 | 210562788 | 2024-03-22 13:21 | 500 | DV8.8501.C4../2320082 | Red light alarm issue Call by Customer Name :-Anand Number :- 9911319889 | Closed | PG. Electroplast Ltd. | Diesel Engineers Sales & Service - Ghaziabad | 15 | Low DEF level alarm (43 % in Tank 1 & 39 % in Tank B). Top up the same also educated Customer, Issue resolved. | Closed | Kapil Solanki |  | Low
9 | 210563110 | 2024-03-22 14:51 | 82.5 | 5H.8901.../2320021 | Starting Issue Call By Customer Name: raju kumar No:9821521689 | Closed | CRMK Select | Vidyut Engineers - Noida | 52.59 | SR generated to change controller parameter engine control unit (Oil Pressure protect action - warning to shutdown | Closed | Kapil Solanki |  | Low
10 | 210563421 | 2024-03-22 15:56 | 100 | 4H.8041.../2420057 | Starting Issue Call By Customer Name :Ashish Mobile No :6280223509 | Closed | Adidas India Marketing P Ltd | Dynamic Engineering Services - Jalandhar | 8 | Low Fuel level alarm, Just remove & refit the Fuel level sensor connector, Issue resolved | Closed | Kapil Solanki | KRM data check. 18-03- Fuel level alarm. CC- 20-02 | Low
11 | 210565804 | 2024-03-22 19:16 | 160 | 6H.8475.../2320024 | High Temperature Issue Call By Customer Name : Sunder Singh No : 9672973802 | Task Start | CHRYSO INDIA PRIVATE LIMITED | Power Trading Company - ALWAR | 45.9 | High Engine Temp alarm, SD team visited & found V-Belt in decoupled condition also Alternator Pulley in Loose condition, sent Failed Alternator to SEG for anaylses, Warranty rejected & got confirmation Alternator is irreparable, Recommend to replace affected Parts (Alternator, Pulley & V-belt) | Open | Kapil Solanki | One pager with details to QA | High
12 | 210565808 | 2024-03-22 19:31 | 160 | 6H.8475.../2320028 | Starting Issue Call By: Customer Name :Rabbani. No :9015201975 | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 24.59 | Starting issue due to discharged battery, checked and found battery charger connections was not fitted refitted the charger issue resolved. | Closed | Kapil Solanki |  | Moderate
13 | 210566157 | 2024-03-23 08:13 | 125.4 | 4H.8041.../2420084 | Trip_Genset_Low_Voltage | Task Start | Aggaarwal Art & Pattern Pvt. Ltd. | Diesel Engineers Sales & Service - Ghaziabad |  | Confirmed with Customer, no issue in DG. SR cancelled | Closed | Kapil Solanki |  | Low
14 | 210566444 | 2024-03-23 10:01 | 250 | F6.8841.../2320047 | Abnormal Sound Issue Call By Customer Name :-Sushil .. Number :-8860089233 | Closed | TRACTEBEL ENGINEERING PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 48 | SPN/FMI:4358/2 engineer checked DEF related connection issue not resolved planned to change supply module. | Closed | Kapil Solanki |  | Moderate
15 | 210566752 | 2024-03-23 11:11 | 20 | GP3.8601.../2320055 | Oil Leakage Issue Call By Customer Name :- Ravi ... Mobile No :- 9818841343 | Closed | Feeken Seating Collection Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 180 | Fuel leakage due to loose fuel filter, retighten the same issue resolved (SD team carried out CSP at 154 HRs on dated 18-Mar-24) | Closed | Ved Gupta | Details required. SD mistake | Low
16 | 210566816 | 2024-03-23 11:14 | 320 | F6.8802.../2320064 | Error Code Issue Call By Customer Name :-Pramod Sharma Number :-9958800244 | Closed | Floeter India Retort Pouches Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 43 | Low Ad blue level , top up the DEF issue resolved. Suggested to the customer about same. | Closed | Ved Gupta |  | Low
17 | 210566889 | 2024-03-23 11:37 | 125.4 | 4H.8041.../2420027 | Oil Leakage Issue Email By - Customer Name - VINOD RANA | Closed | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 246 | Minor Oil leakage from flywheel side. No further check done (Suspected leakage from Flywheel end Oil seal) . Pending on SD side. | Closed | Kapil Solanki |  | High
18 | 210568646 | 2024-03-23 17:19 | 57 | T4.8941.../2320166 | Trip_Genset_Low_Voltage | Open | CAPRI TRANSFORMERS PRIVATE LIMITED | Power Trading Company - Bhiwadi ( Alwar) |  | No update | Open | Kapil Solanki |  | Low
19 | 210569308 | 2024-03-23 17:45 | 320 | F6.8802.../2320058 | Radiator Fan Issue Call By: Customer Name :Prashant Chaudhary No :7011506842 | Open | Popcorn Furniture and Lifestyle Pvt. Ltd. | Vidyut Engineers - Noida |  | Issue resolved on call. SR cancelled. | Open | Kapil Solanki |  | Low
20 | 210569380 | 2024-03-23 18:10 | 320 | F6.8802.../2320002 | Maintenance Due Alarm Call By Customer Name :- Irfan Mobile No :- 7889711040 | Closed | Akbar Agro Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar | 1010 | Maintenance due alram, DG Service done & suggested SD team to close in CSP SR. | Closed | Gourav Sharma |  | Low
21 | 210569889 | 2024-03-24 14:29 | 125.4 | 4H.8041.../2320073 | Tripping issue Call By Customer Name :Sunny Number :8826285164 | Task Start | GUPTA SAREES CENTRE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 92 | DG tripping due to Low Ad blue level alarm (at 8 %) top up the DEF issue resolved and educated to the customer maintain DEF level between 50 to 90 % for trouble free operation. | Closed | Kapil Solanki |  | Low
22 | 210569914 | 2024-03-24 16:04 | 15 | GP3.8501.../2320041 | Red Lamp On Alarm Issue Call By Customer Name:Govind Number :8393890100 | Open | Growmore Signnage LLP. | Espiem Engines & Machines (P) Limited - Agra |  | SD team will attend the site today | Closed | Sudhir Awasthi |  | Low
1 | 210572468 | 26-03-2024 10:22 | 500 | DV8.8501.C4../2320015 | Tripping Issue Call By: Customer Name :Sandeep No :7683063488 | Task Start | MTI. Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Sonipat | 202 | Coolant mixed in Engine Oil due to Puncture Oil Cooler assy, EDO placed for Oil Cooler assy. | Open | Kapil Solanki |  | Moderate
2 | 210572997 | 26-03-2024 12:31 | 82.5 | 5H.8901.../2320043 | Automation Issue Call By Customer Name :- Vijendra .. Mobile No :- 9416517717 | Closed | Mr. Ravinder Kumar | M/s OM Diesels Pvt. Ltd. - Rohtak | 30 | Customer panel side issue…. Proper connection not done of mains… Guided him to correct the same. | Open | Kapil Solanki |  | Low
3 | 210573329 | 26-03-2024 14:23 | 500 | DV8.8501.C4../2320026 | Parameter Chang Issue Call By Customer Name:Imtiyaz Ahmed No:9697461646 | Task Start | M/s. Mas Agro Fresh | Suraj Motor Store - Srinagar | 116 | SR generated, to Update parameters (cooling time and idle cooling time) | Closed | Kapil Solanki |  | Low
4 | 210573599 | 26-03-2024 15:36 | 320 | F6.8802.../2320002 | ECU issue Call By Customer Name :-Irfan Mobile No :-6006102939 | Task Start | Akbar Agro Fresh Pvt. Ltd. | Suraj Motor Store - Srinagar | 1016 | SPN/FMI-3031/14 code was shown,flashing the dummy file (F6_D3.1234_V0) issue resolved. But kept under observation. | Open | Kapil Solanki |  | Low
5 | 210574150 | 26-03-2024 16:38 | 125.4 | 4H.8041.../2420036 | VOC-: AdBlu issue Customer Name- PankajCustomer Number-9694385606 Mode- SR Generated through CDI calling. | Task Start | NEERAJ GENERATOR WORKS | M/s OM Diesels Pvt. Ltd. - Sonipat | 174 | SPN/FMI : 5461/0 code was shown,flashed the latest calibration file issue resolved but kept under observation. As per customer voice there is no DEF Consumption & engineer found there is less than 50% load | Open | Gourav Sharma | KRM data check. DEF consumption | Low
6 | 210574498 | 26-03-2024 17:36 | 320 | F6.8802.../2320035 | Starting issue and Preventive Maintenance Call By Customer Name :Kamal Singh Mobile No :9810018250 | Task Start | Pan India Consultants Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 172 | Customer used Non Koel battery charger, battery discharge due to non koel battery charger are internal malfunction . Connected koel battery charger and charging the battery issue resolved. | Closed | Kapil Solanki |  | Moderate
7 | 210574568 | 26-03-2024 17:53 | 30 | 3H.8902.../2320054 | Trip_Genset_Low_Voltage | Open | Asha Sharma | Diesel Engineers Sales & Service - Ghaziabad |  | KRM generated SR, contact to the customer and found DG was tripping with showing under voltage alarm , guided to the customer on phone call checked the fuel line, and found air lock issue,open the fuel line and refitted the same issue resolved. Mail dropped for SR cancellation. | Closed | Kapil Solanki | KRM data | Low
8 | 210574602 | 26-03-2024 18:00 | 125.4 | 4H.8041.../2420045 | Battery Issue Call By Customer Name:Bupedra Yadav No:9057201129 | Task Start | Shorya Auto Industries | Power Trading Company - ALWAR | 10.22 | No Output form Charging Alternator, Repaired at BOSCH Dealer, issue resolved | Open | Kapil Solanki |  | High
9 | 210575256 | 27-03-2024 10:24 | 125.4 | 4H.8041.../2320143 | Voltage Fluctuation Issue Call By: Customer Name :Pradeep No :9671711123 | Open | Ishwar Eye Center LLP. | M/s OM Diesels Pvt. Ltd. - Rohtak |  | Customer complained about the voltage fluctuation issue, SD team visited the site ,but the customer was not allowed to check the DG on load. | Closed | Sudhir Awasthi | No any fluctuation observed in KRM data | Low
10 | 210575271 | 27-03-2024 10:31 |  | GP3.8604.../2420128 | Lub Oil Sump Fitment | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | Line Rejection SR, Lube oil sump got damaged during transportation, New oil sump fitted issue resolved. | Closed | Gourav Sharma |  | Low
1 | 210580199 | 28-03-2024 12:14 | 30 | 3H.8902.../2320151 | Display Issue Call By Customer Name :Anuj Mishra Mobile No :7703987754 | Task Start | Saras Medical Services | OVN Industries Private Limited - New Delhi | 10 | Fuel level not showing on controller... checked and found Fuel sensor connector wire in push back condition, rectified the same issue resolved. | Closed | Kapil Solanki |  | Low
2 | 210579248 | 28-03-2024 08:54 | 125.4 | 4H.8041.../2320056 | Starting Issue Call By: Customer Name :-Devendar Sharma No :-8950256020 | Task Start | Srihans Technologies Exports Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 10 | e-feed pump kit came fitted from GOEM, Starting issue on suspect bases change the all copper washer also reprogrammed GCU KG640C | Closed | Kapil Solanki |  | Low
3 | 210578993 | 27-03-2024 20:59 | 82.5 | 5H.8901.../2320098 | Stopping Issue Call By: Customer Name :Virendra Bhatnagar No :8146660822 | Closed | Etica Hospital & Research | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 37 | Mains Fault, EB team carried out some work in Distribution panel so one Phase voltage missed, DG not stopped in Auto so Customer ised in Emergency switch & forgot to correct the same. Starting issue as Emergency switch in depressed condition, correct the same, Issue resolved. | Closed | Kapil Solanki |  | Low
4 | 210578902 | 27-03-2024 18:34 | 57 | T4.8941.../2320100 | not working. Email By-Customer Name:- Gaurav Tiwary | Closed | Rishabdeo Crearions Pvt. Ltd. | Vidyut Engineers - Noida | 34.46 | Commissiong date : 2/Jan/2024, Battery was discharged due to battery charger not connected to mains supply, connected the same issue resolved (SD negligence) |  | Kapil Solanki |  | Moderate
5 | 210578728 | 27-03-2024 17:39 | 500 | DV8.8501.C4../2320021 | Over Heat Issue & Voltage Fluctuation Call By Custmer Name :- Amit Tripathi Number :- 6392153886 | Open | SUPRA CRAFT INDIA LTD | Power Trading Company - Bhiwadi ( Alwar) |  | Engineer will visit the site tomorrow. |  | Kapil Solanki |  | Low
6 | 210576839 | 27-03-2024 15:42 | 320 | F6.8802.../2320063 | Display issue Call By: Customer Name :Rajnit No :9466229323 | Task Start | Vashisth Estates Limited | Paluck Technologies Ltd. - Faridabad | 3.1 | Battery was discharged because of DG is not running from last few days also battery charger connection not done as Charger placed in Auto Panel (Supplied by Jakson) & Mains supply not provided by Customer during Commissioning , connected the same issue resolved. |  | Kapil Solanki |  | Moderate
7 | 210576640 | 27-03-2024 15:10 | 320 | F6.8802.../2420021 | Coolant leakage Issue Call by Customer Name ; MANISH GHAI ... Number ; 8920360676 | Closed | HENNA INDUSTRIES PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 7 | Customer complained about a coolant leakage issue, engineer visited the site and found coolant overflow from the recovery bottle due to excessive coolant, correct the same issue resolved. |  | Gourav Sharma |  | Low
8 | 210576389 | 27-03-2024 14:22 | 57 | T4.8941.../2320062 | Coolant Top Up Email By Service dealer Name :-Shiv | Closed | AMIT SEHGAL | Vidyut Engineers - Noida | 112.6 | This SR was mistakenly open for coolant top up which was not needed but customer demanded for coolant top up..but no any issue in DG . |  | Ved Gupta |  | Low
9 | 210576237 | 27-03-2024 13:41 | 15 | GP3.8501.../2320041 | Starting Issue Email By Service dealer Name :-Janmejay Kumar Rajput | Closed | Growmore Signnage LLP. | Espiem Engines & Machines (P) Limited - Agra | 11 | SPN/FMI :190/8 ( Engine speed sensor fault) and also 224/8 (LOP open fault) code was shown,open the sensor connector and refitted the same issue resolved. |  | Kapil Solanki |  | Low
10 | 210576024 | 27-03-2024 12:59 | 200 | 6H.8435.../2320026 | liquid leakage Issue Email By Service dealer Name :-VINIT KUMAR JAIN | Closed | Ajanta Colors Industry | Power Trading Company - Bhiwadi ( Alwar) | 15.51 | Lube oil leakage due to loose oil filter,tighten the same issue resolved. |  | Kapil Solanki |  | Moderate
11 | 210575727 | 27-03-2024 12:05 | 40 | 3H.8951.../2320050 | Oil leakage Issue and Preventive Maintenance Call By: Customer Name :Omveer Singh No :9999786175 | Closed | Chaudhary Generator Service | Vidyut Engineers - Noida | 445 | Oil leakage issue from rocker cover. Bolt in loose condition, tighten the same issue resolved. |  | Kapil Solanki |  | Low
12 | 210575521 | 27-03-2024 11:17 | 750 | DV2.8501.C4../2420006 | Fuel Issue call by Customer Name ; Sachin Kumar Number ; 9931028639 | Closed | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida | 4.37 | Wrong fuel level shown in controller due to stuck fuel sensor (float was not moving) correct the same issue resolved. |  | Gourav Sharma |  | Low
13 | 210575445 | 27-03-2024 11:02 | 250 | F6.8841.../2320047 | Starting Issue Email By Service dealer Name :-Kartikey Rajput | Closed | TRACTEBEL ENGINEERING PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 49 | Engineer visited the site and found that the supply module connection( DEF tank to supply & return line interchanged) was wrongly fitted at the time of servicing by the previous engineer , correct the same issue resolved. |  | kapil Solanki |  | Moderate
1 | 210583864 | 29-03-2024 11:57 | 500 | DV8.8501.C4../2320061 | ECU Warning alarm issue Call by customer Name : Kishan Number:7906268082 | Task Start | PG. Electroplast Ltd. | Vidyut Engineers - Noida | 19.26 | SPN/FMI: 3465/1, Bank 'B' ITV Fault open circuit due to loose connection of male and female connector in control panel, tighten,with cable tie issue resolved. |  | kapil Solanki |  | Low
2 | 210582638 | 28-03-2024 19:21 | 82.5 | 5H.8901.../2320084 | Display Issue & Alarm Issue Call By Customer Name:-Sunny Rana No:-7718681956 | Open | KALYAN JEWELLERS INDIA LTD. | OVN Industries Private Limited - New Delhi | 55 | Low Fuel level alarm (12%) was shown, top up the fuel. also minor Oil leakage from Oil filler cap tighten the same issue resolved. |  | kapil Solanki |  | Low
3 | 210582475 | 28-03-2024 17:48 | 15 | GP3.8501.../2320041 | Red Lamp On Alarm Issue Call By Customer Name: Govind Number :8393890100 | Task Start | Growmore Signnage LLP. | Espiem Engines & Machines (P) Limited - Agra | 14 | DG tripping with Red lamp, Under speed, & Emergency stop alarm, Checked Emergency switch suspected its not functioning, By pass the same then Taken trial 20 mins, Issue resolved. earlier faced Low Oil Pressure & Engine Crank sensor related alram, Placed EDO for LOP & Emergency switch. |  | Ved Gupta |  | High
4 | 210581579 | 28-03-2024 16:37 | 160 | 6H.8475.../2320039 | Loading issue Call By Customer Name: Rahul Singh Number:7876792767 | Open | A. P. Cranes Pvt. Ltd. | Power Trading Company - Bhiwadi ( Alwar) |  | Load fluctuation issue, Planned for Load analyses with GOEM team. Dealer is being terminated so there is a Men power issue. |  | kapil Solanki |  | Low
5 | 210581466 | 28-03-2024 16:14 |  | 5H.5351.C1../2300001 | Starting Issue Email By Service Dealer Name:- Ramesh Kumar | Task Start | AJAX ENGINEERING PRIVATE LIMITED | H.S Enterprises - Leh | 28.2 | Field trial & Validation of BSV Engine, SR generated for Claim purpose. |  | kapil Solanki |  | Low
6 | 210581151 | 28-03-2024 15:54 | 750 | DV2.8501.C4../2320048 | Starting Issue Call By Service Dealer Name :Asish Mobile No :9718850143 | Closed | Jai Mata DI. Generator Service | Vidyut Engineers - Noida | 9.4 | DG tripping due to Negative Phase Sequence alarm, found Unbalance load from Customer side, instructed customer to balance the Load. |  | kapil Solanki | KRM check. No variation in data found. | Low
7 | 210581075 | 28-03-2024 15:34 | 320 | F6.8802.../2420018 | Under Frequency Alarm Issue Call By Customer Name :- Hari Datta Mobile No :- 9958425449 | Closed | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad | 2 | Customer complained about an under frequency alarm issue... SD team visited the site and checked the DG manually and also checked on load but no issue was found..informed the customer about the same. |  | kapil Solanki |  | Low
8 | 210580962 | 28-03-2024 15:17 | 82.5 | 5H.8901.../2320006 | Controller Faulty Urea not show | Task Start | M. K. Textiles | Vishal Power Systems - PANIPAT |  | Line Rejection SR, DEF level not showing in controller, reprogram the same but issue not resolved,then discussed with HO RRT team , Controller will replace. EDO placed for the same. |  | kapil Solanki | Cut off number of controller. | Low
1 | 210587603 | 30-03-2024 11:51 | 250 | F6.8841.../2320006 | Starting issue Call by customer Name : Pravin Gard Number:9818577517 | Open | Katyayani Industries | Power Trading Company - Bhiwadi ( Alwar) |  | Telephonically checked by ASE, SPN/FMI: 168/3, Attended by KGD team. Dealer is being terminated so there is a Men power issue. |  | kapil Solanki |  | Low
2 | 210587374 | 30-03-2024 11:03 | 250 | F6.8841.../2320019 | Oil Leakage Issue Email By - OEM Name - Ashutosh Kumar Singh | Task Start | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 61 | Customer complained about oil leakage issue, engineer visited the site and found fuel seepage from Filler Pipe hose as tank was filled @ 100 % Educated customer to fill the tank (90 to 95 % .) |  | kapil Solanki |  | Low
3 | 210587321 | 30-03-2024 10:50 | 57 | T4.8941.../2320135 | Starting Issue Call By Customer Name :- Khosra . Mobile No :- 9899225353 | Task Start | AHUJA GENSETS | Vidyut Engineers - Noida | 868 | SPN/FMI: 97/5 ( Water in fuel ) alarm was shown,checked physically sensor connector found ok,reset the alarm issue resolved.but kept under observation. |  |  |  | Low
4 | 210587253 | 30-03-2024 10:40 | 750 | DV2.8501.C4../2420004 | Starting Issue Call By Customer Name : Ravi Rajput Mobile No :8800770694 | Open | Skardi Greens | Paluck Technologies Ltd. - Ghaziabad |  | Not attended, Earlier Dealer (DESS) is being terminated so there is a Men power issue. |  |  | Not attended | Low
5 | 210587031 | 30-03-2024 09:51 | 40 | 3H.8951.../2420040 | Starting issue Call by Customer Name :-Bablu Number :-7837494729 | Task Start | Raj Kumar Rai | Royal Power Solutions - Zirakpur | 1 | Starting issue due to Loose connection on Relay Card (-1 & +1 Input wire), Tighten the same, Issue resolved. |  |  |  | Low
6 | 210586906 | 30-03-2024 08:55 | 125.4 | 4H.8041.../2320041 | Power Supply issue Call By Customer Name : Giby Jackob Mobile No : 9891123347 | Closed | Drivewell Auto Industries. | Paluck Technologies Ltd. - Faridabad | 43 | External fuse box installed by customer in between koel panel and customer panel, as the cable size is of lower size, Educated customer remove the fuse box and install the cable of at least 120 sqmm size. |  |  |  | Low
7 | 210586901 | 30-03-2024 07:42 | 125.4 | 4H.8041.../2420084 | Trip_Genset_Low_Voltage | Open | Aggaarwal Art & Pattern Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad |  | Not attended, Earlier Dealer (DESS) is being terminated so there is a Men power issue. |  |  | Not attended | Low
8 | 210586489 | 29-03-2024 18:14 | 82.5 | 5H.8901.../2320034 | Oil lekage issue Call By Customer Name :Suhas Number :8225052174 | Task Start | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 74 | DEF percentage not showing , reprogrammed the GCU issue resolved. |  |  |  | Low
9 | 210586483 | 29-03-2024 18:11 | 160 | 6H.8475.../2420020 | Starting Issue Call By Customer Name:Kumar No:9318463928 | Task Start | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad | 18.19 | Charging Alternator Shaft & V-belt damaged, SD team replaced Alternator & V-belt issue resolved |  |  |  | High
10 | 210584787 | 29-03-2024 15:31 | 125.4 | 4H.8041.../2420074 | Automation issue Call By Customer Name :Lalit Number :9034113888 | Task Start | Sanjeevan Hospital | Vidyut Engineers - New Delhi | 2.5 | Customer complained about the automation issue, and the engineer visited the site and checked DG in manual mode and found OK.but customer was not allowed to check DG on load. |  |  |  | Low
11 | 210584542 | 29-03-2024 14:26 | 160 | 6H.8475.../2320029 | High Coolant consumption issue And Abnormal sound issue Call By Customer Name :- Rajan No :- 9891915401 | Closed | Areol Formulations Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 42 | Coolant leakage from radiator hose pipe due to loose clamp, tighten the same issue resolved and also top up the coolant. |  |  |  | Moderate
12 | 210584539 | 29-03-2024 14:26 | 320 | F6.8802.../2320054 | PUC Alarm issue and oil leakage issue Call By: Customer Name :-Krishna Gopal Mobile No :- 7388874982 | Task Start | Newtech Vinyl | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 58 | SPN/FMI: 5461/0, code was shown,flashed the latest calibration file issue resolved. |  |  |  | Low