## July 24
S.no | Incident Id | Creation Date | KVA Rating | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Running Hrs | Observation | Incident Status | ASM Name
|  | 2024-01-07 20:33 | 82.5 | 5H.8901.../2320084 | Fuel Sensor Issue Call by Customer Name - Sunny .. Number - 8826805993 | Open | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi | 1177 | Fuel level was varying , checked and found fuel sensor connector was in open condition, connected the same issue resolved. | Closed | Kapil Solanki
2 |  | 2024-01-07 19:05 | 25 | GP3.8702.../2420023 | AMF Panel Complaint Email By KGD Name:-Pradeep Tyagi | Task Start | Braj Machines | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 20 | Customer side auto panel emergency switch was pressed by customer end, corrected and reset the alarm issue resolved. | Closed | Kapil Solanki
3 |  | 2024-01-07 18:11 | 58.5 | T4.8941.../2420654 | LLOP Sender found faulty during testing | Open | The Pentecostal Mission Society | Royal Power Solutions - Zirakpur |  | Visit Pending | open | Ved Gupta
4 |  | 2024-01-07 18:02 | 30 | 3H.8902.../2320063 | Starting Issue Call By Â Customer Name :-Dinesh ... Mobile No :-8700288457 | Open | Style Zone Baby Product Private Limited | Paluck Technologies Ltd. - Ghaziabad | 66 | Battery was dischared, customer side mains wire disconnected, cccconnected the same issue resolved. | Closed | Kapil Solanki
5 |  | 2024-01-07 17:44 | 62.5 | T4.8941.../2420008 | Starting Issue Email By-Service Dealer Name:-Madan Chhimpa | Task Start | MAHENDRA ENGINERING & TRADING COMPANY | Paluck Technologies Ltd. - Gurgaon | 81 | DG was tripping with showing Underspeed alarm, found relay connections was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
6 |  | 2024-01-07 17:39 | 400 | DV8.8542.C4../2420006 | Voltage Issue Call by Customer Name - Satish Kumar Number - 7309949618 | Task Start | Dhanvi Engineering | Paluck Technologies Ltd. - Gurgaon | 12.7 | Engine and alternator, coupling plate bolt broken,(need to replaced) | open | Kapil Solanki
7 |  | 2024-01-07 17:16 | 82.5 | 5H.8901.../2420009 | Red Lamp Alarm issue Call by customer Name:PARMIER . No:-951812 | Task Start | Anand Prayag Undyog | Paluck Technologies Ltd. - Faridabad | 17 | SPN/FMI: 516166/0, clear the DTC and educated the customer about the same. | Closed | Kapil Solanki
8 |  | 2024-01-07 17:02 | 40 | 3H.8951.../2320034 | Starting issue Call By Customer Name :-Ashish Sir Mobile No :- 9818955957 | Task Start | Trikuta Retailers Pvt. Ltd. | Vidyut Engineers - New Delhi | 2.1 | Battery was discharged, due to battery charger was not connected to mains supply,connected the same issue resolved. | Closed | Kapil Solanki
9 |  | 2024-01-07 15:40 | 125.4 | 4H.8041.../2420227 | Low speed alarm issue Call by customer : Name : Pooran Singh No :9009005845 | Task Start | Dynamic Anodizer Aluminium Anodizing | Paluck Technologies Ltd. - Faridabad | 17.24 | SPN/FMI: 651/5 (Injector Cylinder 1 fault open), then checked 1 cylinder Injector wiring found broken, connected the same issue resolved. | Closed | Kapil Solanki | Details to be share to QA
10 |  | 2024-01-07 15:18 | 125.4 | 4H.8041.../2320055 | Starting issue Call By Service Dealer Name :-Mohit Mobile No :-7027820044 | Closed | Pri Oil And Gas Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 130.5 | LoW DEF level, top up and clear the DTC issue resolved. | Closed | Kapil Solanki
11 |  | 2024-01-07 15:18 | 125.4 | 4H.8041.../2420245 | Amber Lamp On Alarm issue Call By Customer Name :- Badal Singh Mobile No :- 7814782649 | Open | Suntex Clothing Ltd. | Industrial Power Solutions - LUDHIANA | 4 | SPN/FMI: 516166/0, clear the DTC. | Closed | Ved Gupta
12 |  | 2024-01-07 15:18 | 82.5 | 5H.8901.../2320042 | Urea Error Code issue Call By Customer Name : 8445820675 No: Kasidh Ahmad | Task Start | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 90 | DEF precentage was not showing in display..then reprogramme the controller but issue not resolved, ( Need to change Controller) | open | Sudhir Awasthi
13 |  | 2024-01-07 14:17 | 30 | 3H.8902.../2420044 | Automation Issue Message By Customer Name : Laykat Rai No :9872400103 | Closed | Mr. Laykat Rai | Industrial Power Solutions - LUDHIANA | 19 | Emergency stop alarm showing on display, checked both emergency switches found ok, reset the alarm issue resolved. | Closed | Ved Gupta
1 |  | 2024-02-07 12:48 | 320 | F6.8802.../2320041 | DG overheating issue Email By - Service Dealer Name -Pratap Diesels Pvt. Ltd., BM | Task Start | Mama Foods | Pratap Diesels Pvt. Ltd. - Alwar | 123 | Air Filter chocked, Clean the same issue resolved. | Closed | Gourav Sharma | Detials required
2 |  | 2024-02-07 12:39 | 30 | 3H.8902.../2320194 | . | Task Start | HS. Enterprises | Suraj Moters Stores - Leh |  | SR open for Cold starting trail pupose only. | Closed | Ved Gupta
3 |  | 2024-02-07 12:32 | 40 | 3H.8951.../2320113 | . | Task Start | HS. Enterprises | Suraj Moters Stores - Leh |  | SR open for Cold starting trail pupose only. | Closed | Ved Gupta
4 |  | 2024-02-07 12:00 |  | 5H.5301.../2300001 | ITV to be Change Issue Email By-Service Dealer Name:-Shiv | Task Start | Manitou Equipment India Pvt. Ltd. | Vidyut Engineers - Noida |  | BS V | Open | Kapil Solanki
5 |  | 2024-02-07 11:26 | 57 | T4.8941.../2320164 | Tripping Issue Call By Customer Name :-Aswini Naveen Mobile No :-9811041909 | Open | KAPP. Enterprises | Vidyut Engineers - New Delhi | 23.49 | Customer side auto panel issue.. Educated the customer about the same. | Closed | Kapil Solanki
6 |  | 2024-02-07 10:32 | 500 | DV8.8501.C4../2320089 | Starting Issue Email By-Service Dealer Name:-Akanksha | Task Start | THEMIS MEDICARE LTD. | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 23 | SPN/FMI: 520528/31, 4426/0, 1761/16 523586/16 ,1761/5, found low DEF level, top up and educated the customer about the same. | Closed | Kapil Solanki
7 |  | 2024-02-07 10:11 | 30 | 3H.8902.../2320134 | Starting Issue Call By Â Customer Name :-Navneet Tanwar Mobile No :-9873191980 | Closed | Pankaj Bhatia. | Vidyut Engineers - Noida | 9.23 | Abnormal sound from loose V belt, tighten the same issue resolved. | Closed | Kapil Solanki
8 |  | 2024-02-07 10:04 | 125.4 | 4H.8041.../2320125 | Starting Issue Call By Â Customer Name :-Dilip ... Mobile No :-9555188828 | Closed | YUG ENTERPRISES | Paluck Technologies Ltd. - Faridabad | 559 | SPN/FMI: 3031/14 , 1761/16, low DEF level and flashed latest file issue resolved. | Closed | Kapil Solanki
9 |  | 2024-02-07 06:58 | 125.4 | 4H.8041.../2420008 | Tripping Issue Call By Customer Name :- Ramesh No :- 9718401519 | Closed | Leighton India Contractors Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1236 | Engineer did not found any issue.. DG running ok. | Closed | Kapil Solanki | KRM check
10 |  | 2024-02-07 15:18 | 57 | T4.8941.../2320180 | White Smoking issue Call By Customer Name :- Manju No :- 9899881555 | Closed | BBRS Hospitality Wellness LLP | Paluck Technologies Ltd. - Faridabad | 72 | Customer compliant about White smoke issue.. But there is no white smoke, DG running ok. | Closed | Kapil Solanki
11 |  | 2024-02-07 14:00 | 320 | F6.8802.../2420018 | Tripping issue Call By Service Dealer Name :-Ramesh Mobile No :-9911266168 | Closed | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad | 106 | DG running on overload and jerk load, analyze the load . | open | Kapil Solanki | KRM check | Check KRM data and found it 108 to 148 kw jark load at the starting time
1 |  | 14-06-2024 15:20 | 156 HP | 4H.8041.../2420292 | ns | Task Start | Genlite Engineering Pvt. Ltd. | G-Care Diesels Private Limited - Ernakulam | 1 | GQA is planning to dismantle and inspect the Engine on site itself with help of Service dealer. Today update - they dismental the engine and EDO placed for P.C nozzle from calicut. May be day after tommorow they are going to receive the EDO | open | Mr Sanjay Mon
2 |  | 2024-01-07 14:11 | 30 | 3H.8902.../2420020 | Starting Issue Email By Service Dealer Name:-K.Ramya, | Closed | Kancherla Surya Prakash Educational Society. | Laxmi Diesels - Rajahmundry | 14.33 | 1. fault - SPN =7026 , FMI = 3 FOR - metering unit - short circuit to battery error , SPN = 157 , FMI = 14 - pressure relief valve - pressure 2. After ECU flashing no faullt code shown in panel but engine stop after cranking , today engg. again visit the site and udated next . Today update - supply to battery charger was not given , also some wiring connection found loose in condition , tightend the same issue resloved. | closed | Mr. saleem
3 |  | 2024-01-07 10:49 | 250 | F6.8841.../2320018 | DIEESL FLOAT FAULTY | Task Start | The Uralungal Labour Contract Co-Operative Society Pvt Ltd No.10957 | Electro Controls - Kottayam | 0 | fault code -- low fuel level shown on panel , there is no fault code found in DTC , today they arrange another fuel float sensor and update next . Today update - Fuel float sensor recieved at dealer end , today they work on it and update next . | open | Mr Sanjay Mon
4 |  | 2024-01-07 | 40 | 3H.8951.../2420168 | CC SR | Closed | P. C. Patel Infra Pvt. Ltd. . | UTS | 1 | ECU ignition wire was loose on distribution block(XDBK4) | Closed | Amit Sandilya | GOEM issue
NORTH ZONE
1 |  | 2024-02-07 19:00 | 58.5 | T4.8941.../2420142 | DG not working in auto mode. | Task Start | BHARTI AIRTEL LIMITED | Vidyut Engineers - Noida | 79.59 | Starting issue… with showing Fail to stop & Communication failure,alarm, then connect the Iknonnect tool but did not found any DTC checked panel connections found ok issue not resolved,Today balram will visit site. | Open | Kapil Solanki
2 |  | 2024-02-07 18:45 | 57 | T4.8941.../2420072 | Power Supplay Issue Call By Customer Name :-Dr.Isha ... Mobile No :-8178862019 | Task Start | Kailash Nursing Home | OVN Industries Private Limited - New Delhi | 2.29 | Battery was discharged due to battery charger not connected to mains supply, connected the same issue resolved. | Closed | Kapil Solanki | CC SR check
3 |  | 2024-02-07 17:52 | 125.4 | 4H.8041.../2420084 | Triping Issue And lamp Alarm Issue Call By Customer Name :-Dipak Mobile No :-6396765044 | Task Start | AGGARWAL ART & PATTERN PVT. LTD. | Paluck Technologies Ltd. - Ghaziabad | 94 | Low DEF level, top up the DEF and educated the customer about the same. | Closed | Kapil Solanki
4 |  | 2024-02-07 16:22 | 750 | DV2.8501.C4../2320023 | ECU Protect Alarm Massage By Customer Name : Abhishek Kumar No: 7903795913 | Task Start | HIND TERMINALS PVT LTD | Paluck Technologies Ltd. - Faridabad | 233 | Starting issue..with showing , fail to start alarm, thecn checked panel connections found ok, then checked Interface box fuses then clean and refitted the same issue resolved. | Closed | Kapil Solanki | KRM check
5 |  | 2024-02-07 16:13 | 125.4 | 4H.8041.../2320099 | Starting Issue Call By Customer Name: Chandradev Number:9643819750 | Task Start | Sudh Investments Private Limited | Vidyut Engineers - Noida | 21 | Starting issue.. E- Feed pump not installed. ( It is in Revalidation Flag) | Open | Kapil Solanki
6 |  | 2024-02-07 14:37 | 82.5 | 5H.8901.../2420015 | No Active DTC Alarm issue And Preventive Maintenance Call By Customer Name :- Rahul Kumar Mobile No :-Rahul Kumar | Closed | Rahul Kumar | M/s OM Diesels Pvt. Ltd. - Sonipat | 54.53 | Maintenance due alarm showing on Display.. Reset the alarm issue resolved. | Closed | Kapil Solanki
7 |  | 2024-02-07 13:07 | 20 | GP3.8601.../2420081 | Tripping issue Call by OEM Name:- Aman No:- 7087762059 | Task Start | A. K. Food | Industrial Power Solutions - LUDHIANA | 9 | Customer Complaint about tripping issue.. But engineer checked DG on load, but did not found any abnormality.. DG running ok. | Closed | Ved Gupta | KRM check | Check the KRM but does not found the problem and one time trip because genset does not acihve proper speed with low voltage & 2 kw load .
8 |  | 2024-02-07 12:19 | 20 | GP3.8601.../2420016 | Radiator damage | Task Start | Shri Vaidic Swasti Pantha Nyas | Rajdhani Diesels and Electricals - Jodhpur | 15.18 | Coolant leakage from damage radiator, replaced by Jakson team. | Closed | Kapil Solanki
1 |  | 2024-03-07 12:15 | 750 | DV2.8501.C4../2320026 | Starting Issue Message By Customer Name : Abhishek Kumar No :7903795913 | Task Start | HIND TERMINALS PVT LTD | Paluck Technologies Ltd. - Faridabad | 206 | SPN/FMI: 1244/3(Positive governor deviation and setpoint of the fuel volume flow through the metering unit fuel rail/system pressure- Too Low Bak 2), (633/3 related to rail pressure) , then checked Fuel line , further checked lifting pump was not oprating checked the supply for lifting pump found 26 V (need to replaced) EDO placed. | Open | Kapil Solanki | Faile part required
2 |  | 2024-03-07 12:03 | 15 | GP3.8501.../2420015 | Diseal Filter Leakage issue Call By Customer Name : Manish Gupta No: 9996640702 | Task Start | Manish Gupta | Vishal Power Systems - Karnal | 30 | Fuel leakage from fuel filter ,(O Ring Damaged ) change the filter issue resolved. | Closed | Kapil Solanki
3 |  | 2024-03-07 11:12 | 320 | F6.8802.../2420006 | Starting Issue Call By Â Customer Name :-Vindesh Mobile No :-9958999689 | Task Start | Apeiron Energy & Engineering Pvt. Ltd. | Vidyut Engineers - New Delhi | 157 | Rain Water entry in canopy , rain gaurd not fitted, fitted the same and clean the water . ( there is no starting issue) | Open | Kapil Solanki
4 |  | 2024-03-07 10:55 | 250 | F6.8841.../2320016 | Trip_Genset_Low_Voltage | Task Start | Indogulf Crop Sciences Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 284.4 | KRM generated SR, tripping issue with showing Under volatge and under frequency alarm, found Overload on DG, now balanced the load, and DG running ok. | Closed | Kapil Solanki
5 |  | 2024-03-07 10:13 | 20 | GP3.8601.../2320045 | Maintenance Due Alarm Message By Customer Name : Anjan Das No : 8527230750 | Closed | Anjan Kumar Das | Vidyut Engineers - Noida | 118.29 | Maintenance due alarm showing on Display.. Reset the alarm issue resolved. | Closed | Kapil Solanki
6 |  | 2024-03-07 09:57 | 40 | 3H.8951.../2420103 | ABNORMAL SOUND ISSUE | Task Start | Rajesh Kharbanda Jal. | Dynamic Engineering Services - Jalandhar | 8 | Line Rejection SR, Customer Complaint about Abnormal sound , but engineer checked DG did not found any issue.. Checked noise with DB meter found ok as per koel norms.educated the customer about the same. | Closed | Ved Gupta
7 |  | 2024-03-07 09:55 | 15 | GP3.8501.../2420029 | Under Speed Alarm Issue Call By Customer Name :-Sawan ... Mobile No :-8708826124 | Task Start | Paras Public School Karnal | Vishal Power Systems - Karnal | 8 | DG was tripping with showing Under speed alarm, checked fuel line found main fuel line bolt are loose, tighten the same and also tighten the XDBK connections found ok. | Closed | Kapil Solanki | CC check
8 |  | 2024-03-07 08:58 | 320 | F6.8802.../2320013 | Error Code Issue Call By Customer Name :-Roshanlal Mobile No :-9672175373 | Open | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar | 315 | SPN/FMI: ( 1761/16,), (110/0 ) ,(5419/1 throttle valave - open load erroe for h- bridge of throttle valve), clear the DTC and also found Air filter chocked, clean and refitted the same issue resolved. | Closed | Gourav Sharma
9 |  | 2024-03-07 15:42 | 250 | F6.8841.../2420011 | Canopy Water Leakage issue Call By Customer Name :-Mohan lal Yadav Mobile No :-9717616023 | Task Start | The National Media Centre Cooperative House Building Society Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 12.1 | Rain Water entry in canopy (door side) | Closed | Kapil Solanki
10 |  | 2024-03-07 15:42 | 250 | F6.8841.../2420010 | Canopy Water Leakage issue Call By Customer Name :-Mohan lal Yadav Mobile No :-9717616023 | Task Start | The National Media Centre Cooperative House Building Society Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 12.1 | Rain Water entry in canopy (door side) | Closed | Kapil Solanki
11 |  | 2024-03-07 14:16 | 200 | 6H.8435.../2420017 | Starting Issue Email By-Service Dealer Name:-Niteesh Dhiman | Task Start | ALC BUILDERS AND PROMOTERS | United Gentech Solutions & Services - Mohali |  | DC alternator mounting bolt broken & I bolt broken , replaced the same issue resolved. | Closed | Ved Gupta
1 |  | 14-06-2024 15:20 | 0 | 4H.8041.../2420292 | ns | Task Start | Genlite Engineering Pvt. Ltd. | G-Care Diesels Private Limited - Ernakulam | 1 | 1.GQA is planning to dismantle and inspect the Engine on site itself with help of Service dealer. 2.they dismental the engine and EDO placed for P.C nozzle from calicut may be day after tommorow they are going to recieve. Today update - today may be they recieved the material | open | Mr Sanjay Mon
2 |  | 2024-03-07 09:18 | 40 | 3H.8951.../2320055 | Starting Issue Email By - Service Dealer Name -G-Care Diesels Pvt. Ltd., CRM | Closed | ICAR-INDIAN INSTIUTE OF SPICES RESEARCH | G-Care Diesels Private Limited - Calicut | 35 | Update pending at ASE end. | closed | Mr Sanjay Mon
3 |  | 2024-01-07 10:49 | 250 | F6.8841.../2320018 | DIEESL FLOAT FAULTY | Task Start | The Uralungal Labour Contract Co-Operative Society Pvt Ltd No.10957 | Electro Controls - Kottayam |  | fault code -- low fuel level shown on panel , there is no fault code found in DTC , today they arrange another fuel float sensor and update next . 2. Today update - after changing the fuel float sensor , same alaram came , so today ASE visit the site and give next update soon. | open | Mr Sanjay Mon | Checked as per given points found ok. Suspected controller problem.
1 |  | 2024-03-07 15:13 | 25 | GP3.8702.../2420048 | Emergency Stopped Alarm issue Call By Customer Name :- Keshav Tiyagi Mobile No :- 9654019499 | Task Start | Jitender Kumar | Paluck Technologies Ltd. - Gurgaon | 137 | Emergency stop alarm showing on display..checked both emergency switches found canopy emergency switch connections are minor loose, tighten the same and reset the alarm issue resolved. | Closed | Kapil Solanki | Couple cut-off to be share
2 |  | 2024-03-07 14:34 | 15 | GP3.8501.../2420044 | Maintenance due issue Call By Customer Name :-JM No :- 9212155999 | Task Start | SWAMI ELECTRICALS | Paluck Technologies Ltd. - Faridabad | 55 | Maintenance alarm showing on display, reset the alarm and also Unbalance load on DG , educated the customer about the same. | Closed | Kapil Solanki | KRM check and a check | Customer use to load R-11,Y-5,B-9.
3 |  | 2024-03-07 14:17 | 500 | DV8.8501.C4../2320010 | Auto Stopping Issue Call By Customer Name :-Tajes Patel Mobile No :-7984098726 | Completed | EA TEC ENGINEERING SOLUTION | Espiem Engines & Machines (P) Limited - KANPUR | 9 | DG was taking stop command in auto mode, (VMR faulty ) suggested to customer to check auto panel. | Closed | Sudhir Awasthi
4 |  | 2024-03-07 13:56 | 82.5 | 5H.8901.../2420015 | Starting Issue Call By Â Customer Name :-Rahul Kumar Mobile No :-9958806012 | Task Start | Rahul Kumar | M/s OM Diesels Pvt. Ltd. - Sonipat | 55.59 | Starting issue..found main fuel line ( tank to filter ) bolt are loose, tighten the same issue resolved. | Closed | Kapil Solanki | A check
5 |  | 2024-03-07 13:29 | 160 | 6H.8475.../2420025 | Amber lamp Alarm Issue Call By Customer Name :-Mustak Mobile No :-9058614379 | Task Start | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 692 | SPN/FMI: 516166/0, clear the DTC and educated the customer about the same. | Closed | Kapil Solanki
6 |  | 2024-03-07 19:44 | 125.4 | 4H.8041.../2320024 | Air Lock issue Call By Customer Name:- Manish Tyagi Number:- 9643313743 | Open | KW. Security & Services Pvt. Ltd. | Vidyut Engineers - Noida | 302.1 | Starting issue.. With showing Under speed alarm, found E- feed pump (1 C) connection was in damaged condition, repaired the same issue resolved. | Closed | kapil Solanki
7 |  | 2024-03-07 16:36 | 62.5 | T4.8941.../2420267 | Dislay Issue and Starting Issue Call By Customer Name :-Culkit ... Mobile No :-9871888983 | Completed | NAYASONO INTERNATIONAL ENGINEERS | Paluck Technologies Ltd. - Gurgaon | 1.26 | Starting issue.. Battery was discharged, battery charger not connected to mains supply.. Connected the same issue resolved. | Closed | kapil Solanki | CC check | CC commissioning completed on 3/6/2024. dealer does not maintan any type of problem.
8 |  | 2024-03-07 16:23 | 40 | 3H.8951.../2420084 | B phase overload alarm and automatic shutdown Issue Message By Customer Name :Parveen . No :9729345900 | Task Start | Vishkarma Engineering Works. | M/s OM Diesels Pvt. Ltd. - Sonipat | 4.2 | Unbalance load on DG ( R/Y/B- 35/21/14) Amp, educated the customer for balance the load. | Closed | kapil Solanki | KRM check | Customer use to unblance load on R .some customer use load R-61,Y-45,B-19 A
1 |  | 2024-04-07 14:45 | 40 | 3H.8951.../2420041 | Starting Issue Call By Â Customer Name :-Ashali Varma Mobile No :-9818386619 | Open | Ashali Varma | Vidyut Engineers - New Delhi | 4 | Automation issue.. ( Controller was in manual mode) , educated the customer about the same. | Closed | Kapil Solanki
2 |  | 2024-04-07 13:51 | 125.4 | 4H.8041.../2320125 | Starting Issue Call By Â Customer Name :-Dilip ... Mobile No :-9555188828 | Task Start | YUG ENTERPRISES | Paluck Technologies Ltd. - Faridabad |  | SR Open for only Servicing purpose. | Cancelled | Kapil Solanki
3 |  | 2024-04-07 13:51 | 30 | 3H.8902.../2320103 | Error Code Issue Call By Customer Name :-Vikas ... Mobile No :-9871111419... | Task Start | Nav Durga Enterprises | Paluck Technologies Ltd. - Faridabad | 85 | Fuel Sensor issue.. Fuel percentage was not showing proper, then removed sensor and refitted the same issue resolved. | Closed | Kapil Solanki | Float stuck KRM check | Fuel level sensor stuck with 100 % and show 100 percent fuel on KRM
4 |  | 2024-04-07 13:47 | 250 | F6.8841.../2320006 | Starting Issue Email By-Customer Name:-Praveen Garg | Task Start | Katyayani Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi | 62 | SPN/ FMI : 168/3 ( Actutor relay - short circuit to battery error,) ,( 516166/0) showing in display..and also charging alternator failure alarm showing on display..then checked charging alternator voltage found (3.3 V), then removed charging alternator connector and clean it,then refitted the same issue resolved. and also 3031/14, flashed latest cal file . | Closed | Gourav Sharma
5 |  | 2024-04-07 12:52 | 30 | 3H.8902.../2320175 | Smoke Issue Call By Customer Name: Neelakash ... Number: 9810015024 | Open | Rajender Nagar Nursing Home | Paluck Technologies Ltd. - Ghaziabad |  | Customer complaint about , smoke issue.. but engineer checked DG on load 1 hour but no abnormalitiy was found. DG ruuning ok. | Closed | Kapil Solanki
6 |  | 2024-04-07 12:41 | 125.4 | 4H.8041.../2320181 | Tripping Â Issue Call By Customer Name :-Anil Kumar Mobile No :-9582904448 | Task Start | HI TECH AGRO ENERGY PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 209 | SPN/FMI: 5461/0 in DM 1 and (1761/16), (51/0 throttle valve jammed fault ) in DM 2, flashed the latest file and Clear the DTC issue resolved. | Closed | Kapil Solanki
7 |  | 2024-04-07 12:17 | 125.4 | 4H.8041.../2320062 | Starting Issue Call By Customer Name :-Suraj Pandey Mobile No :-9311203497 | Task Start | Shiv Industries | M/s OM Diesels Pvt. Ltd. - Sonipat |  | SPN/FMI: 1761/16, 516166/0, 110/0, top up DEF and clear the DTC issue resolved. | Closed | kapil Solanki
8 |  | 2024-04-07 11:29 | 62.5 | T4.8941.../2320002 | Tripping Issue Call By Dealer Name :- Deepak Kumar Mobile No:-7027820048 | Task Start | Mittal Maternity and Nursing Home | M/s OM Diesels Pvt. Ltd. - Rohtak | 24 | MCCB was in off condition, corrected the same issue resolved. | closed | Kapil Solanki
9 |  | 2024-04-07 09:56 | 62.5 | T4.8941.../2320076 | INSTANCE ID:-100707064 SITE ID:- CALL BY CUSTOMER// DG ISSUE:-DG ISSUE NAME:-AJAY SHARMA NUMBER:-8851779755 | Open | Tata Tele services | Paluck Technologies Ltd. - Ghaziabad | 171 | Abnormal sound from loose V belt, found DC alternator mounting bracket bolt broken, and I bolt broken,belt loose, changed the I bolt , issue and tighten the belt issue resolved. | Closed | Kapil Solanki
10 |  | 2024-04-07 09:52 | 15 | GP3.8501.../2320033 | Automation Issue Call By Customer Name :-Neeraj .. Mobile No :-7303802988 | Closed | Solve Consulting & Business Services Pvt. Ltd. | Vidyut Engineers - New Delhi | 25 | Customer complaint about DG was not starting in auto mode, but engineer checked DG manually and as well as auto mode, found ok. | Closed | Kapil Solanki
11 |  | 2024-04-07 09:50 | 20 | GP3.8601.../2420068 | Power supply issue & Automation issue Call By Customer Name : Sandip .. No:- 9718887676 | Closed | Charanjeet. | Vidyut Engineers - Noida | 21.45 | Customer side auto panel issue..( sensing missing), DG running on mannual mode ok. | Closed | Kapil Solanki
12 |  | 2024-04-07 09:36 | 125.4 | 4H.8041.../2420109 | ENGINE NOT TAKING LOAD | Task Start | Crescent Techno Solution S. Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 9 | Line Rejection SR, Hunting issue. RPM Variation from. (1460 to 1510), due to load variation (20 t0 55 KW) | Open | Kapil Solanki
13 |  | 2024-04-07 09:34 | 25 | GP3.8702.../2420024 | Voltage Fluctuation Issue Call By Customer Name :-PRAVEEN DHINGRA Mobile No :-9254202829 | Task Start | Panipat Impex India | Vishal Power Systems - PANIPAT | 69 | Unbalanced load on DG, educated the customer about the same. | Closed | Kapil Solanki
1 |  | 14-06-2024 15:20 | 0 | 4H.8041.../2420292 | ns | Task Start | Genlite Engineering Pvt. Ltd. | G-Care Diesels Private Limited - Ernakulam | 1 | EDO pending . | open | Mr Sanjay Mon
2 |  | 2024-04-07 10:25 | 0 | 5H.5353.../2300001 | KOEL JOINT VISIT | Task Start | SCHWING STETTER (INDIA) PVT LTD | Electro Controls - Coimbatore | 184.55 | Visit done | closed | Mr Sanjay Mon
3 |  | 2024-03-07 09:18 | 40 | 3H.8951.../2320055 | Starting Issue Email By - Service Dealer Name -G-Care Diesels Pvt. Ltd., CRM | Closed | ICAR-INDIAN INSTIUTE OF SPICES RESEARCH | G-Care Diesels Private Limited - Calicut | 35 | There is issue with flywheel ring , they replace the same and problem resloved , but didn't find the actual reason So ASE suggest to customer to check AMF contactor because they found some loose wiring in contactor . | closed | Mr Sanjay Mon
4 |  | 2024-01-07 15:16 | 40 | 3H.8951.../2420094 | ENGINE NOT STARTING | Open | JRT Constructions | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | checked the all wiring connections , give the mains sensoning to GCU , did programming to GCU , engine running condition found ok , they take engine under observation for 3 days . | open | Mr Md saleem
5 |  | 2024-01-07 10:49 | 250 | F6.8841.../2320018 | DIEESL FLOAT FAULTY | Task Start | The Uralungal Labour Contract Co-Operative Society Pvt Ltd No.10957 | Electro Controls - Kottayam |  | checked the continuity of harness (Found OK), also discussed with HO , Now they check after changing the panel . Today update -May be there is issue found in control panel , today they change the panel and check . | open | Mr Sanjay Mon
1 | 210930459 | 2024-04-07 13:15 | 20 | GP3.8604.../2420144 | DG not running auto mode | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Patna | 265 | Alarm-Fuel filter warning dirty fuel , choke filter and fuel line. clean the fuel tank & change the fuelfilter at first PM. | closed | prabhakar kumar
2 | 210930457 | 2024-04-07 13:12 | 20 | GP3.8604.../2420141 | DG not running auto mode | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Patna | 170 | voltage drop upto 190V set the AVR hence the problem resolve | closed | prabhakar kumar
1 | 210932945 | 2024-04-07 19:51 | 250 | F6.8841.../2320023 | Stopping Issue Call by Customer Name - Shamsher .. Number - 9468430690 | Open | Haryana Police Housing Corporation Panchkula | Vishal Power Systems - Karnal | 14 | SPN/FMI: (1761/16 Low DEF level), and (3031/14), top up DEF and flashed the latest cal file issue resolved. | Closed | Kapil Solanki
2 | 210932944 | 2024-04-07 19:50 | 125.4 | 4H.8041.../2420096 | Under Voltage issue Call BY Customer Name :- Ashitosh No :- 9058339810 | Open | Macro Plast Private Ltd | Vidyut Engineers - Noida | 45.55 | Starting issue.. R - phase under voltage alarm showing on display..checked panel connections found R phase fuse was in burnt condition, replaced the same and also Low DEF level , clear the DTC issue resolved. | Closed | Kapil Solanki
3 | 210932668 | 2024-04-07 17:50 | 250 | F6.8841.../2420021 | Starting Issue Email By Service Dealer Name:-Sonu Rai | Task Start | ZOOTO FASHION PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 77 | ECU protect lamp alarm showing on display… checked DTC but does not found, then tighten the panel connections isssue resolved. | Closed | Kapil Solanki
4 | 210931545 | 2024-04-07 17:04 | 15 | GP3.8501.../2420084 | Low Speed Alarm Issue Call By Customer Name :-Sandhu Mobile No :- 9896910009 | Completed | G. S. Sandhu. | United Gentech Solutions & Services - Mohali | 23 | Maintenance alarm showing on display..clear the DTC. And checked DG on load found ok. | Closed | Ved Gupta
5 | 210931266 | 2024-04-07 16:29 | 125.4 | 4H.8041.../2420114 | Automation issue Call By Â Customer Name :-Nitin Mobile No :-9205341140 | Task Start | Romana Herbalcare Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 32 | Automation issue.. Customer side panel issue..(No issue in DG) | Closed | Kapil Solanki
6 | 210930982 | 2024-04-07 15:32 | 320 | F6.8802.../2420018 | Trip_Genset_Low_Voltage | Open | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad |  | KRM generated SR, As previously discussed, DG running on jerk load and educated the customer about the Same. | Cancelled | Kapil Solanki | krm CHECK
7 | 210930891 | 2024-04-07 15:13 | 320 | F6.8802.../2320061 | Starting issue Call By Customer Name : Laxminarayan .. No:- 8860089233 | Task Start | Rai Indutrial Power Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 35 | DG was not started in first crank in morning , Checked fuel line found ok.(Kept in Under observation) | open | Kapil Solanki
8 | 210930259 | 2024-04-07 12:41 | 57 | T4.8941.../2320283 | Loading Issue Call By Customer Name: Vivek . Number: 9760627950 | Task Start | AROON AVIATION SERVICES PVT LTD | Vidyut Engineers - New Delhi | 21 | Starting issue..checked fuel line found ok, then checked panel connections found XDBK connections was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
9 | 210929987 | 2024-04-07 11:50 | 500 | DV8.8501.C4../2420039 | Coolant Leakage Issue Email By Service Dealer Name:-Brahmadeo Kumar | Task Start | Gera Ventures | OVN Industries Private Limited - New Delhi | 4 | Coolant leakage from thermostate housing to radiator (DM supply connector) EDO placed. | open | Kapil Solanki | Failed part
1 | 210935338 | 2024-05-07 14:37 | 20 | GP3.8601.../2420019 | Starting Issue Email By - Customer Name - Sahil Gupta | Open | SAHIL POWER SYSTEMS | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Starting issue..fuse faulty.. resolved on call. Customer side pane lissue | Cancelled | Gourav Sharma
2 | 210935235 | 2024-05-07 14:01 | 125.4 | 4H.8041.../2320081 | ECU Malfunc Email By Service Dealer Name:-Pooja Ghode | Task Start | Crown Industry | Pratap Diesels Pvt. Ltd. - Bhiwadi | 140 | Air Filter chocked and Unbalance load on DG , clean the filter and educated customer for balance load. | Closed | Gourav Sharma | DG application check | Industry_Manufacturing
3 | 210934684 | 2024-05-07 12:54 | 57 | T4.8941.../2420049 | Starting Issue Call By Customer Name : Deepak Kumar No :9557673903 | Task Start | Jindalsons Infratex Pvt. Ltd. | Vidyut Engineers - Noida | 18.36 | Emergency stop switch was pressed by Customer end, corrected the same and educated customer about the same . | Closed | Kapil Solanki
4 | 210934678 | 2024-05-07 12:54 | 30 | 3H.8902.../2320064 | Voltage issue Call by customer Name:-Anil. No:-9310619933 | Task Start | Balwan Service Station | OVN Industries Private Limited - New Delhi | 6.15 | Customer side auto panel issue..( No issue in DG) | Closed | Kapil Solanki
5 | 210934390 | 2024-05-07 12:02 | 30 | 3H.8902.../2320045 | Starting issue Call By Customer Name : PUNIT SINGH No:-9643768190 | Task Start | Born Max Gyane Clinic B. M. C. | Paluck Technologies Ltd. - Ghaziabad | 3 | Battery was discharged, due to battery charger output connection disconnected from charger, connected the same issue resolved. | Closed | Kapil Solanki | CC check | does not matian any type of problem
6 | 210934260 | 2024-05-07 11:36 | 40 | 3H.8951.../2420008 | Black Smoke Email By - Service Dealer Name -Vikas Saini | Task Start | R S UDHYOG | M/s OM Diesels Pvt. Ltd. - Rohtak | 20 | Servicing done | Closed | Kapil Solanki
7 | 210934071 | 2024-05-07 10:58 | 750 | DV2.8501.C4../2420006 | ECU Amber Alarm Message by customer Name: Sandeep Srivastava No :9953613456 | Closed | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida | 1044 | As per customer voice no issue in DG | Closed | Kapil Solanki
8 | 210933987 | 2024-05-07 10:44 | 40 | 3H.8951.../2420142 | Mobiel oil Gauge issue Call By OEM Name :-Aman Mobile No :-7087762059 | Open | Rama Krishna Paints & Hardware | Industrial Power Solutions - LUDHIANA |  | Dipstick missing | open | Ved Gupta
9 | 210933953 | 2024-05-07 10:28 | 400 | DV8.8542.C4../2420014 | Tripping issue Call By Â Customer Name :-Tara Chand Mobile No :-9728993286 | Task Start | Powercam Electricals Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 51 | Customer using Solar panel and capacitor bank, bypaas the both ,then does not appear any alarm. DG running ok. | Closed | Kapil Solanki | KRM check | Check the KRM data but does not show any type of problem.
10 | 210933942 | 2024-05-07 10:21 | 125.4 | 4H.8041.../2320099 | Feed pump to be Change Email By-Service Dealer Name:-Shiv | Closed | Sudh Investments Private Limited | Vidyut Engineers - Noida | 26.9 | Electric feed pump not installed the site, fitted E-feed pump. | Closed | Kapil Solanki | Campaign SR check
11 | 210933420 | 2024-05-07 09:30 | 125.4 | 4H.8041.../2320054 | Vibration Issue & Silencer Issue Call By Customer Name :-Rajesh Ram Mobile No :-9953102701 | Task Start | THERMADYNE PVT. LTD. | Paluck Technologies Ltd. - Faridabad | 212 | Canopy door is damage condition, due to door is touching from the silencer, (SR open on GOEM portel) | Closed | Kapil Solanki
12 | 210933350 | 2024-05-07 07:51 | 160 | 6H.8475.../2320027 | Amber lamp Alarm Call By Customer Name :-Amar Mobile No :-9560932926 | Closed | PK. Chavala | Vidyut Engineers - New Delhi | 8.54 | Low DEF level, top up and educated the customer about the same. | Closed | Kapil Solanki
13 | 210936966 | 2024-05-07 19:06 | 125.4 | 4H.8041.../2420125 | Tripping Issue Call By Customer Name :-Rahul ... Number :-9458036424 | Task Start | ATTIC PRODUCTS PRIVATE LIMITED | Vidyut Engineers - Noida | 53.4 | Customer complaint about tripping issue.. But engineer did not found any issue.. | Closed | Kapil Solanki | KRM check | Send mail for revisit.
14 | 210936381 | 2024-05-07 17:24 | 125.4 | 4H.8041.../2420070 | dg not start Email By - Service Dealer Name -Pratap Diesels Pvt. Ltd. SM | Task Start | Rivah Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi | 95 | DG running on jerk load (80 KW), educated the customer for step loading. | Closed | Gourav Sharma
15 | 210936338 | 2024-05-07 17:18 | 30 | 3H.8902.../2320159 | Automation Issue Call by Customer Name - Ankur Kaushik Number - 9958177838 | Closed | Ankur Kaushik | Paluck Technologies Ltd. - Faridabad | 98 | Automation issue.. ( DG was in manual mode) , educated the customer about the same. | Closed | Kapil Solanki
16 | 210936335 | 2024-05-07 17:18 | 30 | 3H.8902.../2320134 | Stop Field Alarm Issue And Starting Issue Call By Customer Name :-Omveer Singh Mobile No :-9971802190 | Closed | Pankaj Bhatia. | Vidyut Engineers - Noida | 10.57 | DG was tripping with showing Communication failure and fail to stop alarm, then checked Can communication and found 14 no wire was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
17 | 210935671 | 2024-05-07 15:51 | 200 | 6H.8435.../2320012 | Starting Issue Email By Service Dealer Name:-Shiv | Closed | NIEVA HOMES PVT. LTD. | Vidyut Engineers - Noida | 167 | Alternator mounting brakect bolt and I bolt broken, and V belt broken ,changed the same issue resolved. | Closed | kapil Solanki
18 | 210935502 | 2024-05-07 15:21 | 40 | 3H.8951.../2320109 | Starting Issue Call By Customer Name :-Aakash Mobile No :-7780889122 | Task Start | Jammu Kashmir Cricket Association | Suraj Motor Store - Jammu | 5 | SPN/FMI: 97/5 (water in fuel sensor) checked sensor found ok , clear the DTC . | open | Ved Gupta | Rearrange visit
1 | 210937533 | 2024-06-07 09:57 | 125.4 | 4H.8041.../2420229 | Battery Issue Call By Customer Name :-Pradip Mobile No :-9319619030 | Closed | A. K. Engineering Industries | Paluck Technologies Ltd. - Faridabad | 102 | Battery was discharged due battery charger mains supply switch was malfunctioning, educated the customer about the same. | Closed | Kapil Solanki
2 | 210938568 | 2024-06-07 11:55 | 15 | GP3.8501.../2420063 | Alarm Issue Email By-Service Dealer Name:-Bharat dixit | Task Start | Cricket Connect | R K Engineers - Meerut | 36 | Sometimes DG was not starting in first attempt, and showing Under speed alarm, checked loose connections found ok, then flahed ECU ( kept in Underobservation for two days) | open | Sudhir Awasthi
3 | 210938985 | 2024-06-07 13:45 |  | 3H.8902.../2420423 | lop issue | Task Start | Industrial Equipments Company | Royal Power Solutions - Zirakpur | 0.1 | Line Rejection SR, LLOP sensor faulty, changed the sensor issue resolved. | Closed | Ved Gupta
4 | 210939418 | 2024-06-07 15:34 | 320 | F6.8802.../2320033 | Over Loading issue Call By Customer Name : Raju .. .. No:- 8130832696 | Completed | NIIT LEARNING SYSTEMS LIMITED | Paluck Technologies Ltd. - Gurgaon | 41 | DG was running on jerk load, educated the customer about the same . | Closed | Kapil Solanki
5 | 210939446 | 2024-06-07 15:42 | 160 | 6H.8475.../2320025 | Starting Issue Call By Customer Name :-Dharmesh ... Mobile No :-9873301320 | Task Start | STRIKER INDUSTRIES PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 42 | SPN/FMI: 1761/16, Low DEF level, top up and educated the customer about the same issue resolved. | Closed | Kapil Solanki
6 | 210939588 | 2024-06-07 16:15 | 125.4 | 4H.8041.../2420100 | Starting Issue And Preventive Maintenance Call By Â Customer Name :-Manoj Kumar Mobile No :-9251982037 | Task Start | Zeniya Electech Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 43 | Low DEF level @ 6% , top up and educated the customer about the same. | Closed | Kapil Solanki
7 | 210939694 | 2024-06-07 16:36 | 15 | GP3.8501.../2320033 | Abnormal Sound Â Issue Call By Customer Name :-Niraj Kumar Mobile No :-9899264577 | Closed | Solve Consulting & Business Services Pvt. Ltd. | Vidyut Engineers - New Delhi | 32 | Auto panel issue.. (contractor not holding ) found panel connection mains sensing wire loose, tighten the same issue resolved. | Closed | Kapil Solanki | Detail required
8 | 210939721 | 2024-06-07 16:44 | 320 | F6.8802.../2320030 | Trip_Genset_Low_Voltage | Task Start | Atma Autotech Engineers Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 119 | KRM generated SR, Jerk load on DG , educated the customer applied load gradually. | Closed | Kapil Solanki | KRM check | Check the KRM data but found out the genset low voltage alarm and low speed so this genset genrate low volatge SR.
1 | 210939960 | 2024-06-07 17:25 | 20 | GP3.8601.../2420110 | Starting Issue Email By-Service Dealer Name:-B.kalyani | Task Start | M/s. Guruvayur Sri Krishna Mandiram Trust | Powerlinks Infra Tech Pvt Ltd - Uppal | 1 | Today engg. visit to site | open | Mr Md saleem
2 | 210939712 | 2024-06-07 16:45 | 125.4 | 4H.8041.../2420260 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai |  | Today engg. visit to site | open | Mr. Nanda Gopal
3 | 210937537 | 2024-06-07 09:52 | 0 | GP3.8702.../2420078 | DG Not starting | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai |  | Today engg. visit to site | open | Mr. Nanda Gopal
4 | 210935233 | 2024-05-07 14:11 | 30 | 3H.8902.../2420024 | Starting Problem Call by :Dealer Name : Seenu Contact :9704396968 | Closed | Anshikkha Industries | Laxmi Diesels - Srikakulam |  | Diesel leakage from suction pipe | closed | Mr. saleem
5 | 210934719 | 2024-05-07 12:59 | 0 | 4H.8041.../2320060 | fip hub replace | Cancelled | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai |  | Pending at ASE end | CANCELLED | Mr. Nanda Gopal | SR for revalidation .
6 | 210930882 | 2024-04-07 15:13 | 500 | DV8.8501.C4../2420052 | Starting Problem Call by : Customer Name :Ganeshan Contact :9344012124 | Closed | Vinayaka Missions Research Foundation | Bharath Diesel Sales and Service - Salem | 62 | Ad-blue low alarm , topup the same , problem reslove | closed | Mr. Nanda Gopal
1 | 210943485 | 2024-08-07 13:09 | 20 | GP3.8604.../ 2420055 | contractor | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif |  | mains contactors burn out , change the same issue resolve. | closed | Prabhakar kumar
2 | 210943385 | 2024-08-07 12:54 | 15 | GP3.8501.../ 2420170 | Automation issue Call By Customer Name:- Dr. Alok Shyandhan Number:- 9835334854 | Open | Alok Shyandan | United Machinery Sales And Service - Dhanbad | na | Visit pending | open | Prabhakar kumar
1 | 210944591 | 2024-08-07 15:29 | 320 | F6.8802.../2320001 | Display Issue Â Call By Customer Name :-Sachin Kumar Mobile No :-7338603759 | Task Start | Suvarna Electricals | Surya Power Services - J C Road, Bangalore |  | tommorow engg. visit to site | open | S.prakash | KRM check
2 | 210942689 | 2024-08-07 11:09 | 82.5 | 5H.8901.../2320019 | starting issue call by customer name :-kadiravan number :-9060089059 | Closed | STOVE KRAFT LIMITED | Surya Power Services - Bangalore | 6.16 | loose wiring at controller end , tightend the same , problem resloved | closed | S.prakash
3 | 210939960 | 2024-06-07 17:25 | 20 | GP3.8601.../2420110 | Starting Issue Email By-Service Dealer Name:-B.kalyani | Task Start | M/s. Guruvayur Sri Krishna Mandiram Trust | Powerlinks Infra Tech Pvt Ltd - Uppal | 1 | customer need to know how to operate the D.G , educate the customer same. | closed | Mr Md saleem
4 | 210939712 | 2024-06-07 16:45 | 125.4 | 4H.8041.../2420260 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 1 | SPN - 3224 , FMI - 2 , ECU alarm FOR nox , loose wiring of Nox sensor , tightend the same problem resloved | closed | Mr. Nanda Gopal
5 | 210937537 | 2024-06-07 09:52 | 0 | GP3.8702.../2420078 | DG Not starting | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 1 | DG not starting due to oil pressure sensor problem, EDO placed for oil pressure sensor | open | Mr. Nanda Gopal
6 | 210934719 | 2024-05-07 12:59 | 0 | 4H.8041.../2320060 | fip hub replace | Cancelled | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai |  | Revalidation | Cancelled | Mr. Nanda Gopal
7 | 210914292 | 2024-01-07 15:16 | 40 | 3H.8951.../2420094 | ENGINE NOT STARTING | Open | JRT Constructions | Powerlinks Infra Tech Pvt Ltd - Madinaguda |  | mains sensoning required for auto start . engg. give the same and problem resolved . | closed | Mr Md saleem | Details required
1 | 210941813 | 2024-07-07 21:20 | 82.5 | 5H.8901.../2320084 | White Smoking Issue and Preventive Maintenance Call by Customer Name - Nandkishor ... Number - 9310826615 | Task Start | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi | 1250 | Customer Complaint about White smoke issue..but there is no such type of issue..only showing Low DEF level top up DEF and educated customer about the same. | Closed | Kapil Solanki
2 | 210941488 | 2024-07-07 15:01 | 400 | DV8.8542.C4../2420007 | Starting Issue Call By Customer Name :-Miraj alimiraj alii Mobile No :-9682193433 | Open | Fetch Construction | Suraj Motor Store - Srinagar |  | SPN/FMI: 516166/0, clear the DTC and educated customer about the same. | Cancelled | Ved Gupta
3 | 210941392 | 2024-07-07 11:51 | 30 | 3H.8902.../2420177 | Dg set showing under speed alarm Email By OEM Name:-Shamim Ahmed | Closed | U. M. A. Bajaj | Pratap Diesels Pvt. Ltd. - Alwar | 29 | SPN/FMI: 97/5 (Water in fuel ) clear the DTC. | Closed | Gourav Sharma | Site visit required
4 | 210941405 | 2024-07-07 11:28 | 57 | T4.8941.../2320140 | Low Speed Â Alarm Issue Call By Customer Name :-Mukesh ... Mobile No :-9911657974 | Open | Gourav Gupta | Vidyut Engineers - New Delhi | 17 | Under speed alarm showing on display..checked fuel line found ok reset the alarm issue resolved. | Closed | Kapil Solanki | KRM check | Check the KRM data but does not show any type of proble only unblance load on B phase and rpm variation 1490 to 1530 .
5 | 210941364 | 2024-07-07 10:00 | 500 | DV8.8501.C4../2420043 | Amber Lamp Alarm & Error Code issue Call By Customer Name :-Rakesh Sharma Mobile No :-9816194371 | Task Start | Nikvin Healthcare India Pvt. Ltd. | SAAN Industrial Solutions - Baddi | 18 | SPN/FMI: 516166/0, clear the DTC and educated customer about the same. | Closed | Kapil Solanki
6 | 210941354 | 2024-07-07 09:24 | 160 | 6H.8475.../2320029 | Oil Leakage Issue Call By Customer Name: Ragan Number:.8700858111 | Task Start | Areol Formulations Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 132 | Oil leakage from core plug,refitted the same issue resolved. | Closed | Kapil Solanki
7 | 210941353 | 2024-07-07 08:51 | 125.4 | 4H.8041.../2420009 | Fuel Sensor Issue Call By Customer Name: Rahul Number:9909018923 | Open | Panipat Elevated Corridor Limited. | Vishal Power Systems - PANIPAT | 112 | Erratic reading showing on display. found.Fuel sensor connector was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
1 | 210943529 | 2024-08-07 13:30 | 320 | F6.8802.../2420024 | DG DISPLAY PROBLEM Email By - Customer Name - Rosa Herbalcare Pvt Ltd Bhiwadi | Open | Rosa Herbal Care India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 39 | Starting issue.. Battery -ve terminal burnt, (Need to replaced) | Open | Gourav Sharma
2 | 210943279 | 2024-08-07 12:30 | 250 | F6.8841.../2320023 | Automation Issue Call by Customer Name - Anurag Bhatia Number - 9915321199 | Task Start | Haryana Police Housing Corporation Panchkula | Vishal Power Systems - Karnal |  | Mains contractor not holding due to mains phase sequence was interchanged.. Corrected the same issue resolved. | Closed | Kapil Solanki
3 | 210943216 | 2024-08-07 12:20 | 57 | T4.8941.../2320118 | Starting Issue Call by Customer Name - Anil Sharma Number - 9314080019 | Task Start | Victor Power Solution | Pratap Diesels Pvt. Ltd. - Bhiwadi | 84 | Starting issue..checked panel connections found 4 no wire was disconnected from connector, connected the same and also water in fuel alarm showing found water in water seprator. | open | Gourav Sharma
4 | 210942968 | 2024-08-07 11:56 | 250 | F6.8841.../2420046 | Tripping issue Call By Customer Name : Pramod No:8595636308 | Task Start | UPPAL CHADHA HI-TECH DEVELOPERS [P] LTD | Paluck Technologies Ltd. - Ghaziabad | 26 | SPN/FMI: 1761/16, LOW DEF LEVEL , top up and educated customer about the same. | Closed | Kapil Solanki
5 | 210942967 | 2024-08-07 11:56 | 160 | 6H.8475.../2320031 | EMERGENCY Shutdown issue Call By Customer Name : Sachin ... No:7827651533 | Task Start | INFRA 13 PVT LTD | Paluck Technologies Ltd. - Ghaziabad | 10 | SPN/FMI : 920/5, checked emergency switches found canopy emergency switch pressed by customer end, corrected the same and clear DTC issue resolved. | Closed | Kapil Solanki
6 | 210942877 | 2024-08-07 11:42 | 30 | 3H.8902.../2420177 | troubleshooting activities Email By - Customer Name - Shamim Ahmed | Task Start | U. M. A. Bajaj | Pratap Diesels Pvt. Ltd. - Alwar | 30 | Erratic running hours showing on KRM , send mail communication to KRM team and also found 15,16 no wire was in loose condition, tighten the same issue resolved. | Closed | Gourav Sharma
7 | 210942798 | 2024-08-07 11:30 | 57 | T4.8941.../2320227 | AMF Panel Issue Call By Customer Name :-anil kumar singh Mobile No :- 9971209995 | Task Start | Komal Co Operative Group Housing Society | Paluck Technologies Ltd. - Faridabad | 146 | AMF Panel issue.. (Mains phase sequence changed, corrected the same issue resolved. | Closed | Kapil Solanki
8 | 210942553 | 2024-08-07 10:52 | 250 | F6.8841.../2420033 | Starting Issue Email By KGD Name:-Manasi Khair. | Task Start | Kids Clinic India Pvt Ltd | S. R Engines Sales And Service - LUCKNOW | 32.43 | Low DEF level, top up and educaed the customer about the same. | Closed | Sudhir Awasthi
9 | 210942338 | 2024-08-07 09:54 | 15 | GP3.8501.../2420029 | Low speed alarm issue Call By Customer Name:- Sawan Number:- 8708826124 | Task Start | Paras Public School Karnal | Vishal Power Systems - Karnal | 9.34 | Customer side mains issue no issue in DG. | Open | Kapil Solanki
10 | 210942286 | 2024-08-07 09:38 | 125.4 | 4H.8041.../2420172 | Starting Issue Call By Â Customer Name :-Ankit .. ... Mobile No :-9350166730 | Closed | Aksh Lights India | Vishal Power Systems - Karnal | 89 | RS-485 (15, 16) wire disconnected from connector, fitted the same issue resolved, and also Low DEF level, and 3031/14, flashed new cal file issue resolved. | Closed | Kapil Solanki
11 | 210942247 | 2024-08-07 09:15 | 320 | F6.8802.../2420021 | Coolant Leakage Issue Call By Customer Name :-Ved Prakash Mobile No :-9717720154 | Task Start | HENNA INDUSTRIES PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 157 | Customer Complaint about Coolant leakage issue…but there is no such type of issue.. DG running OK. | Closed | Kapil Solanki | KRM check | CHECK the KRM found it the proble with spped variation (1495 to 1504 rpm) and engine tempture touch 75 C mainly on 120 kw load.
12 | 210944543 | 2024-08-07 15:12 | 125.4 | 4H.8041.../2420418 | Under Speed Alarm Call By KGD Name :-Pradeep Bhati Mobile No :- 9911316001 | Cancelled | K. R. C. Infra Projects Pvt. Ltd. | R K Engineers - Muzaffarnagar |  | SR open for only Servicing Purpose. | Cancelled | Sudhir Awasthi
13 | 210943917 | 2024-08-07 14:24 | 40 | 3H.8951.../2320060 | Battery issue Call BY Customer Name :- Ram No :- 9953228992 | Closed | KARTIK AUTO CENTRE | OVN Industries Private Limited - New Delhi | 24 | As previously discussed, battery faulty.. Fitted new battery issue resolved. | Closed | Kapil Solanki
14 | 210943866 | 2024-08-07 14:15 | 58.5 | T4.8941.../2420142 | Starting Issue Email By-Service Dealer Name:-Shiv | Closed | BHARTI AIRTEL LIMITED | Vidyut Engineers - Noida | 80.3 | DG was tripping with showing under speed alarm (after safety monitoring periode), checked CAN communication, found resistance 0 ohm, then checked CAN H voltage found 1.9V and CAN L 0V, Changed the ECU can communication found ok, but GCU parameter no showing, after change GCU issue resolved.(All mention in PIR) | Closed | Kapil Solanki | PIR need from field.
15 | 210944961 | 2024-08-07 16:28 | 82.5 | 5H.8901.../2320013 | Automation Issue Call by Customer Name - Anil .. Number - 7807922742 | Closed | GOLDEN MOMENTS RESIDENCY PRIVATE LIMITED | Vidyut Engineers - New Delhi | 25 | Automation issue.. ( Controller was in manual mode) educated customer about the same. | Closed | Kapil Solanki
16 | 210945051 | 2024-08-07 16:50 | 125.4 | 4H.8041.../2420213 | Controller Ala ram Sound issue Call By Customer Name : Umesh ... No:- 9711257735 | Task Start | Sukh Shanti Apartment | Paluck Technologies Ltd. - Gurgaon | 28 | SPN/FMI : 1761/ 16,Low DEF level @ 47% , top up and educated customer about the same. | Closed | Kapil Solanki
17 | 210945016 | 2024-08-07 16:44 | 40 | 3H.8951.../2420141 | Tripping issue Call By Customer Name : Shradha No:- 9958891400 | Task Start | Green Energy Diesel Engines Private Limited. | Paluck Technologies Ltd. - Faridabad | 31 | Customer complaint about tripping issue.. Checked event log found under speed alarm, checked fuel line found ok. | Closed | Kapil Solanki | KRM check. Need to check service history
18 | 210944745 | 2024-08-07 15:51 | 15 | GP3.8501.../2420084 | Low Speed Alarm Call By Customer Name:G. S. Sandhu. . No:9996610001 | Open | G. S. Sandhu. | Royal Power Solutions - Zirakpur |  | SR is in Mohali territory. | Open | Ved Gupta | KRM check | Check the KRM but does not found any type of problem.
1 | 210945696 | 2024-08-07 17:42 | 40 | 3H.8951.../2420209 | Starting issue Call By Customer Name:- Nikunj Patel Number:- 6355360834 | Task Start | AIA Engineering Ltd. | Unique Techno Services Pvt Ltd. - Ahmedabad | 2h | Engine not starting.Sometimes SPN/FMI-100,03 was showing in the controller.SD checked continuity between ECU and lube oil pressure sensor/coolant tem. Sensor. | Open | Amit Sandilya
1 | 210943305 | 2024-08-07 12:38 | 20 | GP3.1021.../2420017 | INSTANCE ID:-100744675 SITE ID:-I-GJ-KDNA-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-DG ISSUE NAME:-PATEL JAYANTIBHAI NUMBER:-6355821991 | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Godhra | 10 | The controller was showing voltage around 20-30 less than the actual voltage. After flashing the controller the voltage related problem was solved but after taking 10 minutes engine trail many SPN and FMI started showing in the controller.100/1,110/0,158/0,190/1. | Closed | Amit Sandilya | details requried
2 | 210942477 | 2024-08-07 10:25 | 20 | GP3.1021.../2420146 | INSTANCE ID:-100747642 SITE ID:-I-GJ-DHDK-ENB-G003 CALL BY CUSTOMER// DG ISSUE:-DG ENGINE STARTING PROBLEM NAME:-Kiran Goswami NUMBER:- 7722070441 | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Ahmedabad | 30 | Super Capacitor Replaced | Closed | Amit Sandilya | check list requried
| 210942809 | 2024-08-07 11:34 | 40 | 3H.8951.../2420150 | Abnormal sound issue Email By - Service Dealer Name -SHILPA | Closed | Bharat Keshav Narvekar. | Dhanashree Technocrats Pvt. Ltd. - Nasik | 21 | SE attend the site find exhaust cliding loosen and glasswool find in canopy. tighten the same and issue resolve. | Closed | Jagdeep Saini
1 | 210947604 | 2024-09-07 13:13 | 58.5 | T4.8941.../2420332 | Voltage Problem Call by : Customer Name : Sri hari Contact : 9573977254 | Task Start | Songs of Earth Plants Nursery | Powerlinks Infra Tech Pvt Ltd - Secunderabad |  | Today engg. visit the site . | open | Mr Md saleem
2 | 210946339 | 2024-09-07 09:20 | 30 | 3H.8902.../2320030 | ENGINE NOT START | Task Start | VST Motors Pvt Ltd | Bharath Diesel Sales and Service - Pattanur | 1.5 | Controller 17 pin found loose connection .engine cranking but not start. tightend the same | closed | Mr. Nandha Gopal | running hours required
3 | 210946308 | 2024-09-07 08:58 | 500 | DV8.8501.C4../2320077 | Tripping Problem Call by : Customer Name : Jay Prakash Contact : 8838242678 | Completed | Bharat Petroleum Corporation Ltd BPCL | Bharath Diesel Sales and Service - Karur | 24 | ecu malfuctioning alaram came due to low DEF level . | open | Mr. Nandha Gopal
4 | 210944591 | 2024-08-07 15:29 | 320 | F6.8802.../2320001 | Display Issue Â Call By Customer Name :-Sachin Kumar Mobile No :-7338603759 | Task Start | Suvarna Electricals | Surya Power Services - J C Road, Bangalore | 20 | Fuel level not showing in panel . After doing configuration in fuel level (they change the parameter in percentage with the help of DSE Software) . Problem resolved | closed | Mr. Prakash S
5 | 210937537 | 2024-06-07 09:52 | 0 | GP3.8702.../2420078 | DG Not starting | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 1 | DG not starting due to oil pressure sensor problem, EDO placed for oil pressure sensor | closed | Mr. Nandha Gopal | oil pressure sensor problem , oil pressure sensor defective checked the sensor input voltage 5 volt DC but alarm oil pressure High engine not running oil pressure 6.5 bar showing the controller. so removed the sensor near by DG set fitted the sensor alarm reset run the DG set found normal Engineer Remark Advice the customer near by DG set (3H.8951/2420186) engine removed the sensor .
1 | 210945901 | 2024-08-07 19:55 | 125.4 | 4H.8041.../2420113 | Amber lamp Alarm issue Call By Customer Name :-Murari Gupta Mobile No :-9953712442 | Open | Mayura Textiles | Paluck Technologies Ltd. - Faridabad | 108 | SPN/FMI: 5461/0, flashed latest cal file issue resolved. | Closed | Kapil Solanki | monitaring
2 | 210945119 | 2024-08-07 16:59 | 125.4 | 4H.8041.../2420186 | Display Issue Call By Customer Name :- Ankur Kumar Mobile No :- 7906860966 | Task Start | ADVANIECH HANDICRAFTS | Paluck Technologies Ltd. - Ghaziabad | 91 | Customer wanted to know how to check DEF percentage..thats why open the SR. | Closed | Kapil Solanki
3 | 210944562 | 2024-08-07 15:19 | 125.4 | 4H.8041.../2320181 | Tripping issue Call By Customer Name : Mukesh Kumar No:- 8273675392 | Task Start | HI TECH AGRO ENERGY PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 216 | Tripping issue..checked event log found Under speed alarm and SPN/FMI: 51/0 ( Throttle valave jammed) removed throttle valve connector and clean it, reconnected the same issue resolved. | Closed | Kapil Solanki
1 | 210948056 | 2024-09-07 14:51 | 125.4 | 4H.8041.../2420223 | Under Speed Alarm Issue Call By Customer Name :-Manish Kumar Mobile No :-9711385189 | Open | Eurokon Global Exports Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 44 | Tripping issue.. With showing Under speed alarm, found block load (60 KW) on DG,educated customer about the same. | Closed | Kapil Solanki
2 | 210947726 | 2024-09-07 13:48 | 15 | GP3.8501.../2320002 | Error Code issue Call By Customer Name : Ajay Wadhawan No:9810172765 | Task Start | Dr. Ajay Wadhawan | Vidyut Engineers - Noida | 39.36 | Customer complaint about Error code issue.. But engineer did not found any DTC, DG running ok. | Closed | Kapil Solanki | KRM check
3 | 210947670 | 2024-09-07 13:35 | 250 | F6.8841.../2420021 | Starting Issue Email By Service Dealer Name:-Sonu Rai | Task Start | ZOOTO FASHION PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 84 | ECU protect lamp alarm showing on display.. Checked Unswitched supply and fuel line found ok but issue not resolved.Today Koel team will visit site. | Open | Kapil Solanki
4 | 210947684 | 2024-09-07 13:32 | 200 | 6H.8435.../2320036 | Abnormal Sound Â Issue Call By Customer Name :-Anand Singh Mobile No :-7011589640 | Task Start | M.M.POLYVINYLS PRIVATE LIMITED | Vidyut Engineers - Noida | 95.15 | Abnormal sound from loose V belt, tighten the same and also Low DEF level, clear the DTC issue resolved. | Closed | Kapil Solanki | campaign cutt off check
5 | 210947656 | 2024-09-07 13:28 | 57 | T4.8941.../2320152 | Starting issue Call BY KGD Name :- Aashi No :- 9718850143 | Task Start | PSG ELECTRICALS | Paluck Technologies Ltd. - Ghaziabad | 697 | Maintenance alarm showing on display.. Reset the alarm and also canopy door lock issue.. | Closed | Kapil Solanki
6 | 210947470 | 2024-09-07 12:44 | 125.4 | 4H.8041.../2420011 | Voltage Issue Call By Service Dealer Name :-Devendra yadhav Mobile No :-9813602579 | Task Start | Sweta Medicose | Paluck Technologies Ltd. - Gurgaon | 285 | Customer side issue..( light flickring due to short wiring), no issue in DG. | Closed | Kapil Solanki
8 | 210947346 | 2024-09-07 12:04 | 320 | F6.8802.../2420029 | Starting issue Call By Customer Name : Rajat . Mobile No : 8146798381 | Task Start | Citi Developers | Royal Power Solutions - Zirakpur |  | SPN/FMI: 97/2 (Water in fuel sensor) found water mix in fuel tank (Need to clean), and also 168/3 (actutor relay- short circuit to battery error) and 3031/14 flashed latest cal file and clear DTC issue resolved. | Open | Ved Gupta
9 | 210947288 | 2024-09-07 11:59 | 625 | DV0.8501.C4../2320010 | Door Look Issue Call By Customer Name :-Sanjiv Kumar Mobile No :-8814828270 | Open | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat |  | Wrong complaint logged by customer. | Cancelled | Kapil Solanki
10 | 210947265 | 2024-09-07 11:48 | 500 | DV8.8501.C4../2320017 | Door Look Issue Call By Customer Name :-Sanjiv Kumar Mobile No :-8814828270 | Task Start | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat | 188.4 | Canopy door lock issue.. Corrected the same issue resolved. | Closed | Kapil Solanki
11 | 210947172 | 2024-09-07 11:33 | 125.4 | 4H.8041.../2320086 | Starting Issue Email By Service Dealer Name:-Sonu Rai | Task Start | Total Construction | Paluck Technologies Ltd. - Gurgaon | 1493 | Starting issue.. Cranking time battery voltage 7 V, checked battery charger found ok, Suspected battery faulty, today again engineer visited site with battery tester,to check battery. | Open | Kapil Solanki
12 | 210947161 | 2024-09-07 11:26 | 320 | F6.8802.../2420016 | Lube oil Leakage Email By Customer Name:-Rahul Singh | Task Start | Aims Angel Infratech LLP. | Vidyut Engineers - Noida | 22.53 | Oil leakage from oil coolar header assly… ( need to check and dismentle) | Open | Kapil Solanki
13 | 210946481 | 2024-09-07 10:12 | 320 | F6.8802.../2320017 | Starting Issue Call By Customer Name :-Kuldeep Sharma Mobile No :-8684002063 | Task Start | MT AUTOCRAFT | M/s OM Diesels Pvt. Ltd. - Rohtak | 233.16 | Overheating alarm showing on display.. Found radiator chocked, ( need to clean ) and also abnormal sound from Inlet manifold gasket (need to check) | Open | Kapil Solanki
14 | 210946410 | 2024-09-07 09:57 | 125.4 | 4H.8041.../2420062 | Error code issue Email By-Service Dealer Name:-Shiv | Closed | Sunita Biotech | Vidyut Engineers - Noida | 33.8 | SPN/FMI: 1761/16, Low DEF level, top up and educated customer about the same. | Closed | Kapil Solanki
15 | 210946357 | 2024-09-07 09:37 | 57 | T4.8941.../2320126 | Starting problem Email By - Customer Name - VINOD RANA | Closed | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 664 | Air lock issue.. Checked fuel line and clean the filter, issue resolved. | Closed | Kapil Solanki
16 | 210948975 | 2024-09-07 16:29 | 15 | GP3.8501.../2420063 | Starting Issue Email By Service Dealer Name:-Bharat dixit | Closed | Cricket Connect | R K Engineers - Meerut | 40 | Sometimes DG was not started in first crank with showing Under speed alarm, checked fuel line found ok. | Closed | Sudhir Awasthi | KRM check | Check the krm but does not show any typr of problem.
17 | 210948370 | 2024-09-07 15:55 | 125.4 | 4H.8041.../2420046 | Starting Issue Call By Â Customer Name :- Virendra Singh Mobile No :- 8586978239 | Task Start | SAMIT SALES PVT LTD | Paluck Technologies Ltd. - Faridabad | 82.53 | Low DEF level @ 38 %, top up and educated customer about the same . | Closed | Kapil Solanki
1 | 210947724 | 2024-09-07 13:46 | 15 | GP3.8501.../2420001 | Red Lamp On Alarm Issue Call By Customer Name :-Pradeep Kumar ... Mobile No :-8825350653 | Closed | Deepak Hospital | Globalline India Services Private Limited - Purnia | 51 | maintenance due alarm was showing ,today engineer will visit for the maintenance. | Closed | Prabhakar kumar
2 | 210947420 | 2024-09-07 12:27 | 58.5 | T4.8941.../2420302 | Starting Issue Call By Customer Name:Aman Singh Number:8210415074 | Closed | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 90 | emergency stop alarm is showing even after releasing the push button then engineer check the ckt found that internal connection of push button got stuck ,hence the push button issue resolve. | Closed | Prabhakar kumar
3 | 210943385 | 2024-08-07 12:54 | 15 | GP3.8501.../2420170 | Automation issue Call By Customer Name:- Dr. Alok Shyandhan Number:- 9835334854 | Task Start | Alok Shyandan | United Machinery Sales And Service - Dhanbad | 1.59 | engineer found that the mains supply wire to controller was damage due to which voltage drop around 110V ,so engineer change the wire issue resolved. | task closed. | Prabhakar kumar
4 | 210869590 | 18-06-2024 00:00 | 20 | GP3.8604…/2420110 | STARTING ISSUE | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Patna | 1 | ECU faulty. Replaced the ECU but found new ECU is also faulty. Another one ECU will be fitted on 11/7/24 | open | Prabhakar Kumar
5 | 210951448 | 2024-10-07 12:40 | 20 | GP3.8604.../ 2420022 | CONTACTOR FAULTY | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | NA | Visit pending | open | Prabhakar kumar
1 | 210952324 | 2024-10-07 15:33 | 160 | 6H.8475.../2420075 | Trip_Genset_High_Voltage | Open | MARUTI INFRACREATION PRIVATE LIMITED | Unique Techno Services Pvt Ltd. - Gandhidham | 40 | KRM generated SR | open | Amit Shandilya
2 | 210951698 | 2024-10-07 13:27 | 625 | DV2.8552.C4../2320004 | DG SET TRIPPING PROBLEM / CODE ISSUE Email By - Service Dealer Name -Dharmendrasinh Zala | Open | ADANI RENEWABLE ENERGY FIFTY SEVEN LIMITED | Unique Techno Services Pvt Ltd. - Gandhidham | 673 | Visit pending | open | Amit Shandilya
1 | 210949294 | 2024-09-07 17:27 |  | DV8.8542.C4../2420016 | Throttle Valve Faulty | Task Start | Green Field Enterprises | Suraj Motor Store - Jammu |  | Line Rejection SR, Throttle valve faulty, EDO placed. | Open | Ved Gupta
2 | 210949131 | 2024-09-07 16:57 | 125.4 | 4H.8041.../2420066 | Fuel Belt Issue Call BY Customer Name :- Amit No :- 7065865836 | Task Start | Welcome Crop Sciences Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 25.3 | Fuel sensor issue..Erratic reading showing on display..sometimes showing 30 %, 70 %, ,checked resistance found ok, but issue not resolved. | Open | Kapil Solanki | Revisit details
3 | 210949085 | 2024-09-07 16:49 | 125.4 | 4H.8041.../2420140 | Over load issue Call By Customer Name :- Manjay No :- 7982970631 | Task Start | BD. Enterprises | Paluck Technologies Ltd. - Faridabad | 116 | Customer side CNC machine was tripped, joint visit will be planed with Jakson team. | Open | Kapil Solanki
1 | 210951758 | 2024-10-07 13:38 | 750 | DV2.8501.C4../2320024 | Oil Leakage Issue Call By Customer Name :Gupta Mobile No9429459334 | Open | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 161.6 | Oil leakage from filter, replace the filter issue resolved. | closed | Kapil Solanki
2 | 210951648 | 2024-10-07 13:24 | 30 | 3H.8902.../2320038 | High Voltage issue Call By Customer Name : - Pradeep Yadav No:-8368321282 | Task Start | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 4.73 | Customer side changeover issue.. No issue in DG. | closed | Kapil Solanki
3 | 210951610 | 2024-10-07 13:20 | 125.4 | 4H.8041.../2320134 | Starting Issue Email By Service Dealer Name:-Bharat dixit | Task Start | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 509 | DEF Crystallization across SCR ,Clean with hot water, and checked Dosing module gasket found ok.refitted the same issue resolved. | closed | Sudhir Awasthi
4 | 210951636 | 2024-10-07 13:19 | 125.4 | 4H.8041.../2320181 | Tripping issue Call by Service Dealer Name:- Ramesh Sharma No:9599006443 | Task Start | HI TECH AGRO ENERGY PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 219 | DG was tripping on load , SPN/FMI: 51/0, ( Throttle valve jammed)checked ITV connector found ok. ITV will be change and also 3031/14, flashed latest cal file . | Open | Kapil Solanki
5 | 210951479 | 2024-10-07 12:47 | 82.5 | 5H.8901.../2320077 | Loading issue Call By Customer Name : -Darshan No:-9811042125 | Task Start | SURYA PRESS MET PVT LTD | Paluck Technologies Ltd. - Faridabad | 85 | Customer complaint about load issue..checked event log but no alarm found , checked DG on load half hours, DG running ok. | closed | Kapil Solanki | KRM check | Check the KRM but does not show any type of problem only show speed variation
6 | 210951439 | 2024-10-07 12:36 | 82.5 | 5H.8901.../2320021 | Power Supply Issue Call By Customer Name :-Piyush .. Mobile No :-7027070040 | Task Start | CRMK Select | Vidyut Engineers - Noida | 315 | Customer side panel issue..(Contractor not holding) ,educated he customer about the same. No issue in DG. | closed | Kapil Solanki
7 | 210951085 | 2024-10-07 11:29 | 82.5 | 5H.8901.../2420006 | Automatically Switching off Call by : Customer Name : Sunil Singh Contact : 9100474206 | Task Start | Valueline Trade Pvt. Ltd. | Vidyut Engineers - New Delhi | 9 | Customer wanted to know about CPCB IV+ product like, DEF level, Operating procedure , that’s why open SR educated customer about the same. | closed | Kapil Solanki
8 | 210950968 | 2024-10-07 11:11 | 125.4 | 4H.8041.../2420240 | Engine not taking load Email By - Service Dealer Name -Vikas Saini | Task Start | Dhani Power Solutions | M/s OM Diesels Pvt. Ltd. - Rohtak | 11 | DG was running on unbalance load (88A,75A,171A) educated the customer about the same. | closed | Kapil Solanki | KRM check | Check the KRM data and found it unblance load some time.
9 | 210950666 | 2024-10-07 09:39 | 160 | 6H.8475.../2420024 | Ad Blue Alarm Call By Customer Name :-Tarun .. Mobile No :-9315743664 | Task Start | Tool Room Engineers LLP | Paluck Technologies Ltd. - Faridabad | 50 | Low DEF level, top up and educated customer about the same issue resolved. | closed | Kapil Solanki
10 | 210951868 | 2024-10-07 14:07 | 20 | GP3.1010.../2300003 | KRM Issue Email By-Service Dealer Name:-Shiv | Closed | Hosexperts | Vidyut Engineers - Noida | 38.48 | KRM issue..(parameter was not showing), found Loose connection (15,16 wire) , tighten the same issue resolved. | Closed | Kapil Solanki
11 | 210951866 | 2024-10-07 14:04 | 320 | F6.8802.../2420016 | Oil Leakage Email By - Service Dealer Name -Shiv | Closed | Aims Angel Infratech LLP. | Vidyut Engineers - Noida | 22.54 | Oil leakage from oil coolar header assly..O ring damaged, ( need to replaced) | Closed | Kapil Solanki
12 | 210950952 | 2024-10-07 10:59 | 125.4 | 4H.8041.../2420345 | Starting issue Call By Customer Name : - jishan No:-8872321519 | Closed | Secret Heart Convent School | Megatron Engineers - Amritsar | 2.5 | SPN/FMI: 516166/0, educated customer about the same. | Closed | Ved Gupta
1 | 210952097 | 2024-10-07 14:38 | 15 | GP3.8501.../2420173 | Starting Problem | Task Start | Maneesh K. S. | G-Care Diesels Private Limited - Thrissur |  | SPN-2791/FMI-31 EGR valve is jammed in closed state, instructed to ASE to release it in idle condition then check OC/SC of EGR harness, update not received. and also I konnect tool is not availiable at the site that time. Tommorow engineer will visit again with Ikonnect tool. | open | Mr Sanjaymon
2 | 210952043 | 2024-10-07 14:31 | 0 | 6H.8475.../2420089 | FUEL LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry |  | Update pending at ASE end. | open | Mr Nanda Gopal | DEF leakage in the hose crimping area
3 | 210950979 | 2024-10-07 11:01 | 0 | 5H.5106.../2300001 | white smoke and HO joint visit | Open | Bull Machines Pvt Ltd | Electro Controls - Coimbatore |  | White smoke issue. Engineer changed the fuel suction line with transparent pipes and observed there are some air bubbles in the fuel line . Today they will visit again and do the needful. | open | Mr Sanjaymon
4 | 210950139 | 2024-09-07 18:37 | 25 | GP3.8702.../2420152 | RAIL PRESSURE SENSOR FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur |  | DTC found for Rail pressure sensor found faulty .So, EDO placed. | open | Mr Nanda Gopal | EDO is in transit
5 | 210947604 | 2024-09-07 13:13 | 58.5 | T4.8941.../2420332 | Voltage Problem Call by : Customer Name : Sri hari Contact : 9573977254 | Closed | Songs of Earth Plants Nursery | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 0.25 | Customer want connection with battery charger . engg. did the same problem resloved . | closed | Mr. Saleem
6 | 210946339 | 2024-09-07 09:20 | 30 | 3H.8902.../2320030 | ENGINE NOT START | Closed | VST Motors Pvt Ltd | Bharath Diesel Sales and Service - Pattanur | 1.5 | After overriding the ECU. The temprature and oil parameter are showing NA in display. 2A1 connector found in loose connection in wiring harness, corrected the same issue resolved. | closed | Mr Nanda Gopal
7 | 210946308 | 2024-09-07 08:58 | 500 | DV8.8501.C4../2320077 | Tripping Problem Call by : Customer Name : Jay Prakash Contact : 8838242678 | Completed | Bharat Petroleum Corporation Ltd BPCL | Bharath Diesel Sales and Service - Karur | 24 | Update pending at ASE end. | closed | Mr Nanda Gopal | Low DEF level alarm popping up.Top uped the same issue resolved.
1 | 210951448 | 2024-10-07 12:40 | 20 | GP3.8604.../ 2420022 | CONTACTOR FAULTY | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 30 | Line Rejection SR- engineer found that the mains contactor not holding i.e. contactors coils may burn out due to low voltage around 110V hence engineer change the same from market. | closed | Prabhakar kumar
1 | 210954692 | 2024-11-07 10:38 | 30 | 3H.8902.../ 2320033 | Tripping Â Issue Call By Customer Name :-Sufiyan .. Mobile No :- 8298184239 | Closed | Care and Cure | Yodha Automobiles Private Limited - Ranchi | 10.59 | overload on B phase educate the customer for load balance. | closed | Prabhakar kumar
1 | 210953961 | 2024-10-07 21:32 | 125.4 | 4H.8041.../2420014 | Amber Lamp Alarm issue Call By Customer Name : Sanjay Sharma No:9811257049 | Open | Mandap International Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 68 | SPN/FMI : 5461/0 , flashed latest cal file issue resolved. | Closed | Kapil Solanki
2 | 210953901 | 2024-10-07 19:20 | 125.4 | 4H.8041.../2420018 | Alarm issue Call By Customer Name:- Varun Goel Number:- 9416337998 / 9817121037 | Open | Sharkline Appliances | M/s OM Diesels Pvt. Ltd. - HISAR |  | Visit Pending | open | Kapil Solanki | KRM check for fault code | Check KRM only found it the 1761/16 fault code
3 | 210953887 | 2024-10-07 19:09 | 82.5 | 5H.8901.../2420112 | Panel Door Lock Problem Email By KGD Name:-Sanjeev Jain | Open | Partap Public School | Industrial Power Solutions - LUDHIANA | 2.2 | Starting issue.. Battery charger not connected to mains supply, connected the same issue resolved. | Closed | Ved Gupta
1 | 210955410 | 2024-11-07 13:11 | 160 | 6H.8475.../2320005 | . | Task Start | MODEL ECONOMIC TOWNSHIP LIMITED | M/s OM Diesels Pvt. Ltd. - Rohtak |  | Line Rejection SR,( Cancelled) | Cancelled | Kapil Solanki
2 | 210955379 | 2024-11-07 12:58 | 625 | DV0.8501.C4../2320026 | Display Issue Call By Customer Name :-Manish Yadav Mobile No :-8707798423 | Task Start | Perigee Infratech Private Limited | Paluck Technologies Ltd. - Ghaziabad | 151 | Customer wants fuel level indication in percentage (%) , Engineer change graph/column lines to percentage , issue resolved | Closed | Kapil Solanki
3 | 210955199 | 2024-11-07 12:20 | 20 | GP3.8601.../2420027 | Amber Lamp Alarm Issue Call by Customer Name: Rahul Number: 9837088880 | Task Start | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 2 | Emergency switch pressed by customer end, corrected the same issue resolved. | Closed | Sudhir Awasthi
4 | 210954933 | 2024-11-07 11:41 | 125.4 | 4H.8041.../2420293 | Starting issue | Task Start | Shakti Pulley | M/s OM Diesels Pvt. Ltd. - Rohtak |  | Line rejection SR , battery was discharge (1.3 volt) , Engineer brings the battery to the dealer office for charge the battery | Open | Kapil Solanki
5 | 210954905 | 2024-11-07 11:18 | 160 | 6H.8475.../2420021 | Starting Issue Email By-Service Dealer Name:-Bharat dixit | Task Start | SRV Industries | R K Engineers - Meerut | 58.38 | DEF level was low top up the DEF and educated the customer about the same | Closed | Sudhir Awasthi
6 | 210954842 | 2024-11-07 11:07 | 160 | 6H.8475.../2420039 | alarm issue. Email By - Service Dealer Name -Bharat dixit | Task Start | Hi Tech Engineers. | R K Engineers - Meerut | 14.26 | charge fail alarm was showing ,found charging alternator (input pin no 6) connector was loose , correct the same issue resolved | Closed | Sudhir Awasthi
7 | 210954855 | 2024-11-07 11:04 | 400 | DV8.8542.C4../2420010 | ECU Mall Functioning Alarm Call By Customer Name :-Yetendra Singh Mobile No :-7042248939 | Task Start | MCAM. Surion India Ltd. | Paluck Technologies Ltd. - Ghaziabad | 46 | SPN/FMI - 523582/0 , clear the DTC issue resolved. | Closed | Kapil Solanki | Details required
8 | 210954785 | 2024-11-07 10:55 | 125.4 | 4H.8041.../2420138 | Tripping issue Call By Customer Name : Sunil Yadav No:- 9151025719 | Task Start | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur | 178 | DEF level was low top up the DEF and educated the customer about the same | Closed | Sudhir Awasthi
9 | 210954685 | 2024-11-07 10:38 | 82.5 | 5H.8901.../2420015 | Tripping Issue and Preventive Maintenance Call By Customer Name :-Rahul Kumar Mobile No :-9958806012 | Task Start | Rahul Kumar | M/s OM Diesels Pvt. Ltd. - Sonipat | 60.33 | Starting issue due to air lock , water separator filter was minor loose, tighten the same issue resolved , service due | Closed | Kapil Solanki
10 | 210955995 | 2024-11-07 15:21 | 1000 | DV8.8502.C4../2420001. & 2420002. | synchronization Optiprime Email By - Service Dealer Name -Sonu Rai | Task Start | Tulip Infratech Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 36 | Sync issue..Sink time out alarm was showing , (both breaker was not holding at one time ),after checking all wiring connections found ok,then found sink activation was not on in 2 nd DG, enable the same and toad trail on DG 30 min. found ok. Then 523576/0 alarm was showing in 2nd DG , checked SM pressure was 0 in bank B after interchanging SM problem remains same in bank B | Closed | Kapil Solanki
1 | 210954431 | 2024-11-07 07:53 | 82.5 | 5H.8901.../2320001 | Automation Issue Call By Customer Name :-Balaji . Mobile No :-9840573732 | Closed | Starrk Revolution | Madhu Engineering Sales & Service - Teynampet,Chennai | 71 | Automation Issue. Found 2A1 connection in loose condition. Corrected the same. Issue resolved. | Closed | Mr. Nanda Gopal
2 | 210952097 | 2024-10-07 14:38 | 15 | GP3.8501.../2420173 | Starting Problem | Task Start | Maneesh K. S. | G-Care Diesels Private Limited - Thrissur | LR | SPN-2791/FMI-31 EGR valve is jammed in closed state. Today update : updated calibration file for ECU is shared to ASE.Also EGR Valve is replaced. fault code is still persist. Today we will calibrate the ECU again. | Open | Mr. Sanjaymon
3 | 210952043 | 2024-10-07 14:31 | 0 | 6H.8475.../2420089 | FUEL LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | LR | DEF leakage in the hose crimping area. | Closed | Mr. Nanda Gopal
4 | 210950979 | 2024-10-07 11:01 | 0 | 5H.5106.../2300001 | white smoke and HO joint visit | Open | Bull Machines Pvt Ltd | Electro Controls - Coimbatore | LR | Field monitering Report attached | Open | Mr. Nanda Gopal
1 | 210957039 | 2024-11-07 20:50 | 15 | GP3.8501.../2320002 | Error Code issue Call By Customer Name : Ajay Wadhawan No:9810172765 | Open | Dr. Ajay Wadhawan | Vidyut Engineers - Noida | 39.59 | Tripping issue..checked event log found Under speed alarm , checked fuel line found ok and the checked panel connections found ok then reset the alarm issue resolved. | Closed | Kapil Solanki
2 | 210957001 | 2024-11-07 19:00 | 30 | 3H.8902.../2320131 | AMF Panel Stating Call By Customer Name :-Nighil No :- 8059940590 | Open | Dr. Surekha Yadav Maternity & Surgical Hospital | Paluck Technologies Ltd. - Gurgaon | 44 | Automation issue.. (AMF Panel selector switch was in manual mode) educated customer about the same . | Closed | Kapil Solanki
3 | 210956857 | 2024-11-07 17:57 | 82.5 | 5H.8901.../2420058 | Over Loading issue Call By Customer Name : Girish Panday No:- 7618539888 | Open | SHREE JASVANT SINGH EDUCATIONAL SOCIETY | Deep Jyoti Electricals and Services - Haldwani |  | customer side issue.. no issue in DG. | Closed | Sudhir Awasthi
4 | 210956579 | 2024-11-07 17:03 | 25 | GP3.8702.../2420066 | Voltage issue Call By Customer Name : Survhi .. No:- 9991400055 | Open | Vikas Kataria. | Vishal Power Systems - PANIPAT | 16.7 | Starting issue.. Battery charger input wire was in losse condition, tighten the same issue resolved. | Closed | Kapil Solanki
5 | 210956353 | 2024-11-07 16:30 | 750 | DV2.8501.C4../2320023 | Starting Issue Message By Customer Name : Abhishek Kumar No : 7903795913 | Task Start | HIND TERMINALS PVT LTD | Paluck Technologies Ltd. - Faridabad | 266 | Starting issue with showing SPN/FMI:( 51/0 throttle valve high) & 5419/1, checked throttle valve connector and clean it properly, then refitted the same issue resolved. | Closed | Kapil Solanki
6 | 210956246 | 2024-11-07 16:12 | 125.4 | 4H.8041.../2320055 | Starting issue & Urea alaram issue Call By Customer Name : Vishvnath ... No:- 9992920383 | Task Start | Pri Oil And Gas Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 132.5 | SPN/FMI; 3031/14, flashed latest cal file issue resolved. | Closed | Kapil Solanki
7 | 210956181 | 2024-11-07 15:59 | 20 | GP3.8601.../2420042 | Automation Issue Call By Â Customer Name :-Rahul ... Mobile No :-8708716510 | Task Start | Fazil Sir | M/s OM Diesels Pvt. Ltd. - Rohtak | 30 | Automation issue.. Customer side panel issue (Sensing missing),educated customer about the same. | Closed | Kapil Solanki
8 | 210956052 | 2024-11-07 15:39 | 57 | T4.8941.../2320027 | Starting issue Call BY KGD Name :- Aashi No :- 9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - New Delhi | 4 | Starting issue.. Found air lock problem due to loose bolt, tighten the same issue resolved. | Closed | Kapil Solanki
9 | 210955833 | 2024-11-07 14:56 | 30 | 3H.8902.../2420009 | Tripping Issue Call By Customer Name :- Pramit Mobile No :- 9896935354 | Task Start | Suraj Auto | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 53 | DG was tripping with showing Under speed alarm , checked fuel line found ok, but issue not resolved, (Revisit Required) | Open | Kapil Solanki
10 | 210955710 | 2024-11-07 14:25 | 57 | T4.8941.../2320287 | Starting issue Call By Customer Name : Tinku .. No:- 9312835568 | Task Start | Karan Ahlawat | Vidyut Engineers - New Delhi | 1.6 | Starting issue due to discharged battery..(Customer using Auto panel charger), connected the koel panel charger issue resolved. | Closed | Kapil Solanki
1 | 210958811 | 2024-12-07 14:55 | 125.4 | 4H.8041.../2420433 | Urea Leakage issue Call BY Customer Name :- Vitul No:- 7351506997 | Open | Payal Ceramics | Espiem Engines & Machines (P) Limited - Aligarh | 19 | Customer complaint about Ad blue leakage, but there is no such type of issue.. Only showing Low DEF level top up and clear the DTC issue resolved. | Closed | Sudhir Awasthi
2 | 210958786 | 2024-12-07 14:45 | 10 | GP3.8301.../2420023 | AUTOMATION ISSUE Email By - Service Dealer Name -Karan | Task Start | Karamveer Singh Sodhi | Dynamic Engineering Services - Jalandhar | 14 | SPN/FMI: 1761/16, low DEF level , clear the DTC issue resolved. | Closed | Ved Gupta
3 | 210958657 | 2024-12-07 14:02 | 82.5 | 5H.8901.../2420011 | Doar Lock Issue Call By Customer Name :-Pawan Gupta Mobile No :-9918982839 | Task Start | Bhavani Enterprises | S. R Engines Sales And Service - Gorakhpur | 23 | Canopy door lock issue.. Adjust lock issue resolved. | Closed | Sudhir Awasthi
4 | 210958621 | 2024-12-07 13:51 | 57 | T4.8941.../2320216 | Power Supply issue Call by customer Name:-Vijay No:- 9717593201 | Task Start | Sahyog Projects Private Limited | Vidyut Engineers - Noida | 81.12 | Customer complaint about power supply issue.. Checked DG on load and manual found ok. No issue in DG. | Closed | Kapil Solanki
5 | 210958320 | 2024-12-07 12:57 | 125.4 | 4H.8041.../2320086 | Battery Issue Email By-KGD Name:- Ashutosh Kumar Singh | Open | Total Construction | Paluck Technologies Ltd. - Gurgaon | 1522 | Starting issue..battery faulty,( checked with battery tester), Changed battery issue resolved. and also oil seepage from injector wiring and loose filter, tighten the filter issue resolved. | Closed | Kapil Solanki | Details to be share to QA
6 | 210958273 | 2024-12-07 12:49 | 82.5 | 5H.8901.../2320071 | Amber Lamp Alarm Call By Customer Name :-S K Mandal No :-9811830989 | Task Start | Harmony Export | Vidyut Engineers - Noida | 35.18 | SPN/FMI: 516166/0, clear the DTC and educated customer about the same. | Closed | Kapil Solanki
7 | 210958033 | 2024-12-07 11:57 | 400 | DV8.8542.C4../2420006 | VOC-ENGINE NOT STARTING - AIR LOCK IN FUEL SYSTEM Customer Name-Satish Customer Number -7309949618 Mode- SR Generated through CDI calling. | Open | Dhanvi Engineering | Paluck Technologies Ltd. - Gurgaon |  | As previously disscussed,Alternator disc bolt broken,(decision pending) | Open | Kapil Solanki
8 | 210957968 | 2024-12-07 11:31 | 40 | 3H.8951.../2420142 | Mobiel oil Gauge issue Email By - Service Dealer Name -Kajal | Task Start | Rama Krishna Paints & Hardware | Industrial Power Solutions - LUDHIANA | 5 | As previously discussed, Dipstick theft, new one given by SD team on paid basis | Closed | Ved Gupta
9 | 210957839 | 2024-12-07 11:03 | 40 | 3H.8951.../2420082 | Starting issue Call By Customer Name : vikram sir No:9671368538 | Task Start | Choudhary Fuels | M/s OM Diesels Pvt. Ltd. - Rohtak | 45 | Starting issue..battery was discharged, battery charger not connected to mains supply, connected the same issue resolved. | Closed | Kapil Solanki
10 | 210957734 | 2024-12-07 10:49 | 160 | 6H.8475.../2420032 | ECU Alarm Issue Call By Customer Name :- Anuj kumar Mobile No :- 8447323227 | Task Start | Airpack Compressor Teknologies P. Ltd. | Paluck Technologies Ltd. - Faridabad | 48 | SPN/FMI: (1761/16)( 516166/0 ), and 3031/14, top up DEF and flashed latest cal file, clear the DTC issue resolved. | Closed | Kapil Solanki
11 | 210957677 | 2024-12-07 10:37 | 125.4 | 4H.8041.../2420067 | Fuel Senseoer Issue Call By Customer Name :- Mobile No :- | Task Start | Mona Power Trading | M/s OM Diesels Pvt. Ltd. - Sonipat | 447.56 | Tripping issue..Low fuel level alarm was showing on Display..but actually 50 % fuel available on tank, checked sensor Connector found loose condition connected properly , and checked resistance found ok, then removed sensor and clean it, and refitted the same issue resolved. | Closed | Kapil Solanki
12 | 210957563 | 2024-12-07 10:12 | 25 | GP3.8702.../2420048 | Emergency Stop Alarm and Automation issue Call By Customer Name :- Jitendra Kumar Mobile No :-9654019499 | Task Start | Jitender Kumar | Paluck Technologies Ltd. - Gurgaon | 137.5 | Customer Complaint about Emergency stop alarm, but engineer did not found any issue.. DG running ok on load. | Closed | Kapil Solanki
13 | 210957435 | 2024-12-07 09:17 | 125.4 | 4H.8041.../2420176 | Starting Issue Email By-Customer Name:-VINOD RANA | Closed | Xpert Powergen Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 460.1 | Tripping issue..Low fuel level alarm was showing on Display..but actually 70 % fuel available on tank, checked sensor Connector found ok, and checked resistance found ok, then removed sensor and clean it, and refitted the same issue resolved. | Closed | Kapil Solanki
14 | 210961546 | 2024-12-07 21:14 | 160 | 6H.8475.../2420034 | Fuel Sensor issue And Fuel Leakage issue Call by customer Name:- Virendra Sir Number:- 8810511604 | Open | SR. Power Engineers | Vidyut Engineers - Noida | 31.45 | Fuel sensor issue.. Erratic reading showing on display..(only 25 % fuel was showing but actual 70 % fuel available on tank,), check sensor resistance found ok, then remove sensor found stuk ( float not moving), refitted the same issue resolved. | Closed | Kapil Solanki
15 | 210961323 | 2024-12-07 17:59 | 125.4 | 4H.8041.../2320133 | Loading Issue Call By Customer Name :-Tiwari Mobile No :- 8617480675 | Completed | Jai Balaji Industries..... | Espiem Engines & Machines (P) Limited - Aligarh | 315 | Starting issue with showing Under speed alarm, found air lock issue..remove air issue resolved. ( E- feed pump not installed) | Closed | Sudhir Awasthi
16 | 210961322 | 2024-12-07 17:59 | 125.4 | 4H.8041.../2420136 | Starting Issue Call By Customer Name :- Sumit Khullar Mobile No :- 8920251062 | Task Start | SHIVAM POWER GENERATORS | OVN Industries Private Limited - New Delhi | 4.21 | Customer side mains wiring problem, no issue in DG. | Closed | Kapil Solanki
17 | 210961264 | 2024-12-07 17:51 | 15 | GP3.8501.../2420054 | AMF Panal issue Call by customer Name:- Vineet Tyagi No:-9018674696 | Task Start | Mr. Vineet Tyagi | R K Engineers - Meerut | 5.35 | Mains contractor was burnt, (Need to replaced) | Open | Kapil Solanki | KRM check for load | Custmor always use below 40 % load and major time three KW load.
18 | 210959357 | 2024-12-07 16:57 | 160 | 6H.8475.../2420024 | Under Voltage Issue Call By Â Customer Name :-Sunil Kumar Mobile No :-7206727293 | Task Start | Tool Room Engineers LLP | Paluck Technologies Ltd. - Faridabad | 57 | Tripping issue.. Checked event log found showing R,Y,B phase under voltage alarm & Under frequency alarm, then checked terminal voltage found L to L- 40 volt , then checked AVR found AVR fuse blown out, replaced the same issue resolved. | Closed | Kapil Solanki | KRM check for load | Check KRM but does not show any type of problem in load.
1` | 210963209 | 13-07-2024 15:09 | 40 | 3H.8951.../ 2420018 | Voltage issue Call BY Customer Name :-Prashant No :- 8340361801 | Closed | R. K. Dayal Nursing Home & Resarch Center. | Globalline India Services Private Limited - Muzaffarpur | 9 | Engginner found over voltage around 250 V so he tunning the AVR for voltage limit of 240 V hence the problem resolved | Closed | Prabhakar kumar
2 | 210962224 | 13-07-2024 10:50 | 100 | 4H.8041.../ 2420498 | Engine trip with alarm Inducement Internal Fault | Task Start | powerline Industries | Hibreed Engineering Pvt. Ltd. - Nagaon | 0 | Dosing module connection was loose then Engginner connect the tool and found one alarm inducement error fault is locked and clear the alarm issue resolved | Open | Subharajit roy
1 | 210962550 | 13-07-2024 12:11 | 250 | F6.8841.../2420050 | Red Lamp On Alarm Call By Customer Name :- Dhruv Bhardwaj Mobile No :-8439496629 | Closed | Hinata Polymers | Vidyut Engineers - Noida | 20 | Low DEF level, Top up DEF and educated customer about the same. | Closed | Kapil Solanki
2 | 210962479 | 13-07-2024 11:50 | 200 | 6H.8435.../2320036 | DG Contractor issue Call by customer Name:-Anand Singh No:-7011589640 | Closed | M.M.POLYVINYLS PRIVATE LIMITED | Vidyut Engineers - Noida | 100.25 | B phase was hot sparking , due to B phase phase bolt was loose, tighten the same issue resolved. | Closed | Kapil Solanki
3 | 210962249 | 13-07-2024 10:56 | 500 | DV8.8501.C4../2420078 | Fuel Cap Issue & Door Lock Issue Call BY Customer Name :- Vinit No:- 9354937132 | Task Start | MTI. Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Sonipat | 25 | Door aligenment issue.( Panel side), fuel cap was not fitted properly, (need to replaced) | Open | Kapil Solanki
4 | 210962201 | 13-07-2024 10:40 | 250 | F6.8841.../2320039 | Starting issue Call By Customer Name : Dinesh . No:9968283648 | Closed | M/s. Classic Generatos | Vidyut Engineers - Noida | 46.8 | Rain water is entering the canopy due to rain gaurds not installed, SD team communicated to supplier for the same. | Closed | Kapil Solanki
5 | 210961949 | 13-07-2024 09:10 | 320 | F6.8802.../2420041 | Starting Issue Call By Customer Name :-Dev Singh Mobile No :-7668363066 | Closed | Eins Technik Formwork System | Paluck Technologies Ltd. - Ghaziabad | 47 | Battery was discharged due to battery charger not connected to mains supply, Connected the same issue resolved. | Closed | Kapil Solanki
6 | 210963211 | 13-07-2024 15:09 | 125.4 | 4H.8041.../2320017 | Error Code issue Call By Customer Name : Rajesh . No:8818088988 | Task Start | RAJESHWARI CHEMICALS | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 132 | Low DEF level, Top up DEF and educated customer about the same. | Closed | Kapil Solanki
7 | 210963632 | 13-07-2024 16:35 | 125.4 | 4H.8041.../2420051 | Abnormal Sound Issue Call By Customer Name :-Ajay Kumar Mobile No :-8287778015 | Closed | RURBAN INTERCORP LLP | Paluck Technologies Ltd. - Ghaziabad | 60 | SPN/FMI: 3218/20 related to Nox sensor, found sensor was in Open Condition, connected the same and clear the DTC issue resolved. | Closed | Kapil Solanki
1 | 210962310 | 13-07-2024 11:09 | 82.5 | 5H.8901.../2420129 | Error Code Issue Email By-Service Dealer Name:- EMKAY MOTORS | Task Start | The Principal. | EMKAY MOTORS - Kollam | 1 | 6 Error codes related to DEF quality, level, temprature found in display. During trouble shooting we found that no 12 V supply at DEF header 4 pin connector ( Can communication is OK) . When we connected 12 V auxiliary supply to DEF header unit and cleared all the DTC. Engine running OK. EDO placed for wiring harness. | Closed | Mr Sanjaymon
2 | 210958506 | 2024-12-07 13:26 | 250 | F6.8841.../2420067 | Starting Problem Call by : Customer Name : Narayana Contact : 6301752674 | Task Start | Vijetha Supermarkets Private Limited | Powerlinks Infra Tech Pvt Ltd - Karimnagar | 51 | Auto mains enabled in KG 745 | Closed | Mr. Saleem
3 | 210958051 | 2024-12-07 11:58 | 40 | 3H.8951.../2420122 | Starting Issue Email By Service Dealer Name:-Jasna N P | Task Start | Muneer | Welcare Engineering And Services Pvt. Ltd. - Kasargod | 17 | Engineer visited the site. There is no issue with genset end. Found issue in customer scope electrical panel. | Closed | Mr Sanjaymon
4 | 210957724 | 2024-12-07 10:47 | 0 | 5H.8901.../2420044 | ENGINE STARING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 0.43 | ITV valve stuked found. Replaced the same. issue resolved. | Open | Mr. Nanda Gopal | engine is shut down at 20% load,found error code 51/1,51/0 error code on the controller, then checked the engine as per the error, checked the Inlet throttle valve input supply found ok.checked the wiring harness found ok.then discussed with koel person and changed the another one inlet throttle valve from stock engine (5H.8901/2420195).then assembled the ITV properly, checked the cable properly connected.then connected the ikonnect tool and clear the fault code .
5 | 210955770 | 2024-11-07 14:39 | 500 | DV8.8501.C4../2320071 | Starting Problem Call by : Dealer Name :Selvi Contact : 6380111106 | Open | Unitherm Engineers Limited | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 5 | Raised complaint for low DEF level. | Closed | Mr. Nanda Gopal
6 | 210952097 | 2024-10-07 14:38 | 15 | GP3.8501.../2420173 | Starting Problem | Task Start | Maneesh K. S. | G-Care Diesels Private Limited - Thrissur | LR | Calibrated the Sedemac ECU with AG48 V5 Flashing file, then EGR 2791/FMI-3 got deactivated, then Sweep stuck fault code came 240/7 then it was not able to clear by changing the Solenoid sweep Difference from 2000 mV to 500 mV then it got deactivated by removing and refixing +,- terminals on the battery. | Closed | Mr Sanjaymon
7 | 210952043 | 2024-10-07 14:31 | 0 | 6H.8475.../2420089 | FUEL LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | LR | DEF Leakage from hose crimping area. EDO is in transit | Open | Mr. Nanda Gopal
West Zone
1 | 210962626 | 13-07-2024 12:30 | 30 | 3H.8902.../2420123 | Starting Issue Call By Customer Name :-Dipak ... Mobile No :-9926090700 | Closed | Jasprit Singh Bhatia | Natraj Power Tech - Indore | 2h | Emergency stop alarm was showing. | Closed | Vijay Patil
2 | 210958137 | 2024-12-07 12:11 | 20 | GP3.1021.../2420095 | Mains contactor faulty | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Vadagam | 8h | Mains contactor coil was burt. | Closed | Amit Shandilya
3 | 210966671 | 15-07-2024 12:46 | 58.5 | T4.8941.../2420269 | FAN BROKEN | Task Start | Omkar Dalvi | Transcreek Engineers Pvt. Ltd. - Wadkhal | 6.33h | Fan and radiator damaged due to broken fan belt | Open | Jagdeep Saini | Details required
4 | 210964221 | 13-07-2024 18:08 | 20 | GP3.8601.../2420311 | ABNORMAL SOUND | Task Start | Shreemohini Energy | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC | 12h | The alternator had a manufacturing defect and was producing abnormal sound. Vendor Issue. | Open | Jagdeep Saini | PIR required from AO
3 | 210963890 | 13-07-2024 17:30 | 750 | DV2.8501.C4../2420006 | ECU Error Code Issue Call By Customer Name :- Manish No :- 9811891788 | Open | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida |  | customer did't allowed to checked DG set. | Cancelled | Kapil Solanki
4 | 210963842 | 13-07-2024 17:15 | 62.5 | T4.8941.../2420125 | Under Speed Alarm Issue Call By Customer Name :-Gurav Mobile No :-7015984471 | Task Start | RS. Udhyog | M/s OM Diesels Pvt. Ltd. - Rohtak | 26 | DG was tripping with showing R,Y,B phase and Under frequency alarm, checked terminal voltage L to L 40 V, then bypass the AVR pass then check terminal voltage L to L 415 V , ( need to replace AVR) | Open | Kapil Solanki
5 | 210963681 | 13-07-2024 16:45 | 625 | DV0.8501.C4../2320001 | Oil filter change Issue Message by customer Name : Pardeep Kumar No : 9910417830 | Open | Tata Tele services | Vidyut Engineers - New Delhi |  | Wrong complaint rasied by customer no issue in DG. | Cancelled | Kapil Solanki
8 | 210963179 | 13-07-2024 14:55 | 750 | DV2.8501.C4../2420011 | Starting Issue Call By Customer Name: Parvesh Kumar Number: 9720093797 | Closed | Sleek Brake Products | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 423 | Water in fuel alarm was showing, SPN/FMI: 6301/2, found water mix in filter, clean and refitted the same issue resolved.( Customer side issue canopy doow was open) | Closed | Kapil Solanki
9 | 210962964 | 13-07-2024 14:04 | 40 | 3H.8951.../2320049 | Power supply issue Call by customer Name:-Rajveershing .. No:-9810937200 | Open | Ruchika Service Station | Vidyut Engineers - New Delhi |  | Customer did't picked up the call. | Cancelled | Kapil Solanki
10 | 210964867 | 14-07-2024 18:47 | 25 | GP3.8702.../2420046 | Emergency Stop Issue Call By Customer Name :-Bahadur Kumar Number :-9315077737 | Open | Sharda Cotton Factory | M/s OM Diesels Pvt. Ltd. - Sirsa | 4 | Starting issue with showing emergency stop alarm , found canopy emergency switch connections was in loose condition , tighten the same issue resolved | Closed | Kapil Solanki
11 | 210965355 | 14-07-2024 18:01 | 160 | 6H.8475.../2420006 | Starting issue Call By Customer Name : Shubahm Kumar No:- 6306784581 | Open | India Shine Technologies | Paluck Technologies Ltd. - Faridabad | 362 | SPN/FMI - 1761/14,1761/18,1761/16,5461/8,516166/0,P1709 , DEF level was low top-up the DEF and educated the customer about the same | Closed | Kapil Solanki
12 | 210964796 | 14-07-2024 16:30 | 30 | 3H.8902.../2320062 | Oil leakage issue Call By Customer Name : Amit .. No:- 9634778306 | Task Start | Buddha Engicon Private Limited | Paluck Technologies Ltd. - Ghaziabad |  | Customer complaint about oil leakage , engineer did not found any issue | Closed | Kapil Solanki
13 | 210964761 | 14-07-2024 14:45 | 125.4 | 4H.8041.../2320134 | Oil leakage issue Call by customer Name:-Kasidh Ahmad No:-8445820675 | Open | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar | 535 | Customer Complaint about OIL leakge issue.. Today engineer will visit site. | Open | Kapil Solanki
14 | 210964733 | 14-07-2024 14:27 | 20 | GP3.8601.../2320039 | Error Code Issue And Red Lamp On Alarm Issue Call By Customer Name :- Mohmmad Wali Mobile No :-9128000020 | Open | Mohammad Wali | Vidyut Engineers - Noida | 292.49 | SPN/FMI - 2802/4, check the battery terminal found ok, and check battery charger found ok , reset the alarm issue resolved | Closed | Kapil Solanki | KRM check | CHECK KRM data but does not show any type of fault related battery voltage.
15 | 210964673 | 14-07-2024 11:48 | 82.5 | 5H.8901.../2320075 | Error code issue & Tripping issue & under voltage issue Call by customer Name:- Mohit Kumar No:- 9899345113 | Open | Rudra Construction | Pratap Diesels Pvt. Ltd. - Bhilwara |  | Customer side panel issue , customer side motor was short circuit , educated the customer about the same | Closed | Gourav Sharma
16 | 210964669 | 14-07-2024 11:38 | 57 | T4.8941.../2420107 | Automaton Issue Call By KGD Name:-Pradeep Bhati Mobile No:-9911316001 | Open | Pratibha Anand & Sons | Vidyut Engineers - Noida | 22 | Customer side panel issue , wrong complaint raised by KGD | Closed | Kapil Solanki
17 | 210964640 | 14-07-2024 10:28 | 57 | T4.8941.../2320169 | Starting issue Call By Customer Name : Samraul No:- 7017630905 | Open | Tiger Ceramics | Espiem Engines & Machines (P) Limited - Aligarh | 371 | Starting issue.. Found XDBK 3 distribution box , 1C2 wire was in loose condition, tighten the same issue resolved | Closed | Kapil Solanki
18 | 210964613 | 14-07-2024 10:01 | 125.4 | 4H.8041.../2420186 | Starting issue Call By Customer Name : Ankur Kumar No:-7906860966 | Closed | ADVANIECH HANDICRAFTS | Paluck Technologies Ltd. - Ghaziabad | 91.1 | Battery was discharge , battery charger was not connected , connected the same and educated the customer about the same | Closed | Kapil Solanki
19 | 210964604 | 14-07-2024 08:42 | 125.4 | 4H.8041.../2320187 | Automation Issue Call By Customer Name:-Pawan Karla .. Mobile No:-9910366000 | Task Start | Rush Enterprises | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 41 | Starting issue due to battery was discharge , battery charger mains supply was in OFF condition from customer side , educated the customer about the same | Closed | Kapil Solanki
1 | 210966927 | 15-07-2024 13:50 | 57 | T4.8941.../2320261 | Starting Issue Call By Customer Name :- Ashok Mobile No :- 7678512026 | Task Start | Kalina Overseas Pvt. Ltd. | Vidyut Engineers - Noida | 68 | Starting issue.. Found air lock in fuel line,remove air issue resolved. | Closed | Kapil Solanki
2 | 210966861 | 15-07-2024 13:30 | 125.4 | 4H.8041.../2320055 | Starting Issue Call by Customer Name - Vishvnath ... Number - 9992920383 | Task Start | Pri Oil And Gas Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 135.2 | Ambar lamp on alarm was showing checked DTC but did not found, issue not resolved. (Revisit required.) | Open | Kapil Solanki | Details required
3 | 210966595 | 15-07-2024 12:23 | 15 | GP3.8501.../2420194 | R Phase Under Voltage Alarm issue Call By customer Name :Puneet Sharma No :9058848425 | Task Start | Vasu and Sons. | Espiem Engines & Machines (P) Limited - Agra | 30 | Changeover wiring shorted, No issue in DG. | Closed | Kapil Solanki
4 | 210966563 | 15-07-2024 12:15 | 125.4 | 4H.8041.../2420185 | Smoke Issue Email By-Service Dealer Name:-Saurabh Singh | Task Start | TSL. Electro Power Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 41.53 | Starting issue..SPN/FMI: 2802/4 (Device bat low vlt), found 1C2 wire was in loose condition tighten the same issue resolved.and also White Smoke issue. | Open | Kapil Solanki
5 | 210966122 | 15-07-2024 10:46 | 20 | GP3.8601.../2420076 | Fuel Leakage Issue Email By - Service Dealer Name -Deepjyoti Electricals & Services, CRM | Closed | Mr. Engineering Works | Deep Jyoti Electricals and Services - Haldwani | 26 | Fuel leakage from return line bolt was in loose condition, tighten the same issue resolved. | Closed | Sudhir Awasthi
6 | 210965936 | 15-07-2024 10:16 | 125.4 | 4H.8041.../2420181 | Under Voltage Â Alarm And Centralization Issue Call By Customer Name :-Pradeep Kumar Mobile No :-9928313164 | Open | Sabo Hema Automotive Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 21 | 3031/ 14 , flashed latest cal file and alao tripping issue with showing Under voltage alram, suggested to team Extracted data log and event log. | Open | Gourav Sharma
7 | 210965914 | 15-07-2024 10:16 | 320 | F6.8802.../2420002 | Under Voltage Â Alarm And Centralization Issue Call By Customer Name :-Pradeep Kumar Mobile No :-9928313164 | Open | Sabo Hema Automotive Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 81 | 3031/ 14 , flashed latest cal file and alao tripping issue with showing Under voltage alram, suggested to team Extracted data log and event log. | Open | Gourav Sharma
8 | 210965883 | 15-07-2024 10:04 | 125.4 | 4H.8041.../2420109 | ENGINE NOT TAKING LOAD/JOINT VISIT WITH MKT TEAM AO | Task Start | Crescent Techno Solution S. Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 8 | Line Rejection SR, Yesterday Marketing & Service team was visited site, found customer side printing machice was tripped then, replaced AVR Card (150), but issue not resolved. | Open | Kapil Solanki
9 | 210965881 | 15-07-2024 10:03 | 125.4 | 4H.8041.../2420419 | Engine tripping | Task Start | OVN INDUSTRIES PVT LTD | OVN Industries Private Limited - New Delhi | 1.41 | Line Rejection SR, Emergency stop alarm was activated, checked both emergency switches found 4 pin connector was in loose condition, connected properly issue resolved. | Closed | kapil Solanki | GOEM issue
10 | 210965879 | 15-07-2024 10:03 | 15 | GP3.8501.../2420183 | Red lamp Alarm Issue Message By Customer Name :Neeraj ... No : 9910405113 | Closed | CIPL. Corporate Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 32 | Engineer did not found any issue.. DG running ok. | Closed | Kapil Solanki | KRM check | KRM does not start send mail to the KRM team.
1 | 210966473 | 15-07-2024 11:49 | 750 | DV2.8501.C4../2320016 | Starting Problem and alarm problem Call by : Customer Name : Naveen Contact : 9686508208 | Task Start | Recaero India (P) Ltd., | Surya Power Services - Billekahalli | 26 | ECU protection shutdown alarm popping up during Engine stopping.We taken a trial , during trial no alarms observed.ECU flashed. Site is in observation. | Open | Mr. Prakash S
2 | 210962761 | 13-07-2024 13:00 | 0 | 5H.8901.../2420195 | ITV issue | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | P2111 Throttle valve Jammed Fault. So Throttle valve changed. Problem resolved. | Closed | Mr. Nanda Gopal
3 | 210962643 | 13-07-2024 12:36 | 15 | GP3.8501.../2320019 | Wire Broken Call by : KGD Name :Devi Madam Contact :9892952105 | Cancelled | KPG. Solutions Pvt. Ltd. | Net Work Diesels - Sholinganallur | 2.19 | Customer wants Oil service so | Closed | Mr. Nanda Gopal
4 | 210957724 | 2024-12-07 10:47 | 0 | 5H.8901.../2420044 | ENGINE STARING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 0.43 | Update pending from ASE end. | Open | Mr. Nanda Gopal | engine is shut down at 20% load,found error code 51/1,51/0 error code on the controller, then checked the engine as per the error, checked the Inlet throttle valve input supply found ok.checked the wiring harness found ok.then discussed with koel person and changed the another one inlet throttle valve from stock engine (5H.8901/2420195).then assembled the ITV properly, checked the cable properly connected.then connected the ikonnect tool and clear the fault code .
1 | 210971419 | 16-07-2024 17:30 | 58.5 | T4.8941.../ 2420302 | Silencer issue and Preventive Maintenance Call By Customer Name:- laddu Number:- 9934663577 | Open | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | NA | Visit pending | Open | Prabhakar kumar
2 | 210970487 | 16-07-2024 13:24 | 15 | GP3.8501.../ 2420002 | AMF Panel Starting Issue Call BY Customer Name :- Vimal No :- 8294099711 | Closed | Laxman Choudhary. | Globalline India Services Private Limited - Darbhanga | 113 | voltage issue found loose, mains R-phase wire tighten the same issue resolved. | Closed | Prabhakar kumar
1 | 210970950 | 16-07-2024 15:36 | 625 | DV0.8501.C4../2320019 | DG issue | Task Start | HDFC Bank Limited | G-Care Diesels Private Limited - Ernakulam | 214 | Water Entry in the Canopy. | Open | Mr Sanjaymon
2 | 210969947 | 16-07-2024 11:36 | 0 | 5H.8901.../2420085 | ecu error code | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | update pending at ASE end | Open | Mr. Nanda Gopal
3 | 210968822 | 15-07-2024 18:49 | 30 | 3H.8902.../2320026 | Over Smoke Issue Email By KGD Name:-J Sathish Balaji | Completed | Jayanth Balakrishnan | Bharath Diesel Sales and Service - Palani | 59 | Over smoke issue.Customer shared a black smoke video during starting the dg in the morning. Video attached.Visited the site and observed cracks in suction line pipe, so replaced the same. But the smoke issue is still persist. Today ASE will visit. | Open | Mr. Nanda Gopal
1 | 210969760 | 16-07-2024 11:03 | 750 | DV2.8501.C4../2320013 | Coolant Leakage Issue Email By Service Dealer Name:-Tanmay A Shinde | Closed | Faster Hydraulics Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 135 | The dealer engineer went to the site to change the make-up pipe of the radiator but the customer refused to do this work because the company was open. | Closed | Jagdeep Saini
2 | 210966671 | 15-07-2024 12:46 | 58.5 | T4.8941.../2420269 | FAN BROKEN | Task Start | Omkar Dalvi | Transcreek Engineers Pvt. Ltd. - Wadkhal | 6 | According to ASE, based on detailed inspection, SE found a T-spanner in the radiator body (between fan and radiator), which caused fan failure and damage to the radiator. | Open | Jagdeep Saini | KRM check for run hr. GOEM check | check KRM data and foud genset last run 7 july and installation data 8 july 2024.
1 | 210967782 | 15-07-2024 17:23 | 30 | 3H.8902.../2420065 | Starting Issue Email By Service Dealer Name:-Sonu Rai | Task Start | Sethi Empiumor. | Paluck Technologies Ltd. - Gurgaon | 55 | Customer side panel issue..no issue in DG. | Closed | Kapil Solanki
2 | 210967611 | 15-07-2024 16:49 | 160 | 6H.8475.../2420083 | Alarm issue Call By Customer Name : -Gourv No:-9855056201 | Task Start | ARK Health Care | Saan Royal Power Solutions Private Limited - Zirakpur | 12 | Low DEF level ,top up and educated customer about the same . | Closed | Ved Gupta
1 | 210970345 | 16-07-2024 12:57 | 160 | 6H.8475.../2420025 | Fan bleat broken issue Call by customer Name:-Mustak . No:-9058614379 | Task Start | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 794 | Fan belt was broken, replace the same issue resolved. | Closed | Kapil Solanki
2 | 210970346 | 16-07-2024 12:57 | 500 | DV8.8501.C4../2320017 | Oil leakage issue Call By Customer Name : -Bhave No:-7722070624 | Task Start | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat | 193.23 | Oil coolar puncture.(Need to replaced) | Open | Kapil Solanki | Failed part and cost impact
3 | 210970210 | 16-07-2024 12:40 | 15 | GP3.8501.../2420054 | Starting Issue Email By - Service Dealer Name -SUNITA | Task Start | Mr. Vineet Tyagi | R K Engineers - Meerut | 6.44 | As previously disscussed, Main contractor was burnt, replaced the same issue resolved. | Closed | Kapil Solanki
4 | 210970133 | 16-07-2024 12:18 | 160 | 6H.8475.../2420057 | STARTING ISSUE | Task Start | icici bank | Saan Royal Power Solutions Private Limited - Zirakpur | 1 | Line Rejection SR, E- feed pump relay not installed from Goem end. | Open | Ved Gupta | GOEM issue
5 | 210970123 | 16-07-2024 12:15 | 82.5 | 5H.8901.../2320042 | Starting Issue Email By - Service Dealer Name -SUNITA | Task Start | Swasrik Pesticides Ltd. | R K Engineers - Muzaffarnagar |  | DEF percentage was not showing in display..(640c-E R00), changed controller issue resolved. | Closed | Sudhir Awasthi | Failed part
6 | 210970122 | 16-07-2024 12:14 | 40 | 3H.8951.../2320050 | Starting issue And Silencer issue Call By Customer Name:- Omveer Singh Number:- 7011204885 | Task Start | Chaudhary Generator Service | Vidyut Engineers - Noida | 1550 | spn/FMI: 110/16 , found silencer expension bellow was broken (need to replaced) | open | Kapil Solanki | Failed part
7 | 210970009 | 16-07-2024 11:54 | 500 | DV8.8501.C4../2320036 | Tripping issue Call By Customer Name : -Harish No:-9720331726 | Task Start | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 54.45 | DG was tripping with showing ECU protect alarm, found controller did not off due to battery charger out put direct connect to negative or positive , correct the same and also SPN/FMI: 523528/15, 651/3, 523576/0, 516166/0 clear the DTC issue resolved. | Closed | Kapil Solanki | GOEM issue
8 | 210969957 | 16-07-2024 11:41 | 62.5 | T4.8941.../2320224 | Tripping Issue Call By Customer Name :-Sonu Mobile No :-8607022439 | Task Start | Sat Jinda Kalyan College | M/s OM Diesels Pvt. Ltd. - Rohtak | 23 | Tripping issue.. DG running on Unbalanced load on DG, educated the customer about the same. | Closed | Kapil Solanki
9 | 210969844 | 16-07-2024 11:23 | 30 | 3H.8902.../2420009 | Starting Issue Email By Service Dealer Name:-Saurabh Singh | Task Start | Suraj Auto | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 60 | When DG running on load,then communication fauilure alarm was showing, cheked CAN communication found ok, then checked battery terminal found loose, tighten the same and also SPN/FMI:-7026/5 related to metering unit and 157/3 (rail pressure fault),refitted the both connector issue resolved.kept in underobservation. | Open | Kapil Solanki
10 | 210969823 | 16-07-2024 11:17 | 57 | T4.8941.../2320287 | Automation Issue Call By Customer Name :-Tinku .. Mobile No :-9312835568 | Task Start | Karan Ahlawat | Vidyut Engineers - New Delhi | 1.7 | Customer side panel not working.(Sensing missing) | Closed | Kapil Solanki
11 | 210969822 | 16-07-2024 11:17 | 30 | 3H.8902.../2420428 | Starting issue Call By Customer Name : -Sushanand No:-100769256 | Task Start | Mr. Sucha Nand. | Saan Royal Power Solutions Private Limited - Zirakpur | 3 | SPN/FMI: 2802/4,157/14, 97/5 err code was showing ,checked PRV count found ok, fuel line found ok, then clear the DTC but stil 97/2 fault code is there , then checked Control panel found wrong connections connected, then connected to Mr. sameer sir and he decided change the Control panel. | Open | Ved Gupta | Issue in panel wiring.
12 | 210969663 | 16-07-2024 10:36 | 160 | 6H.8475.../2420031 | AMBR alarm issue Call By Customer Name : Rohit Malik No : 9999637245 | Task Start | Train High Gym | OVN Industries Private Limited - New Delhi | 40.2 | Abnormal sound from loose V belt,tighten the same issue resolved. | Closed | Kapil Solanki | Belt replacement as per new part number
1 | 210972094 | 17-07-2024 07:32 | 58.5 | T4.8941.../2420013 | Red Lamp Issue Call by Customer Name - Ashok Kumar Number - 7703861207 | Closed | Vinod Kumar | Vidyut Engineers - Noida | 138.2 | Starting issue with showing in I konnect ECU ERROR - NO RESPONSE FROM ECU , found XDBK 4 was in loose condition tighten the same issue resolved | Closed | Kapil Solank
2 | 210972110 | 17-07-2024 08:56 | 30 | 3H.8902.../2420015 | Starting Issue Call By Customer Name :-Sandeep Mobile No :-9144690647 | Task Start | Vardhman Wool Store | Vishal Power Systems - PANIPAT | 35 | Starting issue with showing over current alarm , and unbalance load (23A,12A,50A ) Educated the customer about the same. | Closed | Kapil Solank
3 | 210972115 | 17-07-2024 07:33 | 200 | 6H.8435.../2320002 | Fan belt broken issue Call By Customer Name :-Ashutosh Singh Mobile No :-8303786116 | Closed | MM. Polyvinyls Pvt. Ltd. | Vidyut Engineers - Noida | 138.4 | Fan belt was broken , replace the same issue resolved | Closed | Kapil Solank | As per new part number
4 | 210972144 | 17-07-2024 09:21 | 400 | DV8.8542.C4../2420014 | Tripping Issue Call By Customer Name :-Tara Chand Mobile No :-9728993286 | Task Start | Powercam Electricals Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 81 | Customer complained about tripping issue , Engineer did not found any issue , checked event log no alarm showing , Engineer suggest to customer cheke auto panel | Closed | Kapil Solank | KRM check
5 | 210972182 | 17-07-2024 09:41 | 30 | 3H.8902.../2320183 | STARTING ISSUE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Starting issue..SPN/FMI - 157/3 , Air lock issue , air release from HP pipe ,SPN/FMI - 637/5 checked the continutity found ok replace the Crank sensor issue resolved | Closed | Sudhir Awasthi
6 | 210972187 | 17-07-2024 09:45 |  | 3H.8902.../2320179 | STARTING ISSUE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Air lock issue , air release from HP pipe , issue resolved . | Closed | Sudhir Awasthi
7 | 210972235 | 17-07-2024 09:51 | 320 | F6.8802.../2320013 | Alarm issue Call By Customer Name:- Roshanlal Number:- 9672175373 | Task Start | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar | 351 | SPN/FMI - 5419/1 , Checked ITV connector found ok , reset the alarm issue resolved . | Closed | Gourav Sharma
8 | 210972249 | 17-07-2024 10:01 | 57 | T4.8941.../2420107 | Automaton Issue Call By Customer Name :-Dr. Pratibha Kaushal Mobile No :-9891642653 | Task Start | Pratibha Anand & Sons | Vidyut Engineers - Noida | 21.44 | Customer complained about automation issue but no issue in automation , SPN/FMI - 157/14 (DM2) Checked Rail pressure sensor connector found ok ,and tighten the distribution box connection. | Closed | Kapil Solank
9 | 210972437 | 17-07-2024 10:40 | 15 | GP3.8501.../2420101 | Alternator issue & Hunting issue Call By Customer Name : Ramesh ... No:- 9999125737 | Task Start | Ats Building Systems Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 31 | Customer complained about , alternator vibration issue , engineer did not found any issue checked AVM pad bolt found ok, | Closed | Kapil Solank
10 | 210973191 | 17-07-2024 13:24 | 125.4 | 4H.8041.../2320023 | Alarm issue Call By Customer Name :-Amardeep Singh Mobile No :-8595270952 | Task Start | V. Tech International | Paluck Technologies Ltd. - Faridabad | 241 | SPN/FMI - 1761/18,5461/0 Top up the DEF and flashshed latest cal file. | Closed | Kapil Solank
11 | 210973204 | 17-07-2024 13:20 |  | 4H.8041.../2420545 | ITV Faulty | Open | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | ITV fault EDO place (Under GOEM scope) | Open | Sudhir Awasthi
12 | 210973286 | 17-07-2024 13:47 | 30 | 3H.8902.../2420423 | Tripping Issue Call By Customer Name :- Prince ... Mobile No :- 8505819719 | Open | Allied Trade Links Pvt. Lmt. | Paluck Technologies Ltd. - Faridabad | 7 | DG was tripping with showing over current alarm , found DG was running on over load and unbalanced load (12A,20A,49A) Educated the customer about the same . | Closed | Kapil Solank
1 | 210971234 | 16-07-2024 16:43 | 58.5 | T4.8941.../2420391 | LINE REJECTION | Task Start | S R Power Services | Dicksons Engineering Co.Pvt.Ltd. - Aurangabad | 9 | Attend the site, Engine was tripping with fault code- 157/14 and 97/5 reset the PRV count but still come again find abnormal noise from main relay trace the connection find + positive wire slightly loose in xdbk 4 distribution box therefore supply to main relay and xdbk 2 got disturbed sometime and logged the fault code | Closed | Jagdeep Saini
2 | 210964221 | 13-07-2024 18:08 | 20 | GP3.8601.../2420311 | ABNORMAL SOUND | Task Start | Shreemohini Energy | Dicksons Engineering Co.Pvt.Ltd. - Nagpur_MIDC |  | Alternator issue - Alternator will be receive from nidec by 18-07-2024 | Open | Jagdeep Saini
3 | 210966671 | 15-07-2024 12:46 | 58.5 | T4.8941.../2420269 | FAN BROKEN | Task Start | Omkar Dalvi | Transcreek Engineers Pvt. Ltd. - Wadkhal |  | Radiator and fan damaged | Open | Jagdeep Saini
4 | 210971362 | 16-07-2024 17:15 | 30 | 3H.8902.../2420095 | ENGINE NOT START. | Completed | William Automotive Electrical Supplies Private Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 0.85h | RL2 (Main Relay) of 12RB1 relay board was not getting negative from ECU. Engine started after giving negative from RL1. | Open | Jagdeep Saini
5 | 210973266 | 17-07-2024 13:35 | 750 | DV2.8501.C4../2320020 | ECU Ember Issue Call By Customer Name : Harpal Mehada No :9023111868 | Task Start | Comed Chemicals Limited | Unique Techno Services Pvt Ltd. - Baroda | 750h | DEF related Alarm was showing in the panel.1761/15,523584/15 | Open | Amit Sandilya
1 | 210971893 | 16-07-2024 23:04 | 15 | GP3.8501.../2320002 | Under Speed Alarm Call By Customer Name :- Ajay Wadhawan Number :- 9810172765 | Open | Dr. Ajay Wadhawan | Vidyut Engineers - Noida | 43.2 | Starting issue with showing under speed alarm , checked fuel line or control panel wiring found ok , reset the alarm , under observation 2 day | Open | Kapil Solank | KRM check
2 | 210971810 | 16-07-2024 19:57 | 125.4 | 4H.8041.../2420108 | Voltage problem Call by : Customer Name : Sanjy kumar Contact : 8851505464 | Task Start | OM PRAKASH | OVN Industries Private Limited - New Delhi | 11 | Customer side main voltage was (R- 245,Y-244,B-242), There is no voltage fluctuation on the DG side , test on load . | Closed | Kapil Solank
3 | 210971806 | 16-07-2024 19:49 | 125.4 | 4H.8041.../2420110 | Fuel Sensor Issue Call By Customer Name :-Rahul ... Number :-7533807807 | Task Start | K. 6. Enterprises | R K Engineers - Meerut | 91 | KRM Sync issue..erratic reading showing on krm, sent mail communication to KRM team. | Closed | Sudhir Awasthi
4 | 210971796 | 16-07-2024 19:33 | 125.4 | 4H.8041.../2320039 | Battery charging Issue Call By Customer Name :-Prashant Mobile No :-9911093925 | Open | Godrej Properties Ltd. | Paluck Technologies Ltd. - Gurgaon |  | Service due. | cancelled | Kapil Solank
5 | 210971040 | 16-07-2024 16:01 | 250 | F6.8841.../2420033 | Starting Issue Call By OEM Name :- Deepak Mobile No :-7506947475 | Task Start | Kids Clinic India Pvt Ltd | S. R Engines Sales And Service - LUCKNOW |  | No issue at site , SR will be cancel | cancelled |  | KRM check
6 | 210970864 | 16-07-2024 15:16 | 320 | F6.8802.../2320030 | Trip_Genset_Low_Voltage | Open | Atma Autotech Engineers Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | Jerk load on DG, SD team already sent mail communication to customer , SR will be cancel | Cancelled | Kapil Solank
7 | 210970799 | 16-07-2024 14:44 | 125.4 | 4H.8041.../2420198 | Abnormal Sound issue Call By Customer Name:- Laxman Sir Number:- 9871682146 | Task Start | JK GENERATORS | Vidyut Engineers - Noida | 95 | DEF level was low @16% ,Educated the customer about the same , | Closed | Kapil Solank
8 | 210970796 | 16-07-2024 14:44 | 57 | T4.8941.../2420082 | Starting Issue & AMF Panel Issue Call BY Customer Name :- Kuldeep No :- 9555374601 | Task Start | Technocraft Construction Pvt. Ltd. . | Vidyut Engineers - Noida | 8.33 | starting issue with showing in I konnect ECU ERROR - NO RESPONSE FROM ECU , found XDBK 4 distribution box not get 12 volt supply , tighten the XDBK 4 distribution box issue resolved , | Closed | Kapil Solank | Loose connections
9 | 210970636 | 16-07-2024 14:01 | 625 | DV0.8501.C4../2320013 | Starting issue Call by KGD Name:-Sumit Kumar Singh No:-9205138388 | Task Start | Keystone Solutions Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 7.5 | SPN/FMI - 523576/0,4336/2, checked DEF line found ok,checked supply module connector found ok, code still now active (Revisit required) | Open | Kapil Solank | Details requiered
10 | 210970624 | 16-07-2024 14:01 | 125.4 | 4H.8041.../2420075 | Starting Issue Call by Customer Name - Kaif .. Number - 9315745730 | Closed | Mohit Generator Power Solution | Paluck Technologies Ltd. - Ghaziabad | 52.8 | Starting issue due to battery discharge , battery charger main supply missing from customer side , connect the the mains and educated the customer about the same | Closed | Kapil Solank
1 | 210971419 | 16-07-2024 17:30 | 58.5 | T4.8941.../ 2420302 | Silencer issue and Preventive Maintenance Call By Customer Name:- laddu Number:- 9934663577 | Task Start | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 113 | Expansion bellow found damage, order the parts. Today engineer will visit for replacement. | Open | Prabhakar kumar
2 | 210972391 | 17-07-2024 10:33 | 250 | F6.8841.../ 2420002 | Starting Issue Email By- Service Dealer Name:-SOUMITA | Task Start | Maithan Ferrous Pvt. Ltd. | United Machinery Sales And Service - Asansol | 68 | Engineer was not able to connect the I- konnect tool due to updated version. | Open | Prosenjit saha | KRM check | Send mail for fault code data to KRM team.
3 | 210973937 | 17-07-2024 16:51 | 30 | 3H.8902.../ 2420061 | Tripping Issue Call By Customer Name :-Kumar Das Mobile No :-8002872816 | Open | Shyan Engineers | United Machinery Sales And Service - Dhanbad | NA | visit pending. | Open | Prabhakar kumar
120 | 210973475 | 17-07-2024 14:55 | 10 | GP3.1008.../2300002 | Low voltage issue Call By Customer Name :- Mahesh Shetty Mobile No :- 9167518607 | Open | MAHESH SHETTY | Prasad Power Engineers - Karakala | 41 | AVR was tuned to resolved the low voltage issue | closed | Mr. Prakash S
121 | 210973457 | 17-07-2024 14:44 | 0 | GP3.8702.../2420087 | ENGINE HUNTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | pending at ASE end . | open | Mr. Nanda Gopal | DTC Active alarms are showing (EGR valve pos- vlt high, EGR valve malfunction-wa, Injector cylinder 3 flt-open , oil press flt- vlt high).Replaced the oil pressure sensor and removed and refitted ECU injector wiring ). DTC previous alarm showing in i konnect. Cleared the inactive faults in IKonnect.flashed the ECU.Kept under observation.
122 | 210971414 | 16-07-2024 17:30 | 20 | GP3.8601.../2420186 | Canopy Door Problem Call by : Customer Name :Shyam krishna Contact : 9989944336 | Task Start | Syam Krishna Kovelamudi | Ultimate Power Source - Nellore | 4 | Rusting found in canopy door at the time of commissiong , customer inform to sales department . | cancelled |  | GOEM portal issue
123 | 210971073 | 16-07-2024 16:16 | 20 | GP3.8601.../2420280 | CONTROLLER NOT WORKING | Cancelled | Bismillah Educational Trust | Surya Power Services - Bangalore | 1.56 | Wiring issue found in this complaint while attending CC, so cancel the sr where it was open to replace the controller | closed | Mr. Prakash S
124 | 210970950 | 16-07-2024 15:36 | 625 | DV0.8501.C4../2320019 | DG issue | Task Start | HDFC Bank Limited | G-Care Diesels Private Limited - Ernakulam | 214.49 | water entry in canopy through gate bedding | closed | Mr Sanjaymon
125 | 210969947 | 16-07-2024 11:36 | 0 | 5H.8901.../2420085 | ecu error code | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | ECU error code related to ITV , EDO placed for ITV. | open | Mr. Nanda Gopal
126 | 210968822 | 15-07-2024 18:49 | 30 | 3H.8902.../2320026 | Over Smoke Issue Email By KGD Name:-J Sathish Balaji | Task Start | Jayanth Balakrishnan | Bharath Diesel Sales and Service - Palani | 59 | This case handle by HO. Cold start ECU cal file given | open | Mr. Nanda Gopal | Need update
127 | 210966562 | 15-07-2024 12:14 | 0 | 3H.8951.../2420250 | OIL PRESSURE SENSOR FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | They replaced the oil pressure sensor | closed | Mr. Nanda Gopal
128 | 210966531 | 15-07-2024 12:05 | 0 | GP3.8702.../2420201 | OIL PRESSURE SENSOR FAILURE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | They replaced the oil pressure sensor | closed | Mr. Nanda Gopal
1 | 210976086 | 18-07-2024 14:34 | 1000 | DV8.8502.C4../2420003 & 2420003 | CONTACTOR ON PROBLEM. | Completed | Majestique Homes LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 2 | Electric motor of ACB is found faulty need to be replace | Closed | Jagdeep Saini
2 | 210975825 | 18-07-2024 13:16 | 125.4 | 4H.8041.../2420409 | Amber Lamp Alarm issue Call By Â Customer Name :-Yash Mobile No :-9158699967 | Open | Vijay Sales | Transcreek Engineers Pvt. Ltd. - Ambernath |  | Visit pending | Cancelled | Jagdeep Saini | KRM checkj | KRM does not start send mail for KRM start
3 | 210975417 | 18-07-2024 11:48 | 320 | F6.8802.../2320009 | Starting Issue Call By Customer Name :-Mogre Mobile No :-9766616123 | Completed | The Bishops CO-ED. School | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 79 | Low DEF level, after filling issue resolved | Closed | Jagdeep Saini
1 | 210973929 | 17-07-2024 16:53 | 320 | F6.8802.../2320061 | VOC-ENGINE NOT STARTING AND AIR LOCK IN FUEL SYSTEM Customer Name-vipin Customer Number -9667942611 Mode- SR Generated through CDI calling. | Task Start | Rai Indutrial Power Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 40 | Air lock issue..Fuel Return valve not working properly, corrected the same issue resolved. (Kept in under observation.) | Open | Kapil Solanki | KRM. Pressure relief valve from FIP | Before 17 data does not capture and 18 july oil prassure reah to the 10 bar.
2 | 210973354 | 17-07-2024 14:13 | 160 | 6H.8475.../2320016 | Alarm Issue Call By Customer Name :Mohammad Amjad No :8865019331 | Closed | INFRA 13 PVT LTD | Paluck Technologies Ltd. - Ghaziabad | 3 | Customer Complaint about alarm issue..but engineer did not found any issue.. DG running ok. | Closed | Kapil Solanki | KRM check | Check connection of KRM and KRM showin genset trip with genset low voltage.
3 | 210973347 | 17-07-2024 14:13 | 125.4 | 4H.8041.../2420068 | Starting Issue Call By Customer Name :- Omprakash ... Mobile No :- 8587928826 | Closed | A. P. Associates | OVN Industries Private Limited - New Delhi | 1.18 | Low Fuel level, 0 %, guided to customer about the same. | Closed | Kapil Solanki
1 | 210974866 | 18-07-2024 09:32 | 160 | 6H.8475.../2420031 | Starting issue Call By Customer Name : Rohit Malik No:- 9999637245 | Task Start | Train High Gym | OVN Industries Private Limited - New Delhi | 72.4 | Charging alternator mounting bracket bolt was broken& belt broken (Need to replaced) | Open | Kapil Solank | Campaign need to check.
2 | 210974998 | 18-07-2024 10:11 | 82.5 | 5H.8901.../2420058 | Overload Issue Call by Customer Name - Girish Panday Number - 7618539888 | Open | SHREE JASVANT SINGH EDUCATIONAL SOCIETY | Deep Jyoti Electricals and Services - Haldwani |  | SD Team contact to customer ,issue is from customer panel end. | Cancelled | Sudhir Awasthi
3 | 210975202 | 18-07-2024 10:56 | 500 | DV8.8501.C4../2320081 | Display Issue Call By Customer Name :-Rahul Kumar Mobile No :8227001150 | Task Start | Ozone Overseas Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 84 | GUC was blinking ,checked the GCU DC supply found 25 volt , Electrician will visit. | Open | Gourav Sharma
4 | 210975274 | 18-07-2024 11:17 | 40 | 3H.8951.../2320050 | Starting issue And Silencer issue Call By Customer Name:- Omveer Singh Mobile No :- 7011204885 | Task Start | Chaudhary Generator Service | Vidyut Engineers - Noida | 1562.3 | AC MCB was burnt , R phase output voltage was 0 , replace the MCB ,Issue resolved .and silencer bellow was damage need to replace | Closed | Kapil Solank
5 | 210975298 | 18-07-2024 11:20 | 57 | T4.8941.../2320136 | Red Lamp On Alarm Issue Starting Issue Call By Customer Name :-Gaurav Mobile No :-9560654080 | Task Start | G. S. Flexibles. | Paluck Technologies Ltd. - Faridabad |  | Emergency stop alarm was showing or controller did not off (after remove battery connection),(Revisit Required) | Open | Kapil Solank
6 | 210975366 | 18-07-2024 11:33 | 20 | GP3.8601.../2420046 | Staring Issue Call By Customer Name :-Gulshan Mobile No :-9671641745 | Task Start | Arora Agency | Paluck Technologies Ltd. - Gurgaon | 65 | Maintenance due alarm was showing, (Service due) | Closed | Kapil Solank
7 | 210975413 | 18-07-2024 11:48 | 125.4 | 4H.8041.../2420037 | Stopping Issue Call By Customer Name :-Rajiv Mobile No :-7838640263 | Task Start | Karuna Hospital | Vidyut Engineers - New Delhi | 29.45 | Customer side panel issue . Voltage monitoring relay was not working , bypass the relay , DG side no issue | Closed | Kapil Solank
8 | 210975702 | 18-07-2024 12:52 | 250 | F6.8841.../2320044 | Coolant Leakage Issue Email By - Service Dealer Name - ayush vyas | Task Start | Koolking Udhyog Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 171 | (AS previously discussed, coolant leakage from Coolant pipe), SR open for change the pipe. | Closed | Gourav Sharma
9 | 210975726 | 18-07-2024 12:55 | 40 | 3H.8951.../2320061 | Starting issue Call BY Customer Name :- Aashi No :- 9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 405 | SPN/FMI - 636/5 related to cam sensor , found cam sensor connector was open condition , correct the same issue resolved . | Closed | Kapil Solank
10 | 210975839 | 18-07-2024 13:26 | 20 | GP3.8604.../2420195 | INSTANCE ID:-100742015 SITE ID:-I-RJ-SIWW-ENB-G001 CALL BY CUSTOMER// DG ISSUE:-DG fuel ISSUE /LOAD ALARM FAULTY NAME:-Tika Ram NUMBER:-9166665539 | Task Start | Reliance Jio Infocomm Limited | Rajdhani Diesels and Electricals - Barmer |  | Low fuel level alarm, actual 65 litre fuel persent in tank, checked sensor connections then found sometimes red wire was in NC condition. and then checked manually sensor up down, reading was varying after that float was adjust slightly downward,DG runnig ok (need to replaced sensor) | Open | Gourav Sharma
11 | 210975848 | 18-07-2024 13:29 | 30 | 3H.8902.../2420081 | ON Off Switch Fitting issue Call By Â Customer Name :-Balbir Singh Mobile No :-8398822548 | Open | Nav Nirman Contruction Company | Vishal Power Systems - PANIPAT | 4.42 | GCU on /off switch connections was in Loose condition.tighten the same issue resolved. | Closed | Kapil Solank
12 | 210975913 | 18-07-2024 13:46 | 320 | F6.8802.../2320022 | Amber lamp Alarm Issue And Radiator Fan Issue Call By Customer Name :-Arpit Sukla Mobile No :-7217763009 | Open | Vending Updates India P. Ltd. | Vidyut Engineers - Noida | 155.32 | DEF level was low top up the DEF and educated the customer about same. | Closed | Kapil Solank
13 | 210977158 | 18-07-2024 19:09 | 57 | T4.8941.../2320165 | Panel Burn Issue Call by Customer Name - Om .. Number - 9991208949 | Open | Frank Metal Recyclers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | Controller did not turn on, due to controller wiring shoted, (as per engineer observation, R phase & emergency switch wiring shorted. | Open | Kapil Solanki | Mail to qa for control panel part placing
2 | 210976589 | 18-07-2024 16:37 | 20 | GP3.8604.../ 2420047 | MAINS CONTACTOR COIL BURNT | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 32 | coil burnt due to voltage fluctuation | Open | Prabhakar Kumar
3 | 210973937 | 17-07-2024 16:51 | 30 | 3H.8902.../ 2420061 | Tripping Issue Call By Customer Name :-Kumar Das Mobile No :-8002872816 | Open | Shyan Engineers | United Machinery Sales And Service - Dhanbad | 146.58 | False VOC, customer need service visit. | Open | Prabhakar Kumar
4 | 210972391 | 17-07-2024 10:33 | 250 | F6.8841.../ 2420002 | Starting Issue Email By-Service Dealer Name:-SOUMITA | Task Start | Maithan Ferrous Pvt. Ltd. | United Machinery Sales And Service - Asansol | 68 | visit pending. | Open | Prosanjit saha
5 | 210971419 | 16-07-2024 17:30 | 58.5 | T4.8941.../ 2420302 | Silencer issue and Preventive Maintenance Call By Customer Name:- laddu Number:- 9934663577 | Open | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | NA | wrong part delivered. | Open | Prabhakar Kumar
6 | 210976618 | 18-07-2024 16:40 | 20 | GP3.8601.../ 2420013 | Starting issue Call By Customer Name : -Rajesh Kumar No:-7004319589 | Task Start | Mr. Nirmal Jee. | Globalline India Services Private Limited - Sasaram | NA | visit pending. | OPEN | Prabhakar Kumar
1 | 210975350 | 18-07-2024 11:32 | 25 | GP3.8702.../2420038 | Starting Problem ,Battery under voltage Call by : Customer Name : Prabhakar Contact :887715500 | Open | Swiss Garnier Life Sciences | Net Work Diesels - Chennai | 1.4 | Pending at ASE end | Open | Mr. Nanda Gopal
2 | 210975245 | 18-07-2024 11:08 | 250 | F6.8841.../2420045 | Engine Error Code Issue Email By - Service Dealer Name - GURUMURTHY | Task Start | JRC Projects | Surya Power Services - Bommasandra, Bangalore | 4 | 3041 error code shown( Flash protect lamp) , engg. cleared the fault code , engine start running , under observation . | closed | Mr. Prakash S
3 | 210973457 | 17-07-2024 14:44 | 0 | GP3.8702.../2420087 | ENGINE HUNTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Pending at ASE end | open | Mr. Nanda Gopal
4 | 210972413 | 17-07-2024 10:45 | 82.5 | 5H.8901.../2320041 | Error code Email By - Service Dealer Name - Genearth Services, | Task Start | James&co | Genearth Services - Ramanathapuram | 43 | Coolant leak from main radiator to dehydration tank hose.Tightened the clip corrected the same.And taken 1 hr Trial. DG running OK | closed | Mr. Nanda Gopal
1 | 210983423 | 20-07-2024 08:16 | 160 | 6H.8475.../2420068 | DG SET STARTING PROBLEM | Closed | Hotel Surabhi | Unique Techno Services Pvt Ltd. - Gandhidham | 3.3 | fuel suction tube was touching in fuel tank surface and also NRV was faulty. | Closed | Amit Shandilya
2 | 210984840 | 20-07-2024 12:34 | 20 | GP3.8601.../2420050 | Red Lamp On Alarm Issue Call By Customer Name :-Ganesh Vishwakarma Mobile No :-9309114782 | Task Start | Suzanne Merwanji. | Mahalaxmi Diesels - Goa |  | DG running is ok but mains fluctuation is upto 30 V | Open
1 | 210978724 | 19-07-2024 12:57 | 20 | GP3.8604.../ 2420128 | INSTANCE ID-100741923 SITE ID- I-BR-JHJP-ENB-G001 CALL BY COSTUMER- DG ISSUE-STARTING ISSUE NAME-ARJIT NUMBER-7004414641 | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | 20 | SR open for ECU claim under warranty by dealer. | OPEN | Prabhakar Kumar
2 | 210977951 | 19-07-2024 10:12 | 20 | GP3.8604.../ 2420020 | INSTANCE ID:-100740889 SITE ID:-I-BR-KSRI-ENB-G002 CALL BY CUSTOMER\\ DG ISSUE:-DG ISSUE NAME:-RANJAN KUMAR NUMBER:-8102775134 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Motihari | 21 | Fuel low alarm even after 63L fuel, clean 24 no, wire from controller and reconnect it hence the problem resolved. still DG in observation. | OPEN | Prabhakar Kumar
3 | 210976618 | 18-07-2024 16:40 | 20 | GP3.8601.../ 2420013 | Starting issue Call By Customer Name : -Rajesh Kumar No:-7004319589 | Task Start | Mr. Nirmal Jee. | Globalline India Services Private Limited - Sasaram | 1.3 | starting command not received from ECU check wire continuity but not found. | OPEN | Prabhakar Kumar
4 | 210976589 | 18-07-2024 16:37 | 20 | GP3.8604.../ 2420047 | MAINS CONTACTOR COIL BURNT | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 22 | due to under voltage mains contactor got burnt. hence change the contactor. | OPEN | Prabhakar Kumar
5 | 210986333 | 20-07-2024 17:48 | 20 | GP3.8604.../ 2420145 | INSTANCE ID :-100741931 SITE ID :-I-BR-KSCK-ENB-G001 CALL BY CUSTOMER // DG ISSUE :-DG ALRAM ISSUE / NAME :-AMIT KUMAR NUMBER :-9955400859 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | NA | visit pending. | OPEN | Prabhakar Kumar
1 | 210977165 | 18-07-2024 19:14 | 57 | T4.8941.../2320052 | Diesel Leakage Issue Call By Customer Name :-Mohit ... Mobile No :-8901024218 | Task Start | VICTOR INDUSTRIES | OVN Industries Private Limited - New Delhi | 17.7 | Fuel leakage issue.. Due to Return line connector was in Detached Condition, connected the same issue resolved. | Closed | Kapil Solanki
2 | 210976851 | 18-07-2024 17:43 | 15 | GP3.8501.../2420192 | Abnormal Sound Issue Call by Customer Name - Neeraj Agarwal Number - 8218483250 | Open | Neeraj Agarwal | Espiem Engines & Machines (P) Limited - Agra | 3 | Customer Complaint About Abnormal sound , but engineer checked sound with desible meter and found with in limit . | Closed | Sudhir Awasthi
3 | 210976772 | 18-07-2024 17:23 | 40 | 3H.8951.../2420081 | Tripping Issue Call By Customer Name :-Rahul ... Mobile No :- 9953965999 | Task Start | NEW BHARDWAJ ELECTRICAL WORKS | Paluck Technologies Ltd. - Faridabad | 91 | Tripping issue.. Engineer checked event log found Under voltage , Under frequency alarm was showing,due to Overload on DG educated Customer about the same. | Closed | Kapil Solanki
4 | 210976343 | 18-07-2024 15:43 | 82.5 | 5H.8901.../2420097 | Starting Issue Call By Â Customer Name :-Bablu Mobile No :-9716214162 | Closed | Asian Steel Tubes Industries | Paluck Technologies Ltd. - Faridabad | 3.36 | Starting issue due to loose relay connections, tighten the same issue resolved. | Closed | Kapil Solanki | GOEM issue
5 | 210976243 | 18-07-2024 15:17 | 82.5 | 5H.8901.../2320104 | Alarm Issue Call BY Customer Name :- Rahul No :- 8527924499 | Closed | Max Power Solution | Vidyut Engineers - Noida | 118.56 | Low DEF level, top up and educated customer about the same. | Closed | Kapil Solanki
6 | 210976016 | 18-07-2024 14:20 | 125.4 | 4H.8041.../2320151 | Starting Issue Call By Customer Name :- Minakshi .. Mobile No :- 9958808858 | Closed | AK. Partners | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 25 | SPN/FMI: 2802/4 (device battery low voltage ), in DM 1 and 110/0, in DM 2 , clear the DTC .and ventilation issue. | Closed | Kapil Solanki
7 | 210976240 | 18-07-2024 15:17 | 160 | 6H.8475.../2420016 | Starting issue Call By Customer Name : Balram Singh No:-7983511019 | Task Start | Mahalaxmi Crafts & Tisseus Pvt. Ltd. | R K Engineers - Muzaffarnagar | 97 | SPN/FMI: 516166/0, clear the DTC.and also Battery discharged due to mains connections was in loose condition tighten the same issue resolved. | Closed | Sudhir Awasthi
1 | 210980264 | 19-07-2024 16:28 | 57 | T4.8941.../2320023 | Abnormal Sound Issue Message By Customer Name :- Bediji . No :-9310230055 | Task Start | Har Rai Laces P. Ltd. | Paluck Technologies Ltd. - Faridabad |  | Customer did't picked up call.Iniciated for cancellation. | Cancelled | Kapil Solanki
2 | 210980279 | 19-07-2024 16:25 | 20 | GP3.8601.../2320060 | Error Code Issue Call By Customer Name :-vishal . Mobile No :-7988306931 | Open | Vishal Garg | Paluck Technologies Ltd. - Gurgaon | 75 | Maintenance due alarm was showing, reset the alarm issue resolved. | Closed | Kapil Solanki
3 | 210979386 | 19-07-2024 15:03 | 82.5 | 5H.8901.../2420055 | Preventive Maintenance Call By Customer Name :- Sonam Mobile No :- 9821597325 | Open | Perfectio Panacea LLP. | OVN Industries Private Limited - New Delhi |  | SR open Only for Servicing Purpose. | Cancelled | Kapil Solanki
4 | 210979289 | 19-07-2024 14:52 | 1000 | DV8.8502.C4../2420001 & 2420002 | Starting Issue Call by Customer Name - Amandeep Number - 6283342341 | Completed | SRG. Developers & Promoters | SAAN Royal Power Solutions Private Limited - Zirakpur | 66 | Battery positive terminal phyical damaged, replaced the same issue resolved. | Closed | Ved Gupta
5 | 210979245 | 19-07-2024 14:40 | 57 | T4.8941.../2320200 | Tripping Issue Call By Customer Name : Nitin . Mobile No :9818417735 | Task Start | Lemount Garments Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 75 | Tripping issue..Overload and Unbalanced( R,Y,B - 84,48,41 ) load on DG, educated Customer about the same. | Closed | Kapil Solanki
6 | 210979239 | 19-07-2024 14:40 | 57 | T4.8941.../2420561 | Starting Issue Call By Customer Name :- Aman .. Mobile No :- 9599005112 | Completed | SAHIL POWER SYSTEMS | Paluck Technologies Ltd. - Gurgaon | 5 | Starting issue.. Due to loose relay connections , tighten the same issue resolved. | Closed | Kapil Solanki | Goem issue
7 | 210979164 | 19-07-2024 14:23 | 250 | F6.8841.../2320005 | Starting Issue Call By Customer Name:-Vinod Kumar No:-9728005448 | Task Start | ALFA FLEXITUBES ( P ) LTD | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 187 | Starting issue..SPN/FMI:51/5 (Related to throttle valve) checked ITV connector , found connector pins are in bend condition, corrected the same issue resolved and also 516166/0, 1761/16, clear the DTC. | Closed | Kapil Solanki
8 | 210978682 | 19-07-2024 12:45 | 200 | 6H.8435.../2320031 | Alternator issue & Battery Charger Issue Call By Customer Name :-Raghu Ghanawat Mobile No :-8876376908 | Task Start | Oil India Limited | Rajdhani Diesels and Electricals - Jodhpur | 516 | Charging alternator Output issue.. SD team installed old Charging alternator and new one sent to BOSH for further inspection. | Open | Gourav Sharma
9 | 210978540 | 19-07-2024 12:14 | 125.4 | 4H.8041.../2320133 | Under Speed Alarm Issue Call By Customer Name :- Krishna .. Mobile No :- 8899140202 | Completed | Jai Balaji Industries..... | Espiem Engines & Machines (P) Limited - Aligarh | 373 | Air filter and CAC hose pipe was damaged, changed the same . | Closed | Sudhir Awasthi
10 | 210978150 | 19-07-2024 11:01 | 40 | 3H.8951.../2320031 | Under Speed Alarm issue & Over Current Alarm issue Call By Customer Name :-Joginder Kumar Mobile No :-9999930655 | Task Start | Sai Lighting Components | Paluck Technologies Ltd. - Ghaziabad | 10.2 | DG Running on Overload and Unbalanced load, educated Customer about the same. | Closed | Kapil Solanki
11 | 210978105 | 19-07-2024 10:49 | 125.4 | 4H.8041.../2320160 | Di seal lock issue Call By Customer Name : Mukesh .. No:- 7838207077 / 9255891000 | Task Start | CNC. Solutions... | Paluck Technologies Ltd. - Faridabad | 88 | Fuel tank Cap faulty,(Need to change) and also Low DEF level & 5461/0, flashed latest calfile issue resolved. | Open | Kapil Solanki
12 | 210977897 | 19-07-2024 09:46 | 82.5 | 5H.8901.../2420058 | Load Issue Email By-Service Dealer Name:- Deepjyoti Electricals | Task Start | SHREE JASVANT SINGH EDUCATIONAL SOCIETY | Deep Jyoti Electricals and Services - Haldwani | 28.47 | Overload and Unbalanced load (R,Y,B- 24,98,106) 75 KW, educated customer about the same. | Closed | Sudhir Awasthi
13 | 210977723 | 19-07-2024 07:23 | 15 | GP3.8501.../2420190 | Red Lamp On Alarm Call By Customer Name:- Rajiv Sood Number:-9910111991 | Closed | HIMALAYA GENERATORS | Vidyut Engineers - Noida | 13.1 | Customer Complaint about Red lamp alarm issue.. But engineer did not found any issue.. Checked DG on load found ok. | Closed | Kapil Solanki | KRM check
14 | 210980850 | 19-07-2024 18:00 | 15 | GP3.8501.../2420105 | Starting Issue Call By Customer Name :-Vivek Mobile No :-7905326556 | Closed | Tuteja Steel Corporation. | Paluck Technologies Ltd. - Gurgaon | 8.59 | Customer side switch was malfunctioning (No issue in DG) | Closed | Kapil Solanki
15 | 210980792 | 19-07-2024 18:00 | 750 | DV2.8501.C4../2420007 | Canopy panel door lock faulty Email By - KGD Name - Pankaj Jain | Task Start | Vibracoustic India Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Zirakpur | 82 | Door lock Adjustment issue.. Changed the door lock issue resolved. | Closed | Ved Gupta | GOEM issue
1 | 210984939 | 20-07-2024 12:58 | 160 | 6H.8475.../2420025 | Fan bleat broken issue Call by customer Name:-Mustak . No:-9058614379 | Task Start | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 841.12 | Customer Complaint about belt broken, Checked with Tension meter found 120 hz, | Closed | Kapil Solanki
2 | 210984909 | 20-07-2024 12:55 | 57 | T4.8941.../2320065 | Abnormal Sound Issue Call by KGD Name - Gurpreet Kaur Number - 9311523743 | Task Start | PIONEER ENGINEERING & AUTOMOTIVE CORPORATION | Paluck Technologies Ltd. - Faridabad | 355.51 | Abnormal sound from loose V belt, tighten the same issue resolved. | Closed | Kapil Solanki | Strech belt replacement
3 | 210984719 | 20-07-2024 12:08 | 320 | F6.8802.../2320020 | Tripping Â Issue Call By Customer Name :-Ashok Kumar Mobile No :- 9990220264 | Task Start | SSF POLYMERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | TRIPPING ISSUE.. With showing Under frequency, under voltage alarm, then analyze the load upto 105 % load but no tripping observed. Suspected Customer using initialy jerk load. | Closed | Kapil Solanki | KRM check | Check the KRM but does not found the problem only show jark load.
4 | 210984501 | 20-07-2024 11:23 | 500 | DV8.8501.C4../2320033 | Fuel pipe issue Call By Customer Name : -Subhas Sharma No:-9306952708 | Task Start | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 143 | Starting issue.. Suction pipe length was short (Need to replaced) | Open | Kapil Solanki
5 | 210984455 | 20-07-2024 11:09 | 62.5 | T4.8941.../2420257 | Starting Issue Call By Customer Name :- Rajveer Mobile No :- 7428331441 | Closed | M/s .Ace A One Health Care Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 10 | Starting issue..due to low fuel level, 15 %, top up and educated customer about the same. | Closed | Kapil Solanki
6 | 210984431 | 20-07-2024 11:04 | 125.4 | 4H.8041.../2420138 | Starting Issue Email By - Service Dealer Name -Nimishesh Pandey | Task Start | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur | 259 | Low DEF level , top up and educated customer about the same. | Closed | Sudhir Awasthi
7 | 210984334 | 20-07-2024 10:58 | 500 | DV8.8501.C4../2320019 | Automation Issue and Display Issue Call by Customer Name - anmol ... Number - 7015013910 | Open | Real Heights Developer Pvt Ltd. | Vishal Power Systems - PANIPAT | 48 | Auto starting issue..found 49 no wire was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
8 | 210984269 | 20-07-2024 10:41 | 30 | 3H.8902.../2420179 | VISIT | Task Start | Scorpio Petro | OVN Industries Private Limited - New Delhi | 3 | Line Rejection SR,SPN/FMI: 110/0, 110/16, found recovery bottle empty, and checked raditor found almost empty , Top up 5 liter . | Closed | Kapil Solanki | GOEM issue
1 | 210985285 | 20-07-2024 14:25 | 0 | 6H.8475.../2420063 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Update pending from ASE end. | open | Mr. Nanda Gopal | Error code - SPN 4095, FMI 5. Found DEF inlet and outlet connection are interchanged. Corrected the same, issue resolved.
2 | 210985183 | 20-07-2024 13:47 | 40 | 3H.8951.../2420135 | Abnormal sound Email By - Service Dealer Name - CRM G-CARE EKM | Closed | Shijo George. | G-Care Diesels Private Limited - Ernakulam | 26 | Found abnormal sound from exhaust silencer inside .removed silencer and removed metal pieces from silencer inside.(shelter work carrying out). refitting done. | Closed | Mr Sanjaymon
3 | 210984085 | 20-07-2024 10:03 | 58.5 | T4.8941.../2420240 | Auto start problem Email By - Service Dealer Name -Genearth Services | Closed | John Buildwell India Pvt Ltd | Genearth Services - Tirunelveli | 216 | Auto sensing enable in KG 745 . | Closed | Mr. Nanda Gopal
4 | 210977981 | 19-07-2024 10:20 | 125.4 | 4H.8041.../2420337 | DG Sump crack near bolt Email By - Customer Name - Puli Srinivas | Open | AMR. India Limited. | Ultimate Power Source - Ananthapuramu | 113.19 | Sump crack near bolt , sump needs to be change | open | Mr. Saleem
5 | 210977944 | 19-07-2024 10:08 | 125.4 | 4H.8041.../2420262 | Electrical-add blue level not showing in display | Task Start | Standard Surfa Chem India Private Limited. | Bharath Diesel Sales and Service - Pattanur | 1 | Wrong VOC. VOC - Engine not starting.Visited the site and found ECU is not overriding. Found Loose connection in the wiring. Corrected the same issue resolved. | Closed | Mr. Nanda Gopal
6 | 210977906 | 19-07-2024 09:51 | 20 | GP3.8601.../2420110 | Red lamp alaram problem Call by : Customer Name : Guruvayur Contact : 9705714089 | Task Start | M/s. Guruvayur Sri Krishna Mandiram Trust | Powerlinks Infra Tech Pvt Ltd - Uppal | 1.2 | Emergency button pressed , released the same issue resloved. | Closed | Mr. Saleem
7 | 210977136 | 18-07-2024 18:43 | 25 | GP3.8702.../2420113 | Engine starting problem | Open | N. Murali Rao | Laxmi Diesels - Visakhapatnam | LR | Wiring issue in panel , Water in fuel, fault code shown on panel , XBD2 found in faulty condition . After this ASE plan to visit the site , due to heavy rain next visit pending | open | Mr. Saleem
8 | 210976924 | 18-07-2024 17:59 | 40 | 3H.8951.../2420114 | Starting Problem Call by : Customer Name : Manohar Contact : 7893151851 | Closed | Dr. Reddys Foundation | Laxmi Diesels - Srikakulam | 22 | Battery voltage found low . Recharging after refitted the battery start and observed the dg it's running found ok. | Closed | Mr. Saleem
9 | 210975350 | 18-07-2024 11:32 | 25 | GP3.8702.../2420038 | Starting Problem ,Battery under voltage Call by : Customer Name : Prabhakar Contact :887715500 | Completed | Swiss Garnier Life Sciences | Net Work Diesels - Chennai | 1.4 | .During inspection found controller ON,OFF switch was loose in condition. So Recorrect the switch and tighted properly and started and tested the engine. Running time battery was not charging condition because Charging alternator fuse was failure condition . So temporary connect the fuse , link wire was fitted properly and checked the all engine systems, found ok. Started and tested the engine DG running performance is satisfied charging circuit was working normal So advice the customer fuse needs to be replace | open | Mr. Nanda Gopal
10 | 210973457 | 17-07-2024 14:44 | 0 | GP3.8702.../2420087 | ENGINE HUNTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Pending at ASE end | open | Mr. Nanda Gopal | Alarms showing in controller - EGR valve pos- vlt high, EGR valve malfunction-wa, Injector cylinder 3 flt-open , oil press flt- vlt high.So , Replaced oil pressure sensor. Removed and refitted the injector wiring Cleared the fault codes. Engine running OK.
1 | 210987025 | 20-07-2024 23:14 | 750 | DV2.8501.C4../2420006 | ECU Error Code Issue Call By Customer Name :- Manish No :- 9811891788 | Open | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida | 1207 | SPN/FMI: 1761/16 was showing ,customer already top up DEF , clear the DTC and flashed dummy file. | Closed | Kapil Solanki
2 | 210986662 | 20-07-2024 20:01 | 125.4 | 4H.8041.../2320114 | White Smoke Issue Call By: Customer Name :Joganver Singh No :9911146716 | Open | NEW GAGAN GENERATOR.. | Vidyut Engineers - New Delhi |  | Rental genset tolly mounted ,customer has moved to different location, ( Faridabaad), INICIATED FOR Cancellation.. | Cancelled | Kapil Solanki
3 | 210986490 | 20-07-2024 18:29 | 500 | DV8.8501.C4../2320061 | Starting Issue Call By Customer Name :- Kishan Mobile No :- 7906268082 | Task Start | Goodworth Electronics Private Limited | Vidyut Engineers - Noida | 64.25 | Starting issue.. Interface box fuse was blown out, changed the same issue resolved. | Closed | Kapil Solanki
4 | 210986307 | 20-07-2024 17:46 | 160 | 6H.8475.../2420020 | Maintenance Due Alarm Issue Call By Customer Name :-Chandan Kumar Mobile No :-9560354412 | Open | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad |  | SR open for only Servicing purpose. | Cancelled | Kapil Solanki
5 | 210986152 | 20-07-2024 17:08 | 250 | F6.8841.../2320038 | Voltage Problem Email By - Service Dealer Name -Saurabh Singh | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 114 | Unlanaced load on DG , balanced the load issue resolved and educated customer about the same. | Closed | Kapil Solanki
6 | 210986038 | 20-07-2024 16:49 |  | DV8.8501.C4../2420115 | . | Task Start | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Starting issue.., checked air and fuel line found ok. checked all sensor supply and changed ECU but issue not resolved. | Open | Gourav Sharma
7 | 210985893 | 20-07-2024 16:20 | 125.4 | 4H.8041.../2420238 | Error code Issue Call By Service Dealer Name :-Mohit Mobile No :- 7027820044 | Task Start | OMKAR ENTERPRISES | M/s OM Diesels Pvt. Ltd. - Sonipat | 23.31 | SPN/FMI: 1761/16, Low DEF level, top up and educated customer about the same. | Closed | Kapil Solanki
8 | 210985840 | 20-07-2024 16:12 | 125.4 | 4H.8041.../2320160 | Diesel tank lock issue Email By - Customer Name - Mukesh | Task Start | CNC. Solutions... | Paluck Technologies Ltd. - Faridabad | 89 | Fuel tank cap faulty.. (need to replaced) EDO placed. | Open | Kapil Solanki
9 | 210985812 | 20-07-2024 16:10 | 125.4 | 4H.8041.../2420051 | Abnormal Sound Issue Call By Customer Name :-Ajay Kumar Mobile No :-8287778015 | Open | RURBAN INTERCORP LLP | Paluck Technologies Ltd. - Ghaziabad |  | Low Fuel level, educated customer on call, Iniciated for Cancellation. | Cancelled | Kapil Solanki
10 | 210985641 | 20-07-2024 15:36 | 320 | F6.8802.../2420048 | Under Voltage Issue Call By Service Dealer Name :-Ramesh Sharma Mobile No :-9599006443 | Closed | AG. Contractor & Erectors | Paluck Technologies Ltd. - Faridabad | 3.29 | Tripping issue..with showing Under voltage alarm found,DG supply wiring on controller was in loose condition,corrected the same issue resolved. | Closed | Kapil Solanki
11 | 210985234 | 20-07-2024 14:14 | 30 | 3H.8902.../2320089 | Diesel leakage issue Call By Customer Name :- Pushkar Mobile No :- 8448982807 | Task Start | HITECH INKJET PVT LTD | Paluck Technologies Ltd. - Ghaziabad | 184 | Fuel leakage from fuel return line (bolt loose), tighten the same issue resolved. | Closed | Kapil Solanki
12 | 210985075 | 20-07-2024 13:23 | 20 | GP3.8601.../2420068 | ENGINE NOT TAKING LOAD Email By - OEM Name - Pawan Sahni | Task Start | Charanjeet. | Vidyut Engineers - Noida | 63.14 | Neutral wiring in the panel not fitted properly,due to which valtage was fluctuate, corrected the same issue resolved. | Closed | Kapil Solanki
1 | 210990708 | 21-07-2024 19:34 | 40 | 3H.8951.../2320010 | Smoke Pipe Broken Issue Call By Customer Name:- RAVINDRA SIR Number:8168752914 | Open | Ganpati Enterprises | Vishal Power Systems - Karnal | 67 | Expension bellow was broken,As per engineer observation, alignement issue, changed the same issue resolved. | Closed | Kapil Solanki
2 | 210990666 | 21-07-2024 17:42 | 57 | T4.8941.../2320052 | Diesel Leakage Issue Call By Customer Name :-Mohit ... Mobile No :-8901024218 | Task Start | VICTOR INDUSTRIES | OVN Industries Private Limited - New Delhi |  | Visit pending | Open | Kapil Solanki
3 | 210990603 | 21-07-2024 16:09 | 500 | DV8.8501.C4../2320057 | Starting issue call by customer Name :-Rajesh kumar Number :-9675192005 | Task Start | M/S MEHROTRA CONSUMER PRODUCTS PRIVATE LIMITED | Vidyut Engineers - Noida | 71.36 | Low DEF level, educated customer about the same issue resolved. | Closed | Kapil Solanki
4 | 210990178 | 21-07-2024 14:05 | 15 | GP3.8501.../2420010 | Starting issue call by customer Name :-Satish kumar Number :-9518843316 | Open | Bharat X Ray and Ultra Sound Clinic. | Vishal Power Systems - Karnal | 49 | Starting issue….Battery was discharged , battery charger connected suspected battery faulty sent to TGY for for further inspection. | Open | Kapil Solanki
5 | 210990009 | 21-07-2024 14:00 | 40 | 3H.8951.../2420080 | Tripping issue Call By Customer Name: Rajat Number:8901510059 | Open | PRM. Property Consultant | M/s OM Diesels Pvt. Ltd. - Rohtak | 57 | Tripping issue..Emergency stop alarm was showing, checked 4 pin connector found connections loose, tighten and connected properly issue resolved. | Closed | Kapil Solanki
6 | 210989542 | 21-07-2024 12:45 | 10 | GP3.8301.../2420023 | Power Supply issue Call By Customer Name: Multani Number:9878403031 | Open | Karamveer Singh Sodhi | Dynamic Engineering Services - Jalandhar |  | Customer side Changeover issue ,no issue in DG. | Closed | Ved Gupta
7 | 210988872 | 21-07-2024 10:15 | 20 | GP3.8601.../2420025 | Under speed issue call by customer Name :-R.k Skangal Number :-9811768600 | Task Start | Aviral Sangal Huf. | Vidyut Engineers - Noida | 25.91 | Sometimes DG was tripping with showing Under speed alarm, checked fuel line found ok, reset the alarm issue resolved. | Closed | Kapil Solanki
8 | 210988867 | 21-07-2024 10:07 | 250 | F6.8841.../2320019 | Tripping Issue Call By customer Name - Narendra Nagar Mo No-9811818373 | Closed | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 248 | Customer complaint about tripping issuee..checked event log found over current alarm, then checked load found ok.no issue observed. | Closed | Kapil Solanki
9 | 210987821 | 21-07-2024 06:31 | 200 | 6H.8435.../2320030 | Stopping Issue Call By Customer Name:-Monika No:-8851404360 | Task Start | Usis Infra Solution | Vidyut Engineers - Noida | 12.58 | Customer side panel issue..(Sensing missing), educated customer about the same. | Closed | Kapil Solanki
1 | 210972391 | 17-07-2024 10:33 | 250 | F6.8841.../ 2420002 | Starting Issue Email By-Service Dealer Name:-SOUMITA | Task Start | Maithan Ferrous Pvt. Ltd. | United Machinery Sales And Service - Asansol | 70 | Engineer cleared the DTC(SPN- 5461 , FMI- 0) and then flashed the ECU , problem was resolved but the final root cause was not found. | OPEN | Prosanjit saha
2 | 210976618 | 18-07-2024 16:40 | 20 | GP3.8601.../ 2420013 | Starting issue Call By Customer Name : -Rajesh Kumar No:-7004319589 | Task Start | Mr. Nirmal Jee. | Globalline India Services Private Limited - Sasaram | 1.3 | Guide the enginner to check the wiring and all electrical systems, found OK, today engineer will visit to check fuel rack. | OPEN | Prabhakar Kumar
3 | 210986333 | 20-07-2024 17:48 | 20 | GP3.8604.../ 2420145 | INSTANCE ID :-100741931 SITE ID :-I-BR-KSCK-ENB-G001 CALL BY CUSTOMER // DG ISSUE :-DG ALRAM ISSUE / NAME :-AMIT KUMAR NUMBER :-9955400859 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | NA | visit pending. | OPEN | Prabhakar Kumar
1 | 210985184 | 20-07-2024 13:48 | 200 | 6H.8435.../2420015 | FAN SIDE ABNORMAL SOUND | Task Start | JAKSON & COMPANY | Sahyadri Diesels - Silvassa |  | SD attend the site , as per goem there is sound from radiator fan but no issue observed with this to engineer radiator fan is also ok , taken load trail. | Closed | Amit Shandilya
2 | 210970843 | 16-07-2024 15:04 | 15 | GP3.8501.../2420225 | Engine starter does not work. | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | Starter not Operating, EDO part will be close | Closed | Jagdeep Saini
3 | 210967705 | 15-07-2024 17:07 | 0 | GP3.8301.../2420116 | Engine trip by low oil pressure | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | connect Mechanical oil pressure gauge on engine & Start engine observed oil pressure not builtup in gauge & trip engine.observed no oil in gallery so need to dismental engine for checking oil pump. | open | Jagdeep Saini
4 | 210984461 | 20-07-2024 11:08 | 82.5 | 5H.8901.../2420077 | ENVIRONMENTAL TEMPERA | Closed | Policy X. Com. | Natraj Power Tech - Indore |  | Ambient temp. sensor missing Fitted the same and clr the fault code no issue found, issue resolved. | Closed | Vijay Patil | GOEM issues
5 | 210970929 | 16-07-2024 15:32 | 0 | GP3.8501.../2420102 | STARTING ISSUE | Task Start | JAKSON & COMPANY | Sahyadri Diesels - Silvassa |  | Oil pressure doesn’t build in oil gallery checked by mech. Gauge remove filter no oil found.Engine refer to Kagal Plant. | open | Amit Shandilya
6 | 210993442 | 22-07-2024 15:17 | 82.5 | 5H.8901.../2320044 | RPM dropping issue observed at the time of load applied on engine at 25%,50% and 75% | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | Defence application so that I konnect can not be connect. | Open | Jagdeep Saini | Details required
7 | 210993017 | 22-07-2024 13:58 | 750 | DV2.8501.C4../2320021 | Coolant Leakage Issue Call By Customer Name :-Tejas Bhire Mobile No :-8329369201 | Completed | Bobst India Private Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  |  | Open | Jagdeep Saini
8 | 210991392 | 22-07-2024 11:34 | 25 | GP3.8702.../2420012 | line rejection | Task Start | ICICI Bank | Transcreek Engineers Pvt. Ltd. - Wadkhal |  | SD attend site found VMR faulty Replace the same , issue resolved | Closed | Jagdeep Saini
9 | 210993511 | 22-07-2024 15:28 | 20 | GP3.1021.../2420011 | fuel gauge faulty | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 5.9 | Low fuel level alarm was showing but fuel level was proper in tank. | Closed | Amit Shandilya
10 | 210993509 | 22-07-2024 15:26 | 20 | GP3.1021.../2420191 | fuel gauge faulty | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 22 | Low fuel level alarm was showing but fuel level was proper in tank. | Closed | Amit Shandilya
11 | 210976086 | 18-07-2024 14:34 | 500-2 | DV8.8502.C4../2420003 | CONTACTOR ON PROBLEM. | Completed | Majestique Homes LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 2 | 523576/0,Diesel Exhaust fluid dosing Interrupted. | Completed | Jagdeep Saini | Under observation
1 | 210993299 | 22-07-2024 14:42 | 0 | 6H.8435.../2420027 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | GOEM - Visit pending. | open | Mr. Nanda Gopal | Air lock issue. Issue Resolved.
2 | 210991097 | 22-07-2024 10:05 | 58.5 | T4.8941.../2420397 | .. | Task Start | UMESH SHETTY | Surya Power Services - Peenya, Bangalore | LR | ECU found faulty.EDO placed. | open | Mr. Prakash S
3 | 210991025 | 22-07-2024 09:46 | 30 | 3H.8902.../2420104 | OVER CRACKING | Completed | S. N. J. Traders | Bharath Diesel Sales and Service - Palani | 1 | DG is cranking more than 3 times. Checked the cranking parameters in GCU, Found normal. Then checked the relays, start relay found in stuked condition so removed the same and refitted. Engine running OK. | Closed | Mr. Nanda Gopal
4 | 210977136 | 18-07-2024 18:43 | 25 | GP3.8702.../2420113 | Engine starting problem | Open | N. Murali Rao | Laxmi Diesels - Visakhapatnam | LR | Wiring issue. Water in fuel alarm is showing. Found XDBK2 wiring is not as per wiring diagram, so corrected the same but issue remains same. Co-ordinated with GOEM for Power panel and ECU replacement. Power panel recieved. Today ASE will visit again. | open | Mr. Saleem
1 | 210972391 | 17-07-2024 10:33 | 250 | F6.8841.../ 2420002 | Starting Issue Email By-Service Dealer Name:-SOUMITA | Task Start | Maithan Ferrous Pvt. Ltd. | United Machinery Sales And Service - Asansol | 70 | Engineer cleared the DTC(SPN- 5461 , FMI- 0) and then flashed the ECU , problem was resolved but the final root cause was not found. | CLOSED | Prosanjit saha
2 | 210986333 | 20-07-2024 17:48 | 20 | GP3.8604.../ 2420145 | INSTANCE ID :-100741931 SITE ID :-I-BR-KSCK-ENB-G001 CALL BY CUSTOMER // DG ISSUE :-DG ALRAM ISSUE / NAME :-AMIT KUMAR NUMBER :-9955400859 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | NA | visit pending. | OPEN | Prabhakar Kumar
1 | 210992985 | 22-07-2024 13:50 | 82.5 | 5H.8901.../2320093 | Maintenance Due Alram Issue Call By Customer Name :-Sumit Mongia Mobile No :-9818430800 | Open | GENERAL AUTOMOTIVES COMPONENTS | Paluck Technologies Ltd. - Gurgaon |  | SPN/FMI: 1761/16, (Low DEF level) , Maintenance due alarm was showing,clear the DTC issue resolved. | Closed | Kapil Solanki
2 | 210991673 | 22-07-2024 12:22 | 500 | DV8.8501.C4../2320075 | Over Heating Issue Call By Customer Name :-Amrit Kumar Mobile No :-9268431760 | Task Start | C.E. INFO SYSTEMS LIMITED | Vidyut Engineers - New Delhi | 27.4 | Overheating issue.. Ventilation is not proper.(Hot air recirculated). And also turbo red hot issue... | Closed | Kapil Solanki
3 | 210991551 | 22-07-2024 11:59 | 82.5 | 5H.8901.../2320034 | Starting Problem Call by : Customer Name : Prashant Agarwal Contact : 9900990941 | Task Start | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 260 | Battery was discharged due to battery charger was not connected to mains supply..connected the same and also battery water level low, top up the same issue resolved. | Closed | Kapil Solanki
4 | 210991513 | 22-07-2024 11:55 |  | GP3.8501.../2320012 | STARTING ISSUE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 15 | Line Rejection SR, FIP rack stuck, then manually moved, clean the same and refitted issue resolved. | Closed | Sudhir Awasthi
5 | 210991527 | 22-07-2024 11:46 |  | GP3.8501.../2320014 | STARTING ISSUE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 1.3 | Line Rejection SR, FIP rack stuck, after that manually move it, then clean and refitted the same issue resolved. | Closed | Sudhir Awasthi
6 | 210991479 | 22-07-2024 11:42 | 200 | 6H.8435.../2320033 | Amber Lamp ALarm Issue Call By Customer Name :- Sudeep .. Mobile No :- 9811549751 | Task Start | Bal Bharati Public School | OVN Industries Private Limited - New Delhi | 39.52 | Low DEF level @48%, top up and educated customer about the same. | Closed | Kapil Solanki
7 | 210991394 | 22-07-2024 11:41 | 57 | T4.8941.../2420110 | ENGINE OIL SEAL FAULTY Email By Service Dealer Name:-SUNITA | Task Start | K-6 ENTERPRISES | R K Engineers - Meerut |  | As previously discussed, Oil leakage from timing plate. Today the engineer changed the oil seal issue resolved. | Closed | Sudhir Awasthi
8 | 210991442 | 22-07-2024 11:25 | 15 | GP3.8501.../2420194 | R Phase Under Voltage Alarm issue Call By customer Name :Puneet Sharma No :9058848425 | Task Start | Vasu and Sons. | Espiem Engines & Machines (P) Limited - Agra | 31 | Tripping issue..R phase Under voltage alarm was showing, then checked R phase Voltage found 170 V , after that adjust the AVR voltage 220, but issue not resolved.After sometimes , Customer agin call and said Over voltage alarm was showing suspected AVR faulty , today technicial will visit site again. | open | Sudhir Awasthi | KRM check
9 | 210991209 | 22-07-2024 10:45 | 125.4 | 4H.8041.../2420192 | Amber lamp Alarm Issue Call By Customer Name :-Sanjiv . Mobile No :-9560302292 | Task Start | CRESCENT TECHNO SOLUTIONS PRIVATE LIMITED | Vidyut Engineers - Noida | 38.11 | SPN/FMI: 1761/16 and 51/6 (related to ITV), checked ITV connector found ok. Clear the DTC issue resolved. | Closed | Kapil Solanki
10 | 210991193 | 22-07-2024 10:38 | 40 | 3H.8951.../2320093 | currant issue Call by KGD NAME Pradeep Bhati Number: 9911316001 | Task Start | Leather & Packaging Machinery Corporation | Vidyut Engineers - Noida | 12.51 | Alternator issue.. Checked terminal voltage found phase to neutral 320 V, sent mail communication to the mac alte team. | open | Kapil Solanki
11 | 210991177 | 22-07-2024 10:32 | 40 | 3H.8951.../2320050 | Starting issue And Silencer issue Call By Customer Name:- Omveer Singh Mobile No :- 7011204885 | Closed | Chaudhary Generator Service | Vidyut Engineers - Noida | 1587 | Rental Customer, Battery was discharged, battery charger was not connected, fitted stand by battery. | Closed | Kapil Solanki
12 | 210994551 | 22-07-2024 19:45 | 25 | GP3.8702.../2420048 | Emergency Stop Alarm and Starting Issue Call By Customer Name :-Keshav Mobile No :-9654019499 | Completed | Jitender Kumar | Paluck Technologies Ltd. - Gurgaon | 162 | Tripping issue..with showing Emergency stop alarm, checked and found Canopy emergency switch connection was in loose condition, tighten and refitted the same issue resolved. | Closed | Kapil Solanki
13 | 210994496 | 22-07-2024 18:36 | 250 | F6.8841.../2420014 | Power Supply issue Call By Customer Name :-Vishal Jain Mobile No :-9650684788 | Task Start | Crown Buildhome LLP. | OVN Industries Private Limited - New Delhi | 44 | Customer side changeover issue no issue in DG. | Closed | Kapil Solanki
14 | 210994387 | 22-07-2024 18:17 | 160 | 6H.8475.../2420024 | Oil Leakge issue Call By Service Dealer Name :- Ramesh Mobile No :- 9911266168 | Task Start | Tool Room Engineers LLP | Paluck Technologies Ltd. - Faridabad | 73 | Oil leakage issue from loose oil filter, tighten the same issue resolved. | Closed | Kapil Solanki
15 | 210994343 | 22-07-2024 18:06 | 500 | DV8.8501.C4../2420043 | Amber Lamp Alarm Issue Call By Customer Name :- Rakesh No ;- 9816194371 | Task Start | Nikvin Healthcare India Pvt. Ltd. | SAAN Royal Power Solutions Private Limited - Baddi | 22 | SPN/FMI: 516166/0, clear the DTC and educated customer about the same. | Closed | Ved Gupta
16 | 210993856 | 22-07-2024 16:33 | 125.4 | 4H.8041.../2320037 | Starting Issue Call By Customer Name :-Vipin Mobile No :-9810077547 | Task Start | MAHNA LEATHERS PVT. LTD. | Vidyut Engineers - Noida | 49.28 | SPN/FMI: 3031/14 flashed the latest cal file and also 110/0, 110/16, 4095/1 (interruption of dosing related) checked dosing module and pipe connections found ok clear the DTC. | Closed | Kapil Solanki | KRM check
17 | 210993516 | 22-07-2024 15:30 | 57 | T4.8941.../2420122 | Starting Issue Call By Customer Name :-Zuber .. Mobile No :-6377321912 | Task Start | Bansal Children Hospital | Pratap Diesels Pvt. Ltd. - Bhiwadi | 96 | Water in fuel alarm was showing , checked sensor connector found moisture then clean and refited the same and also Unbalanced load on DG educated customer for balance load. | Closed | Gourav Sharma | DTC check
18 | 210993378 | 22-07-2024 15:03 | 750 | DV2.8501.C4../2420011 | Under Voltage Â Alarm Issue Call By Customer Name :- Parvesh Kumar Mobile No :- 9720093797 | Task Start | Sleek Brake Products | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 464 | Tripping issue..checked event log found Under voltage alarm, then checked DG on load 1 hour no issue observed.DG was running in OK condition. | Closed | Kapil Solanki | KRM check | Genset stop with low fuel,low speed and low voltage alarm.
1 | 210995472 | 23-07-2024 10:49 | 58.5 | T4.8941.../2420471 | ... | Task Start | Siri Malle Infra Developers | Surya Power Services - Billekahalli | LR | Today ASE is visiting. | open | Mr. Prakash S
2 | 210995465 | 23-07-2024 10:47 | 25 | GP3.8702.../2320004 | Starting Issue Email By Service Dealer Name:-G-Care Diesels | Task Start | Muhammed Binnu | G-Care Diesels Private Limited - Calicut | 10 | Customer postponed the visit for today. Today Engineer will visit. | open | Mr Sanjaymon | 1. Error codes - 157/14 , 56166/0 , 97/5 Which are related to High pressure fuel line restriction, ECU internal failure and water in fuel sensor.Checked and found no any abnormality. 2.Manual mode the start delay is 3 seconds. In auto mode the start delay is 5 seconds. Customer wanted to reduce the start delay in auto mode to 3 seconds. so done the same.
3 | 210995045 | 23-07-2024 09:21 | 40 | 3H.8951.../2420128 | Starting Problem Call by : Customer Name : Vishnu Sir Contact : 9633499305 | Task Start | Pramod Nair | EMKAY MOTORS - Kollam | 1 | Main supply input is not given to battery charger. | Closed | Mr Sanjaymon
4 | 210994521 | 22-07-2024 19:27 | 20 | GP3.8601.../2420128 | AMF panel problem Call by : Customer Name : Srinadh Contact : 9700448320 | Task Start | Addanki Jayakavitha. | Ultimate Power Source - Nellore | 2 | Customer want to remotly operate the DG in manual & auto mode , | Closed | Mr. Saleem
1 | 210993514 | 22-07-2024 15:30 | 20 | GP3.1021.../2420005 | llop sensor not working | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 5 | Genset trip due to low lube oil pressure alarm. | Closed | Amit Shandilya
2 | 210995085 | 23-07-2024 09:00 | 20 | GP3.1021.../2420084 | DG not start in auto mode | Task Start | Reliance Jio Infocomm Limited | Mahalaxmi Diesels - Kankavali |  | Supercapacitor lost the 48V constant supply from there system therfore fail to start in auto mode | Closed | Jagdeep Saini
3 | 210995971 | 23-07-2024 12:20 | 20 | GP3.1021.../2420089 | ERROR CODE | Task Start | Reliance Jio Infocomm Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati |  | Error code showing in conroller for high ECU voltage, Low LOP | open | Jagdeep Saini
1 | 210996072 | 23-07-2024 12:44 | 625 | DV0.8501.C4../2320025 | Starting Issue Call By Â Customer Name :-Rinku .. Mobile No :-7652060148 | Task Start | Keystone Solutions Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 6.2 | SPN/FMI: 4336/2 and 523576/0 checked DEF line (SM TO DM ) Dosing module faulty EDO placed. (all mention in PIR) | open | Kapil Solanki | KRM check | KRM shown 4389/2 fault code.
2 | 210996070 | 23-07-2024 12:44 | 625 | DV0.8501.C4../2320013 | Starting Issue Call By Â Customer Name :-Rinku .. Mobile No :-7652060148 | Task Start | Keystone Solutions Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 10.5 | SPN/FMI: 4336/2 and 523576/0 checked DEF line (SM TO DM ) Dosing module faulty EDO placed. (all mention in PIR) | open | Kapil Solanki | KRM check | KRM shown 4358/3,4411/3,4442/5,523591/7,523531/7,4376/5 fault code.
3 | 210995947 | 23-07-2024 12:15 | 20 | GP3.8601.../2420170 | Starting Issue Call By Customer Name :- Devendra singh Sodi Mobile No :- 9810938926 | Open | Devendra Singh Sodi | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 7 | Battery charger input connection was in loose condition , tighten the same issue resolved. | Closed | Kapil Solanki
4 | 210995940 | 23-07-2024 12:15 | 40 | 3H.8951.../2320093 | ALTERNATER ISSUE Call By Â Customer Name :-Rajeshwar Mobile No :-9871276774 | Open | Leather & Packaging Machinery Corporation | Vidyut Engineers - Noida |  | SR open for joint visit with alternator supllier , found aternator faulty, checed earthing and terminal connections found ok and also checked near by electrical equipent (site photographs uploaded in drive) | open | Kapil Solanki
5 | 210995885 | 23-07-2024 12:01 | 500 | DV8.8501.C4../2420003 | Urea Load Issue Call By Customer Name :-Rakesh Kumar Yadav Mobile No 9631113946 | Task Start | Leighton India Contractors Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 119 | SM 2 backflow line was chocked , clean the pipe with hot air issue resolved. | Closed | Kapil Solanki
6 | 210995203 | 23-07-2024 09:58 | 125.4 | 4H.8041.../2320002 | TRIPPING Issue Call By Â Customer Name :-Shokendra Mobile No :-7428316306 | Task Start | Accord Automation Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 138 | Starting issue..Battery was discharged due to battery charger input connection was in loose condition, tighten the same and starting issue resolved. But after sometimes , DG was tripping with showing R,Y,B phase Under voltage alarm, checked terminal voltage L to L found 6 Volt and checked found Exictor and Roter winding damaged.(need to replaced) | open | Kapil Solanki
7 | 210995060 | 23-07-2024 08:06 | 500 | DV8.8501.C4../2320009 | Trip_Genset_Low_Voltage | Task Start | Leighton India Contractors Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 43 | KRM Generated SR,engineer visited site but no isssue observed., | Closed | Kapil Solanki | KRM check | Due to low genset does not achive then speed so controller popup low fuel with genset low voltage.
1 | 210986333 | 20-07-2024 17:48 | 20 | GP3.8604.../ 2420145 | INSTANCE ID :-100741931 SITE ID :-I-BR-KSCK-ENB-G001 CALL BY CUSTOMER // DG ISSUE :-DG ALRAM ISSUE / NAME :-AMIT KUMAR NUMBER :-9955400859 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | 64 | Customer panel issue running hours and other parameters is not displaying in panel hence customer suspect that its is a issue of BMS ,check the connections but no fault found. Hence plan a joint visit . | OPEN | Prabhakar Kumar
1 | 210998983 | 23-07-2024 20:32 | 15 | GP3.8501.../2420194 | Starting issue And High Voltage issue Call By Customer Name :- Puneet Sharma Number :- 9058848425 | Task Start | Vasu and Sons. | Espiem Engines & Machines (P) Limited - Agra | 32 | AVR faulty, changed the AVR issue resolved. | Closed | Sudhir Awasthi
2 | 210998756 | 23-07-2024 18:04 | 82.5 | 5H.8901.../2320005 | Panel Issue Call By Customer Name :-Mahesh Sharma Mobile No :-9817876322 | Task Start | Noxon Blowers Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Customer panel side contractor not holding, change the same by customer. no issue in DG. | Closed | Kapil Solanki
3 | 210998313 | 23-07-2024 16:35 | 57 | T4.8941.../2320023 | sound issue Call By Customer Name :- Sujit Kumar Mobile No :- 8368916449 | Closed | Har Rai Laces P. Ltd. | Paluck Technologies Ltd. - Faridabad | 285 | Abnormal sound from loose V belt , changed the belt issue resolved.(T.4 43801) | Closed | Kapil Solanki
4 | 210996781 | 23-07-2024 15:33 | 125.4 | 4H.8041.../2420423 | Starting Issue Call By Customer Name:-Suraj Jha No:-6205804058 | Task Start | Nexus Technosystems Pvt. Ltd. | Vidyut Engineers - Noida | 57.33 | Auto starting issue..( DG was in manual mode), educated customer about the same. | Closed | Kapil Solanki
5 | 210996569 | 23-07-2024 14:55 | 40 | 3H.8951.../2420005 | DG ISSUE | Closed | BHARTI AIRTEL LIMITED | Vidyut Engineers - Noida | 36.54 | Emergency stop alarm was activated, found Canopy emergency switch connection was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
6 | 210996557 | 23-07-2024 14:47 | 320 | F6.8802.../2320021 | ECU Issue Call By Â Customer Name :-Lovkush . Mobile No :-8739904306 | Closed | Marvel Ceramics Pvt Ltd | Pratap Diesels Pvt. Ltd. - Alwar | 301 | SPN/FMI: 3031/14, flashed latest cal file. | Closed | Gourav Sharma
7 | 210996576 | 23-07-2024 14:45 | 15 | GP3.8501.../2420190 | Red Lamp On Alarm Email By - Service Dealer Name -Shiv | Closed | HIMALAYA GENERATORS | Vidyut Engineers - Noida | 15.6 | SPN/FMI: 970/5, ( emergency stop alarm was activated) found 4 pin connector was not fitted properly, connected the same reset the alarm issue resolved. | Closed | Kapil Solanki
8 | 210996511 | 23-07-2024 14:31 | 320 | F6.8802.../2420012 | Red Lamp Alaram Issue Call by Customer Name - srikant . Number - 9466034034 | Task Start | Ralson Paint | Vishal Power Systems - Karnal | 51 | SPN/FMI: 3031/14, flashing latest cal file issue resolved. | Closed | Kapil Solanki
9 | 210996351 | 23-07-2024 13:46 | 15 | GP3.8501.../2320025 | Starting Issue Call By Customer Name :- Vikas Mishra Mobile No :- 8081328477 | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | SAM Engineering corporation - Varanasi Cantt. | 54.3 | Starting issue..FIP faulty, Fuel was not delevired, today koel team will visit site. | Open | Sudhir Awasthi
10 | 210996262 | 23-07-2024 13:20 | 58.5 | T4.8941.../2420591 | Under Speed Alarm Issue Call By Customer Name :-Ashwani Mobile No :-9310057666 | Task Start | Nidhi Enterprises. | Paluck Technologies Ltd. - Faridabad | 17 | Tripping issue..with showing under speed alarm was showing, found jerk load on DG. Educated customer for applied load gradually . Application- Customer using pressing machine for make Auto parts. | Closed | Kapil Solanki
11 | 210996260 | 23-07-2024 13:20 | 125.4 | 4H.8041.../2420041 | Starting Issue Call By Customer Name :- Prashant Mobile No :- 9911093925 | Completed | Godrej Properties Ltd. | Paluck Technologies Ltd. - Gurgaon | 1304 | ECU propect lamp alarm was showing , found Battery +ve terminal was in loose condition ,tighten the same issue resolved. | Closed | Kapil Solanki | KRM
12 | 210995746 | 23-07-2024 11:34 | 62.5 | T4.8941.../2320246 | Starting Issue Email By Service Dealer Name:- Devender Yadav | Closed | Arora Nursing Home | Paluck Technologies Ltd. - Gurgaon | 38 | SPN/FMI: 97/2 (Water in fuel), alarm was showing checked and found water in tank, customer clean the tank by himself ,clear the DTC and also water in fuel sensor connector O ring missing . | Closed | Kapil Solanki | KRM | check KRM and found it the 97/2 fault code .
13 | 210995667 | 23-07-2024 11:24 | 30 | 3H.8902.../2320183 | CRANCK SENSOR FAULTY | Open | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Visit Pending. | Open | Sudhir Awasthi
14 | 210995660 | 23-07-2024 11:20 | 125.4 | 4H.8041.../2420132 | Tripping Issue Call By Â Service Dealer Name :-Prince Mobile No :-7722070624 | Task Start | Gravolite India Private Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 70 | DG running on over load and Unbalanced load, educated customer and balance the load. DG running ok. | Closed | Kapil Solanki | KRM check | KRM does not capture like overload but show the low power factor somer time reach 0.43.
15 | 210995604 | 23-07-2024 11:11 | 160 | 6H.8475.../2320004 | Starting Issue Email By Service Dealer Name:-Priya Dogra | Closed | JK. Constructions | Suraj Motor Store - kathua | 247 | Tripping issue.. Emergency alarm was activated checked and found 4 pin connector was in loose condition, connected properly issue resolved and also 1761/16, 3031/14 alarm was showing, flashed latest cal file issue resolved. | Closed | Ved Gupta
16 | 210995416 | 23-07-2024 10:40 | 250 | F6.8841.../2420041 | Display Issue & Door Lock Issue Call BY Customer Name :- Arvind No :- 9814526130 | Closed | DASHMEHS BUILDERS | SAAN Royal Power Solutions Private Limited - Zirakpur | 31 | Battery was discharged, battery charger was not connected to mains supply..connected the same issue resolved. | Closed | Ved Gupta
17 | 210995274 | 23-07-2024 10:20 | 160 | 6H.8475.../2320036 | Aid Blue issue Call By Customer Name : Rajiv Gupta No:- 9871151722 | Task Start | VICTOR INDUSTRIES | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 26.48 | Low DEF level, top up and educated customer about the same. | Closed | Kapil Solanki
18 | 210995266 | 23-07-2024 10:17 | 320 | F6.8802.../2420029 | Starting Issue Email By - Service Dealer Name -PREETI OZA | Task Start | Citi Developers | SAAN Royal Power Solutions Private Limited - Zirakpur | 11 | SPN/FMI: 97/5 (Water in fuel) alarm was showing, water found in fuel tank, suggested to customer to clean the tank by himself. | Closed | Ved Gupta | CAL file need to update
1 | 211001497 | 24-07-2024 13:53 | 82.5 | 5H.8901.../2320076 | Tripping Issue Call By Customer Name :-AJIT Singh Mobile No :-7568387586 | Task Start | Sandhu Construction | Vishal Power Systems - Karnal | 1002 | Sometimes DG was tripping with showing Emergency stop alarm, checked the panel wiring connections found ok, and checked emergency switch connection found ok, then negative supply was provided on emergency switch. | Closed | Kapil Solanki
3 | 211001316 | 24-07-2024 13:07 | 250 | F6.8841.../2320046 | Low coolant Pressure Issue Email By Customer Name:-Sobha Limited | Task Start | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 24 | recovery bottle coolant was below H mark, that’s why customer open the SR. | Closed | Kapil Solanki
4 | 211001253 | 24-07-2024 12:59 | 15 | GP3.8501.../2420172 | Noise Problem Email By KGD Name:- SUKOON FARMS | Task Start | SAHIL POWER SYSTEMS | Paluck Technologies Ltd. - Faridabad | 8 | Abnormal sound issue…SD team enable to find, so today SD team will visit site | Open | Kapil Solanki
5 | 211001226 | 24-07-2024 12:53 | 15 | GP3.8501.../2420192 | Sound Issue Call BY Customer Name :- Neeraj No :- 8218483250 | Open | Neeraj Agarwal | Espiem Engines & Machines (P) Limited - Agra | 10 | Customer complaint about sound issue..but there was no such type of issue.. | Closed | Sudhir Awasthi
6 | 211000198 | 24-07-2024 12:02 | 200 | 6H.8435.../2320023 | Emergency stop alarm Issue Call By Â Customer Name :-Rohit Mobile No :-7017202883 | Task Start | Maxwel Exporters | R K Engineers - Meerut | 70 | Emergency stop alarm was showing, found emergency switch 4 pin connector connections was in loose condition,connected external wire to resolved this issue. | Closed | Sudhir Awasthi
7 | 211000092 | 24-07-2024 11:49 | 82.5 | 5H.8901.../2320084 | Red Lamp Alarm Issue Call By Customer Name :Sahil Rana No :7300651325 | Task Start | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi |  | SPN/FMI: 4094/1, 3364/8 related to DEF qualitiy, found DEF concentration was 24.75% (need to checked with Refractometer) | Open | Kapil Solanki
8 | 211000088 | 24-07-2024 11:49 | 320 | F6.8802.../2320028 | Over Heatting Issue Call By Customer Name :- Sourav Tiyagi Mobile No :- 9690706146 | Task Start | Arocon rainbow | Paluck Technologies Ltd. - Ghaziabad | 91 | Customer complaint about overheating issue.. Engineer visited site found Canopy Emergency switch was in pressed condition, release the switch issue resolved. | Closed | Kapil Solanki | Krm check | Check the KRM but does not show any type of overheating.
9 | 211000084 | 24-07-2024 11:49 | 57 | T4.8941.../2320251 | Display Issue Call By Customer Name :-Gopal ... Mobile No :-9910000376 | Task Start | Neev Real Estate Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 69 | Erratic reading showing on display..(fuel reading was varying ), fuel sensor connector was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
10 | 210999928 | 24-07-2024 11:29 | 320 | F6.8802.../2320031 | ENGINE TURBO ISSUE Email By Service Dealer Name:-SUNITA | Task Start | Sanspareils Greenlands Pvt. Ltd. | R K Engineers - Meerut | 329 | Tripping issue.. Under speed alam, checked event log found high coolant temp alarm was there, found radiator chocked, clean the same with pressurised water, then perform the load trail but under speed alarm was till there, during load trail observed, charge air leakge from intake mainfold, remove intake mainfold found gasket was in damaged condition, changed the gasket issue resolved. | Closed | Sudhir Awasthi
11 | 210999936 | 24-07-2024 11:28 | 500 | DV8.8501.C4../2320036 | Generator lockout Alarm Call By Customer Name : Harish . NO : 9720331726 | Task Start | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 57.21 | Starting issue.. With Showing ECU protect lamp alarm, found reley fuse was blown out.changed the same issue resolved. | Closed | Kapil Solanki
12 | 210999823 | 24-07-2024 11:02 | 250 | F6.8841.../2320038 | Automation issue Call by customer Name:- Tej Pratap Singh No:- 7428506588 | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 119 | Automation issue.. Auto connection was not fitted by Kala genset. | Closed | Kapil Solanki
13 | 210999819 | 24-07-2024 11:02 | 250 | F6.8841.../2420004 | Automation issue Call by customer Name:- Tej Pratap Singh No:- 7428506588 | Task Start | TATA TELESERVICES LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 117 | Automation issue.. Auto connection was not fitted by Kala genset. | Closed | Kapil Solanki
14 | 210999816 | 24-07-2024 11:02 | 20 | GP3.8601.../2420001 | Tripping Issue Call By Customer Name:Vikas Gupta Number:9992461642 | Open | Siya Ram Store | Vishal Power Systems - PANIPAT | 72 | MCB was tripped, due to customer side panel short circuit, corrected the same issueresolved. | Closed | Kapil Solanki
15 | 210999700 | 24-07-2024 10:49 |  | GP3.8702.../2420295 | SENSOR ISSUE | Task Start | IEC BARWALA | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Line Rejection SR, Cam sensor faulty, | Open | Ved Gupta
16 | 210999657 | 24-07-2024 10:38 | 500 | DV8.8501.C4../2320033 | Fuel pipe issue Call By Customer Name : -Subhas Sharma No:-9306952708 | Open | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | Suction pipe length was short,(SR open on GOEM portal) | Cancelled | Kapil Solanki
17 | 210999589 | 24-07-2024 10:25 | 125.4 | 4H.8041.../2420263 | Starting Issue Call By Â Customer Name :-Adesh Mobile No :-9810054089 | Task Start | Adworld Graphics Private Limited | OVN Industries Private Limited - New Delhi | 2.31 | Starting issue.. Suction pipe bolt was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
18 | 210999454 | 24-07-2024 09:52 | 25 | GP3.8702.../2420081 | Starting Issue Call By KGD Name :-PRADEEP Mobile No :-9812716452 | Task Start | Devico International | Vishal Power Systems - PANIPAT | 19 | Auto starting issue.. Found 11 no wire was in loose condition ,tighten the same issue resolved. | Closed | Kapil Solanki
19 | 210999383 | 24-07-2024 08:41 | 125.4 | 4H.8041.../2320054 | Maintenance Due Alarm Call By Customer Name :-Rajesh Ram Mobile No :-9953102701 | Task Start | THERMADYNE PVT. LTD. | Paluck Technologies Ltd. - Faridabad |  | Low DEF level, educated customer on Call ,iniciated for Cancellation. | Cancelled | Kapil Solanki
1 | 210999827 | 24-07-2024 11:02 | 250 | F6.8841.../2320041 | ALARM PROBLEM Call by : Customer Name : Rajasekar Contact : 9003313323 | Completed | ST. Marys Hospital | Bharath Diesel Sales and Service - Salem | 13.1 | Low DEF level alarm. | Closed | Mr. Nanda Gopal
2 | 210995472 | 23-07-2024 10:49 | 58.5 | T4.8941.../2420471 | ... | Task Start | Siri Malle Infra Developers | Surya Power Services - Billekahalli | LR | Update pending at ASE end. | Open | Mr. Prakash S | Updated direct to HO by ASE
3 | 211001747 | 24-07-2024 14:51 | 160 | 6H.8475.../2420111 | Error Code Issue Email By Service Dealer Name:-Jasna N P | Open | KVR. Autocars | Welcare Engineering And Services Pvt. Ltd. - Podikundu | 2 | Error codes - 4358/2 &4095/1 ( related to DEF contamination) are active . DEF quality is OK . So flashed the ECU. Issue resolved. | Closed | Mr Sanjaymon | Corrected
1 | 211006613 | 25-07-2024 14:01 | 15 | GP3.8501.../2420119 | Starting Problem Email By - Service Dealer Name -B.kalyani | Task Start | N. P. R. Filling Station | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 10 | DG is in normal condition , issue found at customer end . | Closed | Mr. Saleem
1 | 211007182 | 25-07-2024 16:13 | 58.5 | T4.8941.../ 2420302 | Exaution Fan Broken issue Call By Customer Name :Aman Singh No:8210415074 | Task Start | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 126 | False VOC, exhaust bello broken, set the new bello & resolved the problem. | CLOSED | Prabhakar Kumar | Under observation
1 | 211003732 | 24-07-2024 20:01 | 500 | DV8.8501.C4../2320080 | ECU Error Alarm issue Call By Customer Name :- Deepak Maheshwari M. Number :- 9990371133 | Closed | Hindustan Infra Power Pvt. Ltd.. | Paluck Technologies Ltd. - Ghaziabad | 61 | Low DEF level @ 42% in Bank A , top up DEF and educated customer about the same. | Closed | Kapil Solanki
2 | 211003650 | 24-07-2024 18:40 | 62.5 | T4.8941.../2320168 | Starting Issue Call By Customer Name :-Himanshu Bhartdhwaj Mobile No :-9315511033 | Open | Dr. Rakesh Nathani | Paluck Technologies Ltd. - Gurgaon |  | Visit Pending. | open | Kapil Solanki
3 | 211002748 | 24-07-2024 17:35 | 30 | 3H.8902.../2320064 | Display Issue Email By-Customer Name:-Anil Kumar | Task Start | BALWAN SERVICE STATION | OVN Industries Private Limited - New Delhi | 6.4 | Customer want to know how to check Fuel consumption % in GCU,guided customer there is no such type of provision, and also KRM activation issue..contact to KRM team and activate the KRM issue resolved. | Closed | Kapil Solanki
4 | 211002653 | 24-07-2024 17:28 | 62.5 | T4.8941.../2420057 | Starting Issue call by customer name : Pankaj .. No. 8685991155 | Task Start | Shri Krishna Agro Fresh Mushroom Farm | M/s OM Diesels Pvt. Ltd. - Sonipat | 78 | Tripping issue.. B phase Over voltage alarm was showing checked terminal plate and found sparking produced of Y phase due to loose stud bolt, | Closed | Kapil Solanki
5 | 211002634 | 24-07-2024 17:18 | 57 | T4.8941.../2320121 | Trip_Genset_Low_Voltage | Task Start | Hind Chemisales. | Pratap Diesels Pvt. Ltd. - Alwar | 201 | KRM Generated SR, R phase Under voltage alarm was showing, Alternator output voltage not produced, checked and found AVR neutral sensing separate from lugs , replaced the same and issue resolved. | Closed | Gourav Sharma
6 | 211002392 | 24-07-2024 16:44 | 125.4 | 4H.8041.../2320086 | Oil leakage Issue Email By-Service Dealer Name:-Madan Chhimpa | Task Start | Total Construction | Paluck Technologies Ltd. - Gurgaon |  | EDO placed for Cable Gland Assembly. | open | Kapil Solanki
7 | 211002203 | 24-07-2024 16:17 | 82.5 | 5H.8901.../2320093 | Amber Lamp Alarm issue Call By Customer Name :-Sumit Mongia Mobile No :-9818430800 | Task Start | GENERAL AUTOMOTIVES COMPONENTS | Paluck Technologies Ltd. - Gurgaon | 269 | Customer complaint about Amber lamp alarm issue.. But engineer checked DG on load but no abnormality found . DG running ok. | Closed | Kapil Solanki | KRM check | Hot shut down alarm
8 | 211002024 | 24-07-2024 15:50 | 62.5 | T4.8941.../2320098 | Belt broken Issue Email By Service Dealer Name:-Madan Chhimpa | Task Start | S K Generators | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 417 | Belt was broken , customer purchase local market belt, and replaced by itself, engineer reached at site and found again belt was broken,due to additional washer, then replaced with new one issue resolved. | Closed | Kapil Solanki | Belt tension
1 | 211005254 | 25-07-2024 08:32 | 500 | DV8.8501.C4../2420006 | Auto Starting Issue Call By Customer Name:-Rakesh Kumar No:-8307129537 | Task Start | Pundrik Solvent | Vishal Power Systems - Karnal | 4.25 | Customer complaint about reduce cooling down period from 3 min to 1 or 2 min, educated customer for the same.. | Closed | Kapil Solanki
2 | 211005255 | 25-07-2024 08:33 | 25 | GP3.8702.../2420066 | Starting Issue Call By Â Customer Name :-Vikas Mobile No :-9991400055 | Task Start | Vikas Kataria. | Vishal Power Systems - PANIPAT | 20 | Battery was discharge , mains supply was missing from customer side , connect the same issue resolved | Closed | Kapil Solanki
3 | 211005625 | 25-07-2024 10:56 | 15 | GP3.8501.../2420028 | RR ASEMBLY AND DIORD TO BE CHANGE | Task Start | BHARTI AIRTEL LIMITED | Vidyut Engineers - New Delhi | 194.42 | Line rejection SR , DG was tripping with showing under voltage alarm ,output voltage was 0 , found RRA assembly was faulty ( doide faulty), changed the same issue resolved. | Closed | Kapil Solanki | KRM check. Event log | KRM does not observed under voltage only showing low fuel level alarm.
4 | 211005651 | 25-07-2024 10:55 | 125.4 | 4H.8041.../2420017 | Indicator Lamp Issue Call BY Customer Name :- Archit No :- 9837122533 | Task Start | Modern Process House | R K Engineers - Meerut | 63 | SPN/FMI - 5461/0 flashed latest cal file. | Closed | Sudhir Awasthi
6 | 211005815 | 25-07-2024 11:33 | 125.4 | 4H.8041.../2420041 | Starting Issue Email By-Service Dealer Name:-Saurabh Rajput | Task Start | Godrej Properties Ltd. | Paluck Technologies Ltd. - Gurgaon | 1309 | Starting issue with showing ECU PROTECT alarm, SPN/FMI - 4095/2,4095/1 checked dosing module found chocked, clean the same but issue not reslved.( Revisit Required) | Open | Kapil Solanki | KRM check | Check KRM found it multiple fault code popup related to inducement like 4095/1,4095/2,4339/2,516166/0,520528/0 3031/14.
7 | 211005912 | 25-07-2024 11:58 | 40 | 3H.8951.../2320031 | Under Speed Alarm Issue Call By Customer Name :-Jogender Mobile No :-9811262581 | Task Start | Sai Lighting Components | Paluck Technologies Ltd. - Ghaziabad | 181 | Customer complained about under speed alarm , engineer did not found any issue . Checked fuel line and air line found ok , | Closed | Kapil Solanki | KRM check | Check KRM but does not showing any problem in KRM.
8 | 211006092 | 25-07-2024 12:11 | 40 | 3H.8951.../2320076 | Automation Issue Call By: Customer Name : Gurdeep Singh No :7503779670 | Task Start | PANDA INTERNATIONAL PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 275 | DG was not started in auto mode due to customer select manual mode , educated the customer about the same issue resolved . | Closed | Kapil Solanki
9 | 211006163 | 25-07-2024 12:24 | 30 | 3H.8902.../2320185 | Hunting issue Call By Customer Name :- KP Sharma Mobile No :- 9910841145 | Task Start | SR. Power Engineers | Vidyut Engineers - New Delhi | 11 | DG Was running unbalance load and unstable load , educated the customer about the same . | Closed | Kapil Solanki
10 | 211006164 | 25-07-2024 12:24 | 320 | F6.8802.../2320080 | Display Issue Preventive Maintenance Call By Customer Name:-Sukhendu Chakrawati No:-8116916333 | Task Start | Jagdamba Optics Pvt. Ltd. | Vidyut Engineers - Noida | 240 | Customer complained about display issue but no issue found , customer want to know how to check fuel level , Educated customer about the same, And rain guard was not fitted . | Closed | Kapil Solanki
11 | 211006243 | 25-07-2024 12:39 | 57 | T4.8941.../2320206 | Diesel Meter Issue Call BY Customer Name :- Aashi No :- 9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 78.5 | Wrong fuel level showing , 100 % fuel level was showing .but actually 77% fuel was in the tank . checked sensor connector and resistance found ok .then remove the sensor and refitted the same issue resolved . | Closed | Kapil Solanki | Under observation
12 | 211006319 | 25-07-2024 12:59 | 125.4 | 4H.8041.../2420158 | Door Locking Issue Call By Â Customer Name :-Sanjay Dubey Mobile No :-9899510580 | Task Start | Trimco Group Delhi Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 50 | Door lock adjustment issue.. adjust the same issue resolved. | Closed | Kapil Solanki
13 | 211006368 | 25-07-2024 13:06 | 30 | 3H.8902.../2320062 | Preventive Maintenance Call By Customer Name :- Sumankant Mobile No :- 9634778306 | Task Start | Buddha Engicon Private Limited | Paluck Technologies Ltd. - Ghaziabad | 71 | Service done (Sent mail communication to SD team for claim to be reject) | Closed | Kapil Solanki
14 | 211006428 | 25-07-2024 13:18 | 125.4 | 4H.8041.../2420181 | Tripping Issue Call By Customer Name:-Pradeep Kumar No:-9928313164 | Task Start | Sabo Hema Automotive Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | visit pending(Men Power Issue) | Open |  | Update pending
15 | 211006565 | 25-07-2024 13:41 | 160 | 6H.8475.../2320030 | Coolant Leakage Issue Call By Customer Name :-Rabbani. Mobile No :-9015201975 | Open | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 131 | Coolant leakage from radiator top tank . Tighten the Clamp issue resolved . | Closed | Kapil Solanki
1 | 211007065 | 25-07-2024 15:50 | 40 | 3H.8951.../2420160 | voltage prome | Task Start | Mohammad Sayeed Shaikh | Transcreek Engineers Pvt. Ltd. - Boisar | 2.4 | Alterntor output voltage is too low, Check AVR all the fuse found ok, replace the AVR issue resolved | Closed | Jagdep Saini
2 | 211005896 | 25-07-2024 11:48 | 500 | DV8.8501.C4../2320092 | Starting Issue Call By Customer Name :-Sandeep Sir Mobile No :-7875770737 | Closed | Madhuban Trade Steel Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 28 | 25 amp fuse burn in interfacebox replace the same issue resolved Is there circular to replace 25 amp fuse with 30 amp? | Closed | Jagdep Saini
3 | 211006324 | 25-07-2024 13:05 | 30 | 3H.8902.../2320086 | starting issue | Task Start | JAKSON & COMPANY | Sahyadri Diesels - Silvassa | 52 | Battery voltage low so after replaced it with the another battery and 1C2 wire was loose Problem solved. | Closed | Amit Shandilya
211006159
5 | 211003774 | 24-07-2024 21:39 | 400 | DV8.8542.C4../2320002 | Battery and Canopy Issue Call By Customer Name :-Navnath Mobile No :-7304928174 | Open | HINDUSTAN UNILIVER LTD | Transcreek Engineers Pvt. Ltd. - Mumbai |  | GOEM issue canopy leakage. | Closed | Jagdep Saini | Goem issues
1 | 211008009 | 25-07-2024 20:18 | 62.5 | T4.8941.../2420119 | Trip_Genset_High_Voltage | Open | Jain Garments | M/s OM Diesels Pvt. Ltd. - HISAR |  | KRM Generated SR, as per customer voice unbalance load on DG, customer balanced load itself. . Initiated for Cancellation. | cancelled | Kapil Solanki
2 | 211007757 | 25-07-2024 17:54 | 320 | F6.8802.../2320013 | Under Voltage Alarm Issue Call By Customer Name:- Roshanlal Number:- 9672175373 | Open | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar | 363 | SPN/FMI: 5419/1( related to throttle valve) and air leaking issue.. Intake manifold gasket was damaged, (Need to Replaced) | open | Kapil Solanki
1 | 211007657 | 25-07-2024 17:34 | 40 | 3H.8951.../2420125 | Red Lamp Issue Call by Customer Name - Girish .. Number - 6260891135 | Open | I.F.T. Health Care LLP. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | Low Fuel level , educated customer on Call. | Cancelled | Gourav Sharma
4 | 211007499 | 25-07-2024 17:08 | 200 | 6H.8435.../2420003 | Oil leakage Issue Call By Customer Name :Mohammad Amjad No :8865019331 | Open | UPPAL CHADHA HI-TECH DEVELOPERS [P] LTD | Paluck Technologies Ltd. - Ghaziabad | 46 | Oil leakage from loose oil filter, tighten the same issue resolved. | closed | Kapil Solanki | need photographs
5 | 211007467 | 25-07-2024 17:05 | 82.5 | 5H.8901.../2320006 | EMERGENCY SWITCH ALARM PROBLEM Email By Service Dealer Name:-SANDEEP | Task Start | M. K. Textiles | Vishal Power Systems - PANIPAT | 7.2 | Canopy emergency switch was in pressed condition, release the switch issue resolved. | closed | Kapil Solanki
6 | 211007008 | 25-07-2024 15:36 | 20 | GP3.8601.../2420025 | Starting Issue Email By-Service Dealer Name:-Shiv | Closed | Aviral Sangal Huf. | Vidyut Engineers - Noida | 27 | customer repoted DG tripping issue.. Team visited checked event log found, emergency and under speed tripping , checked for emergency alarm checked switch connections and as wel as canopy harness found no abnormality till, then tighten all the lugs and connector, for under speed tripping checked mpu minar iron partical on in mpu , clean the same and also updated ECU calevaration,there after perform 1 to 2 hour load trail, found DG running ok. | closed | Kapil Solanki | Need to campare wirh CPCB2
7 | 211006964 | 25-07-2024 15:30 | 20 | GP3.8601.../2320003 | Automation Issue And Power Suplay Issue Call By Customer Name :-Mayank . Mobile No :-9580623696 | Closed | SPA. Yoga Private Limited | Vidyut Engineers - Noida | 37.1 | Customer complaint about automation issue..and select manual mode, educated customer about the same. | closed | Kapil Solanki
8 | 211006947 | 25-07-2024 15:26 | 57 | T4.8941.../2420455 | Starting Issue & Stopping Issue Email By Service Dealer Name:-Kaushik | Open | Meerut Ptfe Products Pvt. Ltd | R K Engineers - Meerut |  | Wrong complaint logged by Customer, intiated for Cancellation. | Cancelled | Sudhir Awasthi
9 | 211006943 | 25-07-2024 15:25 | 320 | F6.8802.../2320006 | Trip_Genset_Low_Voltage | Open | Super Seal India Ltd. | Paluck Technologies Ltd. - Faridabad |  | KRM Generated SR, as per customer voice no issue in DG. Initiated for Cancellation. | Cancelled | Kapil Solanki | KRM check
10 | 211006647 | 25-07-2024 14:13 | 625 | DV0.8501.C4../2420007 | Starting Issue & Urea Leakage Issue Call BY Customer Name :- Sagar No :- 8077553635 | Task Start | S M BROTHERS | R K Engineers - Saharanpur | 64.5 | Starting issue.. Found Interface box 25 Amp fuse was blown out, changed the same issue resolved. | closed | Sudhir Awasthi
11 | 211006660 | 25-07-2024 14:13 | 57 | T4.8941.../2420135 | Starting Issue Call By Customer Name :-Bablu Mobile No :-9958778186 | Task Start | Baba Generator Services | M/s OM Diesels Pvt. Ltd. - Sonipat | 48.1 | SPN/FMI: 110/0, 102/4 ( related to Intake Air pressure fault),checked and found,Intake air pressure sensor connector pin was not proper fitted, corrected the same issue resolved. | closed | Kapil Solanki
12 | 211006424 | 25-07-2024 13:18 | 125.4 | 4H.8041.../2420345 | Automation Issue Call By Customer Name :- Madanlal Mobile No :- 9876264562 | Completed | Secret Heart Convent School | Megatron Engineers - Amritsar | 16 | Customer side mains phase sequence issue.. No issue in DG. | closed | Ved Gupta
13 | 211005742 | 25-07-2024 11:17 | 20 | GP3.8601.../2420208 | Staring Problem Email By-KGD Name:-Sanjeev Jain | Task Start | Winstic Insurance Brokers India Pvt. Ltd. | Industrial Power Solutions - LUDHIANA |  | Unbalanced load on DG,Initiated for Cancellation. | Cancelled | Ved Gupta | KRM check
14 | 211005650 | 25-07-2024 10:55 | 30 | 3H.8902.../2320069 | Battery Issue & Starting issue Call By Customer Name :- Vishnukant Mobile No :- 8178923362 | Task Start | Jindal Service Station | Vidyut Engineers - New Delhi | 24 | Battery was discharged, due to battery charger was not connected to mains supply, connected the same issue resolved. | closed | Kapil Solanki
1 | 211008512 | 26-07-2024 09:31 | 500 | DV8.8501.C4../2320042 | ECU Issue Email By-Service Dealer Name:-Akanksha | Closed | Kedar Drugs & Pharmaceuticals Pvt. Ltd. | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 11 | SPN/FMI -4336/2 . Found bank A not dosing , checked interface box found loose connection on RL 1 , tighten the same issue resolved . | closed | Sudhir Awasthi
2 | 211008549 | 26-07-2024 09:40 | 82.5 | 5H.8901.../2420015 | Starting issue Call by Service Dealer Name:-Price No:-7027820044 | Task Start | KISHOR PACKAGING | M/s OM Diesels Pvt. Ltd. - Sonipat | 79.5 | starting issue with showing emergency stop alarm . Found emergency switch was internally malfunction , emergency switch will be change | open | Kapil Solanki
3 | 211008555 | 26-07-2024 09:40 | 750 | DV2.8501.C4../2320023 | ECU Amber Alarm Message by customer Name : Abhishek Kumar No : 7903795913 | Closed | HIND TERMINALS PVT LTD | Paluck Technologies Ltd. - Faridabad | 287 | SPN/FMI - (51/0), (5419/1) , clean the ITV connector and clear the DTC issue resolved . | closed | Kapil Solanki
4 | 211008585 | 26-07-2024 09:47 | 500 | DV8.8501.C4../2320028 | Low Coolant Level Alarm Issue Call By Customer Name :-Atul Kumar Mobile No :-9953698074 | Closed | Neel Kamal Enterprises Private Limited | Paluck Technologies Ltd. - Faridabad | 204 | Coolant level low alarm was showing on controller . Top up the coolant issue resolved . | closed | Kapil Solanki
5 | 211008678 | 26-07-2024 10:15 | 250 | F6.8841.../2420039 | Fuel Sensor and Error Code Issue Call By Customer Name :- Sonu Kumar Mobile No :- 7082013728 | Closed | Karnal Green Energy Pvt. Ltd. | Vishal Power Systems - Karnal | 24 | Fuel leakage from .fuel tank breather , due to breather pipe was not fitted ,need to breather pipe | open | Kapil Solanki | GOEM issue
6 | 211008954 | 26-07-2024 11:04 | 25 | GP3.8702.../2420088 | Oil Pressure Sensor Faulty | Task Start | Green Field Enterprises | Suraj Motor Store - kathua |  | Oil pressure Sensor faulty, change the same. ( under GOEM scope) | closed | Ved Gupta
7 | 211009090 | 26-07-2024 11:33 | 30 | 3H.8902.../2320031 | Maintenance Due Alarm Issue Call By Customer Name :-Azad Mobile No :-9996663879 | Open | Dr. Prashant Gupta | Paluck Technologies Ltd. - Faridabad |  | Need to CSP . SR will be cancel | cancelled | Kapil Solanki
8 | 211009115 | 26-07-2024 11:33 | 125.4 | 4H.8041.../2320026 | Starting Issue Call By Customer Name :- Yash Pal Mobile No :- 9599117169 | Task Start | SAMPARK Global Logistics Private Limited | Paluck Technologies Ltd. - Faridabad |  | starting issue with showing ECU protect lamp ON , DM1 no fault code found , disconnect the battery positive ,negative . And reconnect the same issue resolved . | closed | Kapil Solanki | KRM check
9 | 211009232 | 26-07-2024 11:58 | 320 | F6.8802.../2420040 | High Temperature Alarm issue Call By Customer Name :-PRAKAHS JHA Mobile No :-8510000448 | Closed | PM. Cinemas Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 9.24 | SPN/FMI - 110/0,516166/0 , checked coolant and fanbelt found ok . Clear the DTC and educated the customer about the same. | closed | Kapil Solanki | KRM check
10 | 211010280 | 26-07-2024 12:07 | 30 | 3H.8902.../2320142 | Error Code Issue Â Call By Customer Name :-Atul Yadav Mobile No :-9810264277 | Task Start | Caster Wheels India | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Customer complained about error code issue ,engineer did not found any issue , checked DM1,DM2 and no DTC found In ikonnect tool. | closed | Kapil Solanki | KRM check
11 | 211010661 | 26-07-2024 12:26 | 125.4 | 4H.8041.../2320163 | Abnormal Sound Â Issue Call By Customer Name :-Rajeev Mobile No :-8459775078 | Closed | Panchachuli Sehkari Aavak Samiti | Vidyut Engineers - Noida | 63 | DEF level was low @16%, Educated the customer about the same issue resolved . | closed | Kapil Solanki
12 | 211010666 | 26-07-2024 12:29 | 125.4 | 4H.8041.../2420283 | Starting Issue Call By Customer Name :-Pavan Rajput Mobile No :-9971445699 | Closed | VIJAY SALES | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 38 | battery was discharge , due customer side (NON koel ) battery charger was fault , educated the customer about the same issue resolved . | closed | Kapil Solanki
13 | 211010772 | 26-07-2024 12:51 | 125.4 | 4H.8041.../2420036 | Hunting Issue & Preventive Maintenance Call By Customer Name :- Hari Dutt Mobile No :- 9520854571 | Open | NEERAJ GENERATOR WORKS | M/s OM Diesels Pvt. Ltd. - Sonipat |  | Need to CSP . SR will be cancel | cancelled | Kapil Solanki
14 | 211010857 | 26-07-2024 13:04 | 57 | T4.8941.../2320089 | Sound Issue Call By Customer Name :- Sandip No :- 9639977495 | Task Start | Truestar Air System | Vidyut Engineers - Noida |  | abnormal sound from fanbelt side , found fanbelt was loose . Tighten the same issue resolved . | closed | Kapil Solanki | Fan belt replce
15 | 211011201 | 26-07-2024 14:31 | 10 | GP3.8301.../2420140 | fuel level sensor | Task Start | SHIVALAYA CONSTRUCTION CO. PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - HISAR | 1 | Air lock in fuel system, due to Fuel suction tube threads was damage, need to change (Line rejection SR) | open | Kapil Solanki | GOEM issue
16 | 211011273 | 26-07-2024 14:55 | 320 | F6.8802.../2420049 | Abnormal sound issue Call by KGD Name:-Kaur No:-9311523743 | Task Start | Vasant Valley School | Vidyut Engineers - New Delhi | 181 | Lube oil level was low L mark . Top up 8 litre the lube oil and kept in under observation for 100 days. . | closed | Kapil Solanki | Need more details
17 | 211011376 | 26-07-2024 15:09 | 125.4 | 4H.8041.../2320134 | Error Code Issue Â Call By Customer Name :-Kasidh Ahmad Mobile No :-8445820675 | Task Start | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar |  | SPN/FMI - 516166/0 clear the DTC and educated the customer about the same. | closed | Sudhir Awasthi
18 | 211011553 | 26-07-2024 15:53 | 200 | 6H.8435.../2420071 | lub oil leakage | Task Start | Heritage Overseas | Vishal Power Systems - PANIPAT |  | Lube oil leakage from lube oil filter and lube oil header assembly . Need to check. | open | Kapil Solanki | GOEM issue
19 | 211012622 | 26-07-2024 17:55 | 125.4 | 4H.8041.../2420045 | DG set not start Email by KGD Name :-Neeraj Saini | Closed | Shorya Auto Industries | Pratap Diesels Pvt. Ltd. - Alwar | 57 | SPN/FMI - 516166/0 and jerk load on DG educated the customer about the same | closed | Gourav Sharma
1 | 211014589 | 27-07-2024 13:49 | 40 | 3H.8951.../2420080 | Tripping issue Call By Customer Name: Rajat Number:8901510059 | Open | PRM. Property Consultant | M/s OM Diesels Pvt. Ltd. - Rohtak | 59.2 | Emergency stop alarm was showing in Display.. checked emergency switch found ok, after that checked panel connections found 1c2 wire was in loose condition, tighten the same issue resolved. | closed | Kapil Solanki
2 | 211014600 | 27-07-2024 13:45 | 25 | GP3.8702.../2420082 | diesel issue | Task Start | Surya Model school | OVN Industries Private Limited - New Delhi | 1 | Line Rejection SR, air lock issue.. Pipe alignement issue..(pre filter to main filter) corrected the same issue resolved.but kept in Under Observation. | open | Kapil Solanki
3 | 211014243 | 27-07-2024 12:22 | 20 | GP3.8601.../2420323 | Door Look Issue Call By Customer Name :-Mahadev Mobile No :-7400259313 | Open | Mahadev Jewellers | SAAN Royal Power Solutions Private Limited - Zirakpur | 4 | Customer complaint about door lock issue.. But door lock was found ok. Rain water entry in canopy issue.., sent mail communication regrding this issue. | closed | Ved Gupta | GOEM issue
4 | 211014238 | 27-07-2024 12:22 | 500 | DV8.8501.C4../2320036 | ECU PROTECT Issue Call By Customer Name :-Harish . Mobile No :- | Task Start | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 59.31 | Customer complaint about ECU protect alarm issue.. But engineer did not foundany DTC and also checked KRM but no any faul code at that time. | closed | Kapil Solanki | KRM check
5 | 211014239 | 27-07-2024 12:22 | 57 | T4.8941.../2320004 | Belt Issue & KRM App Issue Call By - Customer Name - Pankaj Goyal No. - 9654058093 | Open | SUN N SAND INDIA | M/s OM Diesels Pvt. Ltd. - Rohtak | 355 | Abnormal sound from loose belt, tighten the same issue resolved.and also Fuel sensor issue, today again engineer visited site for sensor issue.. | open | Kapil Solanki
6 | 211014236 | 27-07-2024 12:20 | 125.4 | 4H.8041.../2420530 | Stopping Issue Email By - KGD Name - Devendra Kumar Saxena | Task Start | Mascot Health Series Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 5.3 | Customer side VMR issue, no issue in DG. | closed | Kapil Solanki
7 | 211014217 | 27-07-2024 12:19 | 125.4 | 4H.8041.../2420283 | Battery issue Call by GOEM Name:- Satish Kumar No:- 9810263281 | Cancelled | VIJAY SALES | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Customer side AMF panel battery charger issue.. No issue in DG. | closed | Kapil Solanki
8 | 211014112 | 27-07-2024 11:59 | 320 | F6.8802.../2320057 | Error Code issue Call By Customer Name : -Balvindra singh No:-9289147063 | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 151 | tripping issue..checked event log found Canopy emergency alarm was activated, found, 4 pin connector was in loose condition, connected the same issue resolved. | closed | Kapil Solanki
9 | 211014076 | 27-07-2024 11:45 | 25 | GP3.8702.../2420024 | Voltage Problem Email By - Service Dealer Name - Sandeep | Task Start | Panipat Impex India | Vishal Power Systems - PANIPAT |  | Customer did not allow to checked DG set . | Cancelled | Kapil Solanki
10 | 211013793 | 27-07-2024 10:45 | 320 | F6.8802.../2320030 | Trip_Genset_Low_Voltage | Task Start | Atma Autotech Engineers Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 162 | KRM Generated SR, Engineer visited site but did not found any issue.. And without load DG running ok. | closed | Kapil Solanki | KRM check
11 | 211013715 | 27-07-2024 10:23 | 500 | DV8.8501.C4../2420042 | Error Code issue Email By - Service Dealer Name - Shiv | Task Start | Avaada Group | Vidyut Engineers - Noida | 50.2 | SPN/FMI: 523576/0( Interruption of dosing) ,(4336/2 Dosing valve is blocked), (171/3 related to ambient air temp. sensor circuit)( 523582/0),( 516166/0), (3031/14), ( 4427/1), checked dosing module found ok, then checked ambiant temp. sensor found missing.(171/3 fault code activated till now) | open | Kapil Solanki | ECU KRM check
12 | 211013645 | 27-07-2024 10:10 | 30 | 3H.8902.../2420044 | Automation Issue Message By Customer Name : Laykat Rai NO : 9872400103 | Open | Mr. Laykat Rai | Industrial Power Solutions - LUDHIANA |  | Low Coolant level, Initiated for Cancellation. | Cancelled | Ved Gupta
1 | 211011935 | 26-07-2024 16:49 | 57 | T4.8941.../ 2420312 | Automation Issue Call By Customer Name :-Supriya Sinha Mobile No :-9434031039 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | NA | Visit pending | OPEN | Prosanjit saha
| 211014624 | 27-07-2024 13:59 | 250 | F6.8841.../2420103 | ISSUE | Task Start | Kala Genset Pvt Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | o ring of oil filter came out due rising pr at starting, refitted the same ,no issue observed. | Closed
| 211014619 | 27-07-2024 13:53 | 0 | DV0.8501.C4../2420051 | issue | Task Start | Kala Genset P Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | Control panel isssue, change control panel, isue resolved. | Closed
| 211013984 | 27-07-2024 11:32 | 82.5 | 5H.8901.../2420146 | Display problem | Closed | Shree Krishna Homes | Transcreek Engineers Pvt. Ltd. - Ambernath | 5 | Controller power remains constant even power cut the control panel, observed +ve wire connected directly correct the connection issue resolved | Closed |  | GORM issue
| 211011571 | 26-07-2024 15:52 | 40 | 3H.8951.../2420324 | Under Speed Alarm issue Call By Customer Name :-Kiran Mobile No :-9022212318 | Task Start | Sent Meri Public School | Dhanashree Technocrats Pvt. Ltd. - Jalgaon | 17.1 | Showing spn 1485/4,5 920/5 2802/3 clear the fault code,then engine trip with under speed alarm, check all the connection , found ok,refitted the fuel filter remove the air , clear the fuel line, issue remain same. Check the voltage in crank sensor but engine didnt crank and trigger fault code- 637/5 which can not be clear after reconnect the connector. | OPEN
| 211008832 | 26-07-2024 10:52 | 25 | GP3.8702.../2420236 | oil pressure flt-vlt high shown in controller | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | 10 Bar oil pr shown in controller but in mech. Gauge oil pr is 7.5 bar then replace the sensor, flash the ecu but issue remain same. | OPEN
| 211008804 | 26-07-2024 10:38 | 25 | GP3.8702.../2420261 | Oil pressure high shown. | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | 10 Bar oil pr shown in controller but in mech. Gauge oil pr is 7.5 bar then replace the sensor, flash the ecu but issue remain same. | OPEN
1 | 211011124 | 26-07-2024 14:23 | 20 | GP3.8601.../2420136 | FIP | Task Start | Pookolathur Mahallu Auditorium. | G-Care Diesels Private Limited - Malappuram | LR | Electric feed pump not working | open | Mr Sanjaymon
2 | 211010588 | 26-07-2024 12:12 | 30 | 3H.8902.../2320061 | Under Voltage Â Alarm Issue Call By Customer Name :-Prabhu Mobile No :-8431773085 | Open | KGD Aravind Power Systems | Vijayshree Diesel Sales and Service - Bellary | 31 | Under Voltage Alarm issue - checked the AVR voltage setting found ok. taken a trial. DG Running in Good condition. | Closed | Mr. Prakash S | KRM check | Field team check the wire of KRM module. because KRM does not capture data.
3 | 211009149 | 26-07-2024 11:46 | 15 | GP3.8501.../2420077 | Line Rejection | Task Start | Kuruwahi Studios Pvt. Ltd. | Prasad Power Engineers - Udupi | 9 | Opened the SR because Earthing is not proper during commissioning.Commissioning is pending. | open | Mr. Prakash S
4 | 211008864 | 26-07-2024 10:58 | 82.5 | 5H.8901.../2420088 | Amber lamp on Issue Email By-Service Dealer Name:-Geetha. | Closed | A. E. C. S. Maaruti College of Nursing | Surya Power Services - Billekahalli | 5.39 | SPN: 516166 FMI: 0 related to ECU fault. Cleared the error codes. Engine running OK. | Closed | Mr. Prakash S
5 | 211008648 | 26-07-2024 10:01 | 58.5 | T4.8941.../2420792 | OIL LEAK | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Visit pending | open | Mr. Nanda Gopal
6 | 211008544 | 26-07-2024 09:40 | 58.5 | T4.8941.../2420341 | Smoke Problem Calle by: Customer Name: Kumar Number: 9003527733 | Closed | Geri Care Health Services Pvt. Ltd. | Madhu Engineering Sales & Service - Teynampet,Chennai | 9 | Smoke issue. Visited site found smoke is OK. | Closed | Mr. Nanda Gopal
7 | 211007505 | 25-07-2024 17:09 | 20 | GP3.8601.../2420039 | Starting Issue Email By - KGD Name -Genlite Calicut | Closed | ST.PAULS KG SCHOOL | G-Care Diesels Private Limited - Calicut | 4.31 | Fuse blown in controller line. | Closed | Mr Sanjaymon | Detiails required
1 | 211011935 | 26-07-2024 16:49 | 57 | T4.8941.../ 2420312 | Automation Issue Call By Customer Name :-Supriya Sinha Mobile No :-9434031039 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | NA | Visit pending | OPEN | Prosanjit saha
1 | 211001614 | 24-07-2024 00:00 | 57 | T4.8941.../2420435 | NA, CC SR | Task Start | Madhusudan Agrawalproject Pvt. Ltd. | Shree Engineering Service - Bilaspur | Na | The wires of the distribution blocks (XDBK2 and XDBK4) were interchanged.So 97/5 (water in fuel) was showing in controller. | OPEN | Vijay Patil | GOEM issue
| 211021725 | 29-07-2024 17:43 | 500 | DV8.9313.../2400001 | Urea tank cap broken & day tank supply pipe broken | Task Start | SENIOR SECTION ENGINEERS | Transcreek Engineers Pvt. Ltd. - Mumbai |  | DEF tank B supply pipe broken | OPEN | Jagdeep Saini
| 211021719 | 29-07-2024 17:41 | 500 | DV8.9313.../2400002 | Urea tank cap broken & day tank supply pipe broken | Task Start | SENIOR SECTION ENGINEERS | Transcreek Engineers Pvt. Ltd. - Mumbai |  | urea tank level not showing in controller in B bank | Closed | Jagdeep Saini
| 211021042 | 29-07-2024 15:33 | 58.5 | T4.8941.../2420527 | Automation Issue Call By Customer Name :-Sanjay Mobile No :- 7030668546 | Task Start | Shakar Steel Fuirniture | Dicksons Engineering Co.Pvt.Ltd. - Akola |  | Customer required education for operating DG | Closed | Jagdeep Saini
| 211019449 | 29-07-2024 10:44 | 20 | GP3.1021.../2420006 | ENGINE NOT START | Completed | Reliance Jio Infocomm Limited | Dicksons Engineering Co.Pvt.Ltd. - Aurangabad |  | ECU out can't generate output voltage replace the ECU and flash again same issue reported | OPEN | Jagdeep Saini
1 | 211020199 | 29-07-2024 13:08 | 160 | 6H.8475.../2420067 | Red Lamp On Alarm Issue Call By Customer Name :-Dipak . Mobile No :-9019748033 | Task Start | G S Bhaskar and G K Susheel | Surya Power Services - Bommasandra, Bangalore | 1 | QLT sensor wire found in loose condition , fitted the same , clear the fault code . problem resloved . | open | Mr. Prakash S | KRM check for fault code
2 | 211019314 | 29-07-2024 10:17 | 30 | 3H.8902.../2420103 | Starting Problem Call by : Dealer Name : Ramakrishna Contact : 6305359891 | Closed | Ananth Mourya Enterprises | Powerlinks Infra Tech Pvt Ltd - Madinaguda | LR | Auto sensing wire found in loose condition, tightend the same issue resloved. | Closed | Mr. Saleem
3 | 211019167 | 29-07-2024 09:30 | 40 | 3H.8951.../2420116 | STARTING PROBLEM | Completed | Rudraash Diagnostic Labs Pvt. Ltd. | Bharath Diesel Sales and Service - Trichy | LR | Flickering issue. Checked the Voltage-RY - 245 YB - 248 YR - 252. Alternator make authorised person was also visited. They suggest to change the AVR , but the problem is same . They check step by step and found when they adding the UPS load flickering problem happen so recommended to the customer to contact the UPS vendor | open | Mr. Nanda Gopal
4 | 211015675 | 27-07-2024 17:40 | 82.5 | 5H.8901.../2320046 | Error Code Issue Call By - Customer Name - Ravish No. - 9964076714 | Closed | Vasavi Kalyana Mantapa. | Surya Power Services - Billekahalli | 6.52 | Error code( 4225/1 related to NOx limits exceeded due to error in the NOx control system).Checked all the wirings are OK. Cleared the error code, then taken a trial. Error code again persists. Flashed the ECU, taken a trial. DG running OK | Closed | Mr. Prakash S | KRM Fault code photo attached
5 | 211015647 | 27-07-2024 17:38 | 20 | GP3.8601.../2420335 | Starting Issue Call By Â Customer Name :-Jogee . Mobile No :-Jogee . | Task Start | Jogee S Bhar | Surya Power Services - Bangalore | 2 | Error code related to LOP sensor. Found connector in loose condition. Corrected the same, issue resolved. | Closed | Mr. Prakash S
6 | 211014938 | 27-07-2024 15:13 | 625 | DV0.8501.C4../2420035 | FAN ISSUE | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | fan damage . | open | Mr. Nanda Gopal | EDO placed for fan
7 | 211014724 | 27-07-2024 14:17 | 25 | GP3.8702.../2420070 | Preventive Maintenance Call by : Customer Name : Muhammad Rijas Contact : 8075353819 | Open | Kolathukkara Fuels | G-Care Diesels Private Limited - Calicut | 2.2 | Customer raised the SR for oil service. | Cancelled | Mr Sanjaymon
8 | 211013694 | 27-07-2024 10:22 | 0 | 5H.8901.../2420203 | ITV ISSUE | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 0.2 | visit pending | open | Mr. Nanda Gopal | ITV replaced .
9 | 211012742 | 26-07-2024 18:31 | 0 | GP3.8702.../2420174 | Abnormal Noise | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Update pending at ASE end . | open | Mr. Nanda Gopal
10 | 211008648 | 26-07-2024 10:01 | 58.5 | T4.8941.../2420792 | OIL LEAK | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | Oil leakage from turbocharger hose. | open | Mr. Nanda Gopal | Pricing is not availiable in the system. Manual EDO placed.
1 | 211015871 | 27-07-2024 18:55 | 125.4 | 4H.8041.../2320052 | Stopping issue Call By Customer Name :- Nikhil Singla Mobile No :- 9971857680 | Open | Singla Trading Company | Paluck Technologies Ltd. - Faridabad |  | Customer want to reduce cooling time from 5 min to 30 sec, educated customer about the same . | Cancellation | Kapil Solanki
2 | 211015045 | 27-07-2024 15:37 | 125.4 | 4H.8041.../2320092 | Amber Lamp Alarm Issue Call By Customer Name :-Laxman Mobile No :-9050839880 | Task Start | Prabha Eye Hospital | Paluck Technologies Ltd. - Faridabad | 177 | SPN/FMI: 1761/16, 1761/14, 520528/31,4095/1, 3031/14, top up DEF clear the DTC issue resolved. ( Flashing Required). | Closed | Kapil Solanki
3 | 211014792 | 27-07-2024 14:42 | 250 | F6.8841.../2320016 | Coolant Leakage Issue Call By - Service Dealer Name - Prince No. - 7722070624 | Task Start | Indogulf Crop Sciences Limited | M/s OM Diesels Pvt. Ltd. - Sonipat | 326.4 | Modified Sensor installed. | Closed | Kapil Solanki
4 | 211018176 | 28-07-2024 13:02 | 250 | F6.8841.../2420138 | Coolant Leakage issue & Tripping issue Call By Customer Name : Yadav . No:- 8953943141 | Open | Vikas Stainless Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - HISAR | 13 | Coolant level low alarm was showing, but actually coolant was ok, checked coolant switch ,and tighten properly issue resolved. | Closed | Kapil Solanki | Under observation
5 | 211017603 | 28-07-2024 10:57 | 125.4 | 4H.8041.../2320200 | Auto panel issue Call by customer Name:- Vinay Gupta No:- 8707336707 | Open | NCC LImited | M/s OM Diesels Pvt. Ltd. - Sonipat | 439.46 | SPN/FMI: 3031/14 , 516166/0 in DM 1 and 1761/16, 110/3 , 4095/1, 520528/31, 51/1, 51/0 in DM 2 , tool was not connected ,today again engineer will visit the site. | Open | Kapil Solanki | Detail pending
6 | 211017494 | 28-07-2024 10:35 | 200 | 6H.8435.../2420020 | Heating Issue Call By Customer Name :- Mahendra Singh Mobile No :- 9910567755 | Open | Shanti Prakash Associates. | Vidyut Engineers - New Delhi |  | DG running on over load, educated customer about the same | Cancellation | Kapil Solanki | Detail pending
7 | 211017588 | 28-07-2024 10:33 | 62.5 | T4.8941.../2320076 | INSTANCE ID :-100707064 SITE ID : CALL BY CUSTOMER// DG ISSUE :- DG STARTING PROBLEM NAME : AJAY NUMBER :-8851779755 | Closed | Tata Tele services | Paluck Technologies Ltd. - Ghaziabad | 181 | Starting issue… fuel filter chocked, (Customer filling dirty fuel), clean the tank itself and change the filter issue resolved. | Closed | Kapil Solanki
8 | 211016932 | 28-07-2024 10:06 | 250 | F6.8841.../2320044 | Radiator cleaning charges Email By - Service Dealer Name -Sanjay Joshi | Closed | Koolking Udhyog Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 179 | SR open for vent pipe claim purpose. | Closed | Gourav Sharma
9 | 211017404 | 28-07-2024 08:35 | 125.4 | 4H.8041.../2320004 | Automation issue Call by customer Name:- Bhawan . No:- 9899373168 | Open | ARIHANT INDUSTRIAL EQUIPMENT | Vidyut Engineers - New Delhi |  | wrong complaint repoted by customer no issue in DG. | Cancellation | Kapil Solanki
1 | 211019059 | 29-07-2024 07:46 | 160 | 6H.8475.../2420031 | Tripping Issue Call By Customer Name: Rohit Malik Number:9999637245 | Task Start | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 238 | Starting issue with showing ECU ERROR NON RESPOND FROM ECU , found 15 RB1 - RL 1 -2A7 Wire was loose tighten the same issue resolved . | Closed | Kapil Solanki
2 | 211019245 | 29-07-2024 09:57 | 40 | 3H.8951.../2420025 | EB contactor faulty | Task Start | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 24 | Customer side DG contractor was not hold , (customer side panel issue) ,No issue in DG. | Closed | Kapil Solanki
3 | 211019249 | 29-07-2024 10:02 | 625 | DV0.8501.C4../2320010 | Starting Issue Call By Â Service Dealer Name :-Prince Mobile No :-7722070624 | Task Start | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat | 164.3 | Sometimes DG was tripping with Negative phase sequence alarm. Checked on KRM found R phase 0 A, out put . Checked on CT connection and wiring on control panel found ok. | Closed | Kapil Solanki | KRM check | Check KRM data and found it some time R phase current value zero and other phase current vlaue above 160 A.
4 | 211019259 | 29-07-2024 09:59 | 500 | DV8.8501.C4../2320030 | Tripping issue Call By Customer Name :-Bijendra Kumar Mobile No :- 7633873576 | Task Start | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 185 | DG running on Sink, and in deepsea emergency alarm was activated, and in woodward high coolant temp alarm was appered, we suggested to engineer connected Iknoonect tool but tool was not connected, (Revisit Required) | Open | Kapil Solanki
5 | 211019268 | 29-07-2024 10:04 | 125.4 | 4H.8041.../2320161 | Automation Issue Call By Customer Name :- Ram milan Mobile No :- 9810927574 | Task Start | Indraprakash Apartment Occupants Association Redg | Vidyut Engineers - New Delhi | 10.1 | DEF level was low top up the DEF and educated the customer about the same | Closed | Kapil Solanki
6 | 211019387 | 29-07-2024 10:32 | 125.4 | 4H.8041.../2420066 | Fuel Sensor Issuer Call BY Customer Name :- Amit No :- 7065865836 | Task Start | Welcome Crop Sciences Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 25.6 | As previously discussed (Fuel sensor issue..Erratic reading showing on display..sometimes showing 30 %, 70 %, ,checked resistance found ok, but issue not resolved.) change the fuel level sensor | Closed | Kapil Solanki
7 | 211019517 | 29-07-2024 10:58 | 500 | DV8.8501.C4../2420078 | Door Lock Issue Diesel Fuel Cap Issue Urea Leakage Issue Call By Customer Name :-Vinit ... Mobile No :-7683063495 | Open | MTI. Industries Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Sonipat | 51.1 | Door lock adjustment issue.. and also fuel tank cap faulty, (need to replaced) | Open | Kapil Solanki
8 | 211019555 | 29-07-2024 11:08 | 250 | F6.8841.../2320040 | ECU malfunction Issue Email By-Customer Name:-Hony. Secretary | Task Start | Anand lok CGHS.Mayur Vihar Phase 1 | Vidyut Engineers - New Delhi | 14 | SPN/FMI - 1761/18 DEF level low @16% but physicaly on tank @100 % , found 2A6 to 2A8 fues was internally loose replace the fuse issue resolved and SPN/FMI - 516166/0 found cooling down period was 30 sec need to change. | Closed | Kapil Solanki
9 | 211019790 | 29-07-2024 11:38 | 82.5 | 5H.8901.../2320070 | Starting Issue Call By Customer Name :-Monu Mobile No :- 8434625450 | Task Start | Gen Power Generator | Vidyut Engineers - New Delhi | 2 | DEF percentage was not showing in display..(need to programme) | Open | Kapil Solanki
10 | 211019826 | 29-07-2024 11:48 | 160 | 6H.8475.../2320015 | Amber Lamp Issue Call By Customer Name :- Vikash Sharma Mobile No :- 9812514442 | Task Start | Ambadi Enterprise | Vishal Power Systems - PANIPAT |  | DEF level was low and need to CSP , SR will be cancel | cancelled | Kapil Solanki
11 | 211019846 | 29-07-2024 11:56 | 20 | GP3.8601.../2420319 | sensor issue | Task Start | ICICI Bank Limited | Pratap Diesels Pvt. Ltd. - Bhilwara | 1 | Line Rejection SR, Emergency alarm was showing is display..checked and found 4 pin connector was in loose condition, tighten the same issue resolved. | Closed | Gourav Sharma
12 | 211019893 | 29-07-2024 12:09 | 30 | 3H.8902.../2420330 | Under Speed Ala ram issue Call by Customer Name:- Nikil ... No:- 9958901282 | Closed | Vee Kay Industries. | Paluck Technologies Ltd. - Faridabad | 2.5 | Under speed alarm was showing on event log , checked fuel line found ok , and coolant leakage from block at core plug tighten the same issue resolved . | Closed | Kapil Solanki
13 | 211019916 | 29-07-2024 12:09 | 160 | 6H.8475.../2420025 | Tripping Issue Call By Customer Name :- pratap .singh Mobile No :- 9811134852 | Completed | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi |  | Fan belt change , SR open for claim purpose | Closed | Kapil Solanki
14 | 211020078 | 29-07-2024 12:45 | 40 | 3H.8951.../2320010 | Starting Issue Call By Â Customer Name :-RAVINDRA SIR Mobile No :-8168752914 | Task Start | Ganpati Enterprises | Vishal Power Systems - Karnal | 70 | Starting issue due to main fuel pipe was choke . Clean the pipe issue resolved . | Closed | Kapil Solanki
15 | 211020198 | 29-07-2024 13:08 | 125.4 | 4H.8041.../2320168 | Oil Leakage Issue Call By Customer Name :- Pradeep Yadav Mobile No :-8368321282 | Open | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 317 | Oil leakage from rocker cover gasket , and lube oil filter side plug . changed Gasket issue resolved. | Open | Kapil Solanki
16 | 211020229 | 29-07-2024 13:17 | 250 | F6.8841.../2420004 | Automation Issue Email By - GOEM Name - Anil Wagh | Task Start | TATA TELESERVICES LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | customer Need manual mode to auto mode. (connection done) | Closed | Kapil Solanki
17 | 211020232 | 29-07-2024 13:19 | 250 | F6.8841.../2320038 | Automation Issue Email By - GOEM Name - Anil Wagh | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | customer Need manual mode to auto mode. (connection done) | Closed | Kapil Solanki
18 | 211020732 | 29-07-2024 14:10 | 125.4 | 4H.8041.../2420423 | Starting Issue Call By Customer Name:-Suraj Jha No:-6205804058 | Task Start | Nexus Technosystems Pvt. Ltd. | Vidyut Engineers - Noida | 69.43 | Fuel level low alarm on event log , before engineer reach at site customer top up fuel , educated the customer about the same issue resolved . | Closed | Kapil Solanki
19 | 211020853 | 29-07-2024 14:59 | 40 | 3H.8951.../2320014 | Starting Issue And Preventive Maintenance Call By Customer Name :-ATUL AGNIHOTRI Number :-9899010324 | Open | Ganpati Legal Advisors Pvt. Ltd. | Vidyut Engineers - New Delhi | 12 | Starting issue with showing Emergency stop alarm , found emergency switch was in pressed condition , correct the same issue resolved | Closed | Kapil Solanki
1 | 211011935 | 26-07-2024 16:49 | 57 | T4.8941.../ 2420312 | Automation Issue Call By Customer Name :-Supriya Sinha Mobile No :-9434031039 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | 18 | connection of R,Y,B in LVM had changed ,due to which the mains contactor was not holding .Then the engineer replaced R with R ,Y with Y,B with B and the issue was resolved. | OPEN | Prosanjit saha
1 | 211025703 | 31-07-2024 06:46 | 625 | DV0.8501.C4../2420030 | WIRING HARNESS DEFECTIVE | Task Start | AIA Engineering Ltd. | Unique Techno Services Pvt Ltd. - Ahmedabad | Na | The CAM sensor connector was found broken even before the genset was commissioned at site. | OPEN | Amit Shandilya
2 | 211023338 | 30-07-2024 11:19 | 20 | GP3.1021.../2420113 | INSTANCE ID:-100744687 SITE ID:-I-GJ-PTNN-ENB-G003 CALL BY CUSTOMER// DG ISSUE:-DG gcu alram issue /automation NAME:-Uday Prajapati NUMBER:-9601297100 | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 51h | Low fuel(54) in tank and super capacitor was discharge. | Closed | Amit Shandilya
1 | 211021984 | 29-07-2024 18:49 | 30 | 3H.8902.../2320053 | Trip_Genset_Low_Voltage | Open | Shree Organic Chem Industries Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 208 | KRM Generated SR, DG was tripping with showing under voltage alarm , found Customer side load cable shorted. | Closed | Gourav Sharma
2 | 211021852 | 29-07-2024 18:16 | 82.5 | 5H.8901.../2320009 | Oil Leakage Issue & Starting Issue Call By - Customer Name - rajiv No. - 9717973393 | Open | ARSH LADIES SUIT PRIVATE LIMITED | Vidyut Engineers - Noida | 88.44 | Starting issue due to DEF level was @0% also DEF percentage was not showing on controller .(need to programme) | Open | Kapil Solanki | krm CHECK
3 | 211021282 | 29-07-2024 16:15 | 58.5 | T4.8941.../2420725 | Starting Issue Call By Customer Name :- Bittu .. Mobile No :- 8860972935 | Closed | Nirakara Jewels | Vidyut Engineers - New Delhi | 9 | Battery was discharge(8 volt) , battery charger mains supply was missing from battery charger, correct the same issue resolved | Closed | Kapil Solanki
4 | 211021283 | 29-07-2024 16:15 | 750 | DV2.8501.C4../2420019 | Tripping issue Call By Customer Name :-Vivek Mishra Mobile No :- 8529794176 | Task Start | Homekraft Infra Pvt. Ltd. | Vidyut Engineers - Noida | 8.42 | DG was tripping with showing Negative phase sequence alarm. Found unblanced load . Educated the customer about the same. | Closed | Kapil Solanki | KRM check. FAult logic check
5 | 211021262 | 29-07-2024 16:06 | 750 | DV2.8501.C4../2420001 | Tripping issue Call By Customer Name :-Vivek Mishra Mobile No :- 8529794176 | Task Start | Homekraft Infra Pvt. Ltd. | Vidyut Engineers - Noida | 25.53 | DEF level was low @14%, educated the customer about the same. And also sometimes DG was tripping, But engineer did not check on load. Without load DG ruuning ok. | Closed | Kapil Solanki
6 | 211021260 | 29-07-2024 16:06 | 320 | F6.8802.../2320041 | Voltage Issue Call By - Customer Name - Bunty No. - 8000289498 | Task Start | Mama Foods | Pratap Diesels Pvt. Ltd. - Alwar | 113 | DG was tripping with showing Under speed alarm, checked fuel line and tighten all panel connections found ok. | Closed | Gourav Sharma | KRM check. Details required
7 | 211021104 | 29-07-2024 15:47 | 125.4 | 4H.8041.../2320007 | Starting Issue Call By Customer Name :-Rajiv Mobile No :- 7053881104 | Closed | Meru Resorts LLP. | Vidyut Engineers - New Delhi | 25.35 | Customer complaint about the starting issue , but engineer did not found any issue on DG . | Closed | Kapil Solanki
1 | 211024031 | 30-07-2024 13:02 | 250 | F6.8841.../2320020 | Red Lamp Alarm Issue Call By Customer Name :-Manewar ... Mobile No :-9310802007 | Open | ZNR. Consultancy Services Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 39 | Low DEF level @ 18 % , top up DEF and educated customer about the same. | Closed | Kapil Solanki
2 | 211024032 | 30-07-2024 13:02 | 20 | GP3.8601.../2420251 | Automation Issue Call By Customer Name :- Gurupreet Singh Mobile No :- 8557099817 | Open | Mr. Guri. | SAAN Royal Power Solutions Private Limited - Zirakpur | 1.2 | Mains setting for auto mode desible. | Closed | Ved Gupta
3 | 211023484 | 30-07-2024 11:45 | 82.5 | 5H.8901.../2420021 | Low oil issue Call By Customer Name :- Lalit Tyagi Mobile No :-9810138700 | Task Start | Sgs Diesel Power And Heavy Electrical. | Vidyut Engineers - Noida | 29.2 | SPN/FMI: 1761/16, (Low DEF level @ 47 %), top up and educated customer about the same. | Closed | Kapil Solanki
4 | 211023062 | 30-07-2024 11:03 | 40 | 3H.8951.../2420236 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | During transportation,(vehicle Accident) need to proper check | Open | Sudhir Awasthi
5 | 211023056 | 30-07-2024 11:00 | 40 | 3H.8951.../2420243 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | During transportation,(vehicle Accident) need to proper check | Open | Sudhir Awasthi
6 | 211022892 | 30-07-2024 10:58 | 40 | 3H.8951.../2420238 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | During transportation,(vehicle Accident) need to proper check | Open | Sudhir Awasthi
7 | 211022886 | 30-07-2024 10:54 | 40 | 3H.8951.../2420248 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | During transportation,(vehicle Accident) need to proper check | Open | Sudhir Awasthi
8 | 211022923 | 30-07-2024 10:53 | 40 | 3H.8951.../2420200 | Load Issue Call By Customer Name :-Ujjal Das Mobile No :-9382724016 | Open | SCC INFRASTRUCTURE PVT.LTD. | Pratap Diesels Pvt. Ltd. - JAIPUR |  | SR open for Servicing Purpose. | Cancelled | Gourav Sharma
9 | 211022871 | 30-07-2024 10:42 | 160 | 6H.8475.../2320036 | Coolant Issue Call BY Customer Name :- Rajiv No :- 9871151722 | Task Start | VICTOR INDUSTRIES | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 27 | Coolant level low below L mark, top up the same. | Closed | Kapil Solanki | Under observation
10 | 211022806 | 30-07-2024 10:30 | 15 | GP3.8501.../2420009 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | 1.24 | Canopy damaged (Need to chenge) | Open | Sudhir Awasthi
11 | 211022790 | 30-07-2024 10:28 | 57 | T4.8941.../2420046 | Voltage issue. Call By Customer Name :-Dinesh Kumar Mobile No :-9729808788 | Open | Jindal Industries. | M/s OM Diesels Pvt. Ltd. - Sonipat |  | Visit Pending | Open | Kapil Solanki
12 | 211022788 | 30-07-2024 10:28 | 160 | 6H.8475.../2320034 | Mubel Leakage issue Call By Customer Name :- Mohammad Amjad Mobile No :- 8865019331 | Task Start | INFRA 13 PVT LTD | Paluck Technologies Ltd. - Ghaziabad | 26 | Oil through from Exhaust manifold, (customr using only 20 % load ), educated customer please maintain load atleast 50 % load. | Closed | Kapil Solanki | KRM check
13 | 211022803 | 30-07-2024 10:27 | 15 | GP3.8501.../2420371 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | 3.12 | During transportation,Canopy roof damaged, (need to check proper) | Open | Sudhir Awasthi
14 | 211022795 | 30-07-2024 10:23 | 15 | GP3.8501.../2420022 | Transit damage | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | 2.4 | During transportation,Canopy roof damaged, (need to check proper) | Open | Sudhir Awasthi
15 | 211022708 | 30-07-2024 10:10 | 500 | DV8.8501.C4../2320036 | Starting Issue Call By Customer Name :-Harish . Mobile No :-9720331726 | Closed | SATYA MICROCAPITAL LIMITED | Vidyut Engineers - Noida | 59.51 | SPN/FMI: 651/3 (Short circuit of the power stage low side (Clyinder 1), checked injector wiring found wire touch from body, corrected the same issue resolved. | Closed | Kapil Solanki
16 | 211022636 | 30-07-2024 09:54 | 125.4 | 4H.8041.../2420018 | Error Code Issue Email By-Service Dealer Name:-Rahul Sharma | Task Start | Sharkline Appliances | M/s OM Diesels Pvt. Ltd. - HISAR | 117.2 | Low DEF level and 5461/0, flashed latest cal file issue resolved. | Closed | Kapil Solanki
1 | 211022641 | 30-07-2024 09:55 | 100 | 4H.8041.../2420648 | ADD BLUE LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | LR | pending at ASE end | open | Mr. Nanda Gopal | ad-blue pipe damage in condition , replaced the same .
2 | 211021972 | 29-07-2024 19:04 | 20 | GP3.1021.../2420035 | DG Silencer Exhaust covering damaged | Open | Reliance Jio Infocomm Limited | G-Care Diesels Private Limited - Malappuram | 8.5 | Due to heavy rainfall unable to attend the site | open | Mr Sanjaymon | photo atteched
3 | 211021888 | 29-07-2024 18:25 | 58.5 | T4.8941.../2420511 | R Phase Under Voltage Complaint Email By - KGD Name -Genlite Service | Task Start | KPN. Farm Fresh Pvt. Ltd. | Powerlinks Infra Tech Pvt Ltd - Hyderabad | 6 | pending at ASE end | open | Mr. Saleem | R-phase sensing wire , found loose in condition , tightend the same , problem resolved .
4 | 211021730 | 29-07-2024 17:46 | 25 | GP3.8702.../2420216 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PVT LTD | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | air lock issue , release the same issue resloved. | Closed | Mr. Nanda Gopal
5 | 211014791 | 27-07-2024 14:41 | 58.5 | T4.8941.../2420495 | Line Rejection | Closed | Alwyn Bakery | Prasad Power Engineers - Udupi | 1 | one body earthing is missing | open | Mr. Prakash S
1 | 211020269 | 29-07-2024 13:26 | 0 | 4H.8041.../2420657 | ECU issue | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | Burnout the ignition fuse when starting command engg. Suspected short the ECU internally Replaced the ECU, Issue resolved. | open | Jagdeep Saini
2 | 211019543 | 29-07-2024 11:07 | 58.5 | T4.8941.../2420875 | Diesel leakage from injector inlet pipe joint. | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | Visit But Panel not available therefore don’t have any findings. | open | Jagdeep Saini
3 | 211027510 | 31-07-2024 13:15 | 20 | GP3.1010.../2200002 | Starting Issue Call By Customer Name :- Prshant Pawar Mobile No :-8888880055 | Open | DICKSONS ENGINEERING CO.PVT.LTD. | Unique Techno Services Pvt Ltd. - Gandhidham | NA | Customer is not receiving the Call. | open | Amit Shandilya
4 | 211025930 | 31-07-2024 08:32 | 160 | 6H.8475.../2420068 | FUEL LEVEL WRONG SHOW Email By - Service Dealer Name -Dharmendrasinh Zala | Task Start | Hotel Surabhi | Unique Techno Services Pvt Ltd. - Gandhidham | 14h | Fuel was filled upto 95% by Customer but fuel level was showing almost 50% in the gauge or controller. SDE visited the site removed the float of the fuel level sensor and refitted it properly. The issue is resolved now. | Closed | Amit Shandilya
5 | 211022028 | 29-07-2024 00:00 | 259 | F6.8841.../2420122 | CSP CC DG Commissioning Mr-Rahulbhai Mo-9892137705 | Task Start | C. C. Logix Parks India Private Limited. | Unique Techno Services Pvt Ltd. - Bhavnagar | NA | Leakage was detected in the fuel tank even before commissioning the genset. | open | Amit Shandilya | goem ISSUE
| 211028288 | 31-07-2024 15:37 | 58.5 | T4.8941.../2420377 | LVM ISSUE | Task Start | Shangrila Construction Company | K.C. Diesel Services - SILIGURI | 2 | Engineer visited the site and found that LVM is faulty because the mains supply is coming in the LVM but it is not working. | open | Prosenjit saha
| 211029745 | 31-07-2024 20:02 | 58.5 | T4.8941.../2420302 | Tripping Â Issue Call By Customer Name :-laddu ... Mobile No :-9934663577 | Open | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 140 | "engineer visit the site found the unbalance load upto 47% educate the customer about balancing of load." | Closed | Prabhakar kumar
1 | 211025572 | 30-07-2024 19:50 | 30 | 3H.8902.../2420330 | Under Speed Alarm issue Call by Customer Name:- Nikil ... No:- 9958901282 | Task Start | Vee Kay Industries. | Paluck Technologies Ltd. - Faridabad | 4 | Tripping issue.. Under speed alarm was showing, customer put load on DG instantly without completed Saftey monitoring time, educated customer to put load on DG after compliting saftey monitoring time.and also checked fuel line found ok. | Closed | Kapil Solanki
2 | 211025441 | 30-07-2024 18:19 | 82.5 | 5H.8901.../2320034 | KRM Issue Call By Customer Name :- Subhashchandra Mobile No :-8225052174 | Task Start | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 303 | KRM faulty, contact to KRM team, and he suggested for KRM replacement. | open | Kapil Solanki
3 | 211025409 | 30-07-2024 18:09 | 82.5 | 5H.8901.../2320042 | Error Code Issue Call By Customer Name :-Kasidh Ahmad Mobile No :-8445820675 | Open | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar | 123 | SPN/FMI: 6595/0, (Additional Dosing Chk err),tool not connected, today engineer will visit the site. | open | Sudhir Awasthi | Update required
4 | 211025240 | 30-07-2024 17:38 | 30 | 3H.8902.../2320142 | Starting Issue Email By-Service Dealer Name:-Saurabh Rajput | Task Start | Caster Wheels India | Paluck Technologies Ltd. - Gurgaon | 46.31 | Controller was in Programming mode, correted the same. | Closed | Kapil Solanki
5 | 211025031 | 30-07-2024 16:55 |  | T4.5201.C1../2300001 | Load testing claim. Email By Service Dealer Name:-Bharat Singh | Closed | AJAX ENGINEERING PRIVATE LIMITED | Rajdhani Diesels and Electricals - Jodhpur | 410 | BS V (load trail ) | Closed | Gourav Sharma
6 | 211025021 | 30-07-2024 16:54 | 25 | GP3.8702.../2420048 | Emergency Stop Alarm and Starting Issue Call By Customer Name :-Keshav Mobile No :-9654019499 | Closed | Jitender Kumar | Paluck Technologies Ltd. - Gurgaon | 191.47 | Tripping issue..Emergency stop alarm was showing ,found canopy emergency switch connections was in loose condition, tighen the same issue resolved. | Closed | Kapil Solanki
7 | 211024925 | 30-07-2024 16:36 | 40 | 3H.8951.../2420074 | Tripping Issue Call By Customer Name:-Umesh .. Mobile No:-9560990602 | Task Start | Techfroeb Machinery Pvt. Ltd. | Vidyut Engineers - Noida | 2.8 | load side MCB manually tripped by customer, educated customer about the same. | Closed | Kapil Solanki
8 | 211024849 | 30-07-2024 16:20 | 320 | F6.8802.../2320028 | Automation issue Call By Customer Name :-Sourav Tiyagi Mobile No :-9690706146 | Task Close | Arocon rainbow | Paluck Technologies Ltd. - Ghaziabad | 114 | Tripping issue..Emergency alarm was showing checked and found Canopy Emergency switch NC element faulty ( need to replaced) | open | Kapil Solanki
9 | 211024504 | 30-07-2024 15:15 | 500 | DV8.8501.C4../2420048 | Load Issue Email By-GOEM Name:-Nishit Kumar | Task Start | Shahi Dyeing Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | DG tripping with SPN/FMI: 633/3, ( Rail pressure function ) after DG acrosses approxmitally 420 amp.checked water and fuel sensor o Ring found damaged condition, replaced with new one from local market , then issue resolved . and take load trail issue resolved. | Closed | Kapil Solanki | Update required
10 | 211024528 | 30-07-2024 15:15 | 30 | 3H.8902.../2320100 | Power Supply Issue Call By Customer Name :-Ankit Jain Mobile No :-9811194649 | Task Start | Nagina Metal & Egineers | Paluck Technologies Ltd. - Faridabad | 139 | Power supply issue...Neutral link was burnt, (need to replace) | open | Kapil Solanki | Failed part
11 | 211024483 | 30-07-2024 15:03 | 125.4 | 4H.8041.../2420140 | Over Load issue Call BY Customer Name :- Manjay No :- 7982970631 | Open | BD. Enterprises | Paluck Technologies Ltd. - Faridabad |  | Visit pending | open | kapil Solanki
12 | 211024480 | 30-07-2024 15:03 | 750 | DV2.8501.C4../2420006 | ECU Alarm issue Call By Customer Name :-Arun Mobile No :-9871566559 | Task Start | Seven R Hotels Pvt. Ltd. DS Group | Vidyut Engineers - Noida | 1308 | Abnormal sound issue.. Fan blade ,drive bearing and belt damaged, (need to dismentle and check). | open | Kapil Solanki
13 | 211024280 | 30-07-2024 14:14 | 125.4 | 4H.8041.../2420439 | Door lock Call by customer Name:-Charan Singh No:-9812754609 | Task Start | Baba Amarnath Enterprises. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Service due. | Cancelled | Gourav Sharma
14 | 211024109 | 30-07-2024 13:22 | 320 | F6.8802.../2320006 | Trip_Genset_Low_Voltage | Cancelled | Super Seal India Ltd. | Paluck Technologies Ltd. - Faridabad |  | Check KRM no abnormility found DG running ok. | Cancelled | Kapil Solanki | KRM check
15 | 211024037 | 30-07-2024 13:02 | 250 | F6.8841.../2420138 | Starting issue Call By KGD Name: Surender Kumar Number:9996543876 | Task Start | Vikas Stainless Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - HISAR | 19.5 | Coolant level low alarm was showing in display, checked coolant found ok, then checked coolant level sensor connector was in loose condition , connected the same issue resolved. | Closed | Kapil Solanki
1 | 211027464 | 31-07-2024 13:16 | 57 | T4.8941.../2320199 | Door Lock Issue & Preventive Maintenance Call BY Customer Name :- Ravindra No :- 9811227341 | Task Start | RAJPOOT GENERATORS | Paluck Technologies Ltd. - Ghaziabad | 498 | Service done | Closed | Kapil Solanki
2 | 211027271 | 31-07-2024 12:38 | 62.5 | T4.8941.../2420297 | Tripping issue Call By Customer Name : Suhas .. No:- 9053689638 | Open | Ecowalk Impex Private Limited | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 30 | SPN/FMI: 97/5 in DM 1 and (1485/5 main relay open ), (1485/4 Main relay short to ground) (157/14 ), (97/5 ) in DM 2 found 36 pin connector was not fitted properly , connected properly issue resolved.and suggested to engineer checked XDBK connections for 97/5. | Open | Kapil Solanki
3 | 211027159 | 31-07-2024 12:10 | 125.4 | 4H.8041.../2420445 | Mubel Pipe leakage issue Call By Customer Name : Ashok Kumar No:- 9999370657 | Task Start | Sunny Wears Inc | Paluck Technologies Ltd. - Faridabad | 46 | Lube oil leakage from lube oil filter header assembly , tighten the same but issue not resolved , Engineer will visit today | Open | Kapil Solanki | CSP need to check
4 | 211027002 | 31-07-2024 11:37 | 200 | 6H.8435.../2320031 | V Belt Has Broken Call By Customer Name :- Aditya Aryan Mobile No :-8839388441 | Task Start | OIL INDIA LTD. | Rajdhani Diesels and Electricals - Jodhpur |  | Abnormal sound from V bel broken, (Need to replaced) | Open
5 | 211026902 | 31-07-2024 11:13 | 40 | 3H.8951.../2420023 | DG not working in Auto mode. | Task Start | BHARTI AIRTEL LIMITED | Vidyut Engineers - Noida | 45 | Automation issue due to negative supply missing . Automation wire was loose condition on Customer panel tighten, tha same issue resolved | Closed | Kapil Solanki
6 | 211028117 | 31-07-2024 14:58 | 30 | 3H.8902.../2420009 | Starting Issue Email By-Service Dealer Name:-ARJUN PANWAR | Open | Suraj Auto | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 69 | Tripping issue with showing Communication failure and under speed alarm , found CAN L Was loose condition , tighten the same . And DG was running unblace load , | Closed | Kapil Solanki
7 | 211028076 | 31-07-2024 14:51 | 125.4 | 4H.8041.../2320198 | Maintenance Due Alarm Issue Call By Customer Name :-Abdul Kasim Khan Mobile No :-7982938601 | Open | BKDJ Packagings Pvt. LTD | Paluck Technologies Ltd. - Gurgaon | 297 | maintenance due alarm was showing on controller . Reset the alarm issue resolved | Closed | Kapil Solanki
8 | 211027833 | 31-07-2024 14:40 | 125.4 | 4H.8041.../2320161 | Automation Issue & Display Issue Call By Customer Name :-Ram milan Mobile No :-9810927574 | Task Start | Indraprakash Apartment Occupants Association Redg | Vidyut Engineers - New Delhi | 10.13 | SPN/FMI - 1761/18 DEF level low @0% but physically on tank @100 % , found 2A6 to 2A8 fues was internally loose need to replace. | Open | Kapil Solanki
9 | 211027826 | 31-07-2024 14:40 | 500 | DV8.8501.C4../2320027 | Radiator Issue Call By Customer Name:-Pradeep Verma Mobile No:-9582199953 | Task Start | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Previously quality team visited site and found radiator was choked , Need to clean in Warranty.. | Open | Kapil Solanki
10 | 211027796 | 31-07-2024 14:28 | 125.4 | 4H.8041.../2420050 | Red Lamp On Alarm Issue Call By Customer Name :-Kumar Shankar Mobile No :-8700992489 | Task Start | International Automotive Components | Paluck Technologies Ltd. - Faridabad | 236 | DEF level was low , top up the DEF and educated the customer about the same issue resolved . | Closed | Kapil Solanki
1 | 211027374 | 31-07-2024 12:55 | 20 | GP3.1021.../2420014 | not start | Task Start | Reliance Jio Infocomm Limited | G-Care Diesels Private Limited - Calicut | LR | EDO placed for super capacitor | Closed | Mr Sanjaymon
2 | 211026183 | 31-07-2024 10:21 | 0 | F6.8802.../2420120 | Smoke From Breather | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | engg. found more smoke , Today Mr. kaleshwar visit the site. | open | Mr. Nanda Gopal | ,run the generator breather smock heavy ( koel team quality team mr.kalishwar marrla) joined the site, removed the Rocker cover checked the bolt and nut rockram side, exhaust side checked the bolt and nut no issues blow bye tool connected 100% load on uppnormal blow bye so discussion koel ho team after plan
3 | 211026159 | 31-07-2024 10:18 | 40 | 3H.8951.../2420199 | Starting Issue Email By - Service Dealer Name -Surya power | Task Start | COORG GATE FAMILY RESTURENT | Surya Power Services - Kushalanagara | 38 | , Fues is missing For the battery charger ,during commissioning . | Closed | Mr. Prakash S | GORM issue
4 | 211025269 | 30-07-2024 17:43 | 10 | GP3.8301.../2420026 | Starting Issue Call By Customer name:Irshad Mobile No:-9980171350 | Task Start | Hotel Shain. | Prasad Power Engineers - Haveri | 6 | An error code has occurred in the DG, Today cpcb4+ trained engg. visit the site . | open | Mr. Prakash S | Update required 2791 28002. Under opbservation
5 | 211024959 | 30-07-2024 16:43 | 250 | F6.8841.../2420155 | FUEL LEAKAE | Closed | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | 1.12 | engine checked-in fuel leakage from fuel leak off pipe rail to pump house damaged condition and new replaced condition engine checked , normal condition load checked normal | Closed | Mr. Nanda Gopal