## August 24
| Incident Id | Creation Date | KVA Rating | Engine no | Customer VOC | SR Status | Account Name | Service Dealer Name | Running Hrs | Observation | Incident Status | ASM Name
1 | 211028108 | 31/07/2024 15:03:54 | 40 | 3H.8951.../2420016 | Starting Issue Call By Customer Name :-Harendra Kumar Sharma Mobile No :-9068357745 | Task Start | KLJ Petroplast Limited | Unique Techno Services Pvt Ltd. - Ankleshwar | 409 | The winding of alternator is burnt but due to absence of Genset CSP the warranty of alternator is rejected and the alternator is given to vendor for repair on customer pay basis. | OPEN | Amit Shandilya | Oil sample required. KRM check
2 | 211035967 | 2024-01-08 10:43 | 57 | T4.8941.../2420034 | DG SET STARTING PROBLEM | Task Start | Pravesh Paper Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Gandhidham | 1 | The wires of the distribution blocks XDBK2 and XDBK4 were interchanged.So 97/5 (water in fuel) was showing in controller. | Closed | Amit Shandilya
1 | 211029745 | 31-07-2024 20:02 | 58.5 | T4.8941.../ 2420302 | Tripping Â Issue Call By Customer Name :-laddu ... Mobile No :-9934663577 | Task Start | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 145 | engineer visit the site found the unbalance load upto 47% educate the customer about balancing of load. | CLOSED | Prabhakar Kumar
2 | 211036519 | 2024-01-08 12:40 | 20 | GP3.8604.../ 2420107 | INSTANCE ID :- 100741899 SITE ID :- I-BR-KJUL-ENB-G001 CALL BY CUSTOMER DG ISSUE :- DG MAINS CONTACTOR HOLDING /SELF ALRAM FAULTY NAME :- RAAM NUMBER :- 6206296484 | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | NA | Visit pending | OPEN | Prabhakar Kumar
3 | 211028288 | 31-07-2024 15:37 | 58.5 | T4.8941.../2420377 | LVM ISSUE | Task Start | Shangrila Construction Company | K.C. Diesel Services - SILIGURI | 2 | The conversation happened with GOEM and we will replace this part under warranty from KOEL. | OPEN | Prosenjit saha
1 | 211029819 | 31-07-2024 21:06 | 750 | DV2.8501.C4../2420012 | Diaplay and Starting Issue Call By Customer Name :Robin Singh Mobile No :9990530606 | Open | SPJ. Cold Storage | Vidyut Engineers - Noida | 127.57 | Controller Display was blinking , found battery +ve supply at controller end was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
2 | 211029767 | 31-07-2024 20:09 | 57 | T4.8941.../2320257 | Starting Issue Call By KGD Name:-Aashu Jeshwal Mobile No:-9718850143 | Open | ASIAN GENERATOR AND POWER CO. | Paluck Technologies Ltd. - Ghaziabad | 115 | Battery was discharged, due to battery charger not connected to mains supply.. Connected the same issue resolved. | Closed | Kapil Solanki | CC check
3 | 211029720 | 31-07-2024 19:20 | 20 | GP3.8601.../2320003 | Error Code and Automation Issue And Power Suplay Issue Call By Customer Name :-Mayank . Mobile No :-9580623696 | Open | SPA. Yoga Private Limited | Vidyut Engineers - Noida | 37.2 | Customer Side Mains contractor not holding, No issue in DG set. | Closed | Kapil Solanki
4 | 211029565 | 31-07-2024 18:22 | 1000 | DV8.8502.C4../2420001 & 2420002 | Battery Issue & KRM Issue & Starting Issue Call By - Customer Name - Amandeep No. - 6283342341 | Open | SRG. Developers & Promoters | SAAN Royal Power Solutions Private Limited - Zirakpur |  | KRM connector were not connected properly , connect the same issue resolved . | Closed | Ved Gupta
5 | 211029450 | 31-07-2024 17:51 | 45 | 3H.8951.../2420047 | ISSUE ALARM | Task Start | SGS Weather & Environmental Systems Pvt. Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1 | Line Rejection SR, SPN/FMI: 97/5 (water in fuel sensor), found XDBK 2 and XDBK 4 connections were Interchanged, Connected properly issue resolved. | Closed | Kapil Solanki
6 | 211029110 | 31-07-2024 17:13 | 320 | F6.8802.../2320022 | Tripping issue & Loading issue & Radiator service Call By Customer Name : Arpit Sukla No: 7217763009 | Task Start | Vending Updates India P. Ltd. | Vidyut Engineers - Noida | 157.2 | Voltage dropped from 415 to 249, when DG was running on approx 300 Amp, Suggested to Engineer for Extracted Event log and Data log. | Open | Kapil Solanki | KRM check
7 | 211028990 | 31-07-2024 16:56 | 20 | GP3.8601.../2420046 | Starting issue Call By Customer Name : -Gulshan No:-9671641745 | Open | Arora Agency | Paluck Technologies Ltd. - Gurgaon |  | by mistake SR open by customer , SR will be cancelled | Cancelled | Kapil Solanki
8 | 211028370 | 31-07-2024 15:51 | 250 | F6.8841.../2420041 | Door Look Issue Call By Customer Name :-Arvind Saini Mobile No :-9814526130 | Open | DASHMEHS BUILDERS | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Door lock isse found ,replaceed the lock with new one | Closed | Ved Gupta
9 | 211028318 | 31-07-2024 15:42 | 320 | F6.8802.../2420073 | Tripping Issue Call By Customer Name:-Rishi Pal Mobile No:-7838955880 | Task Start | A. G. Pipes Private Limited | Paluck Technologies Ltd. - Faridabad | 35 | as per koel team instraction . SR open for collect EVNT LOG and DATA loag , DG was tripping with showing ECU protect alarm. | Open | Kapil Solanki | KRM check
10 | 211028246 | 31-07-2024 15:28 | 250 | F6.8841.../2320010 | Black Smoke Issue Call By Customer Name :-Chandrapal Mobile No :-8700424158 | Task Start | SEETA FOODS PVT LTD | Paluck Technologies Ltd. - Faridabad | 523 | Starting issue due to DEF level was low @0% , top up the DEF and air filter was chocked , service due | Closed | Kapil Solanki
11 | 211028190 | 31-07-2024 15:14 | 82.5 | 5H.8901.../2320050 | Under Speed Alram Issue & Starting Issue Call By Customer Name :- Ashwani Kumar Mobile No :- 8448933478 | Open | NPP. Engineering | Paluck Technologies Ltd. - Ghaziabad | 235 |  | Closed | Kapil Solanki
12 | 211026128 | 31-07-2024 10:09 | 15 | GP3.8501.../2320024 | Maintenance Due Alarm Call By Customer Name :-Monoj Kumar Mobile No :-6394828613 | Task Start | Shri Panchmukhi Sewa Trust | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | Engineer visited site but did not found any issue.initiated for cancellation. | Cancelled | Sudhir Awasthi
13 | 211027004 | 31-07-2024 11:37 | 57 | T4.8941.../2320141 | Starting Issue Call By Customer Name :-Shiva Battoo Mobile No :-9718118948 | Task Start | Sinkers & Jacks India | Paluck Technologies Ltd. - Faridabad | 312 | Starting issue, battery discharged battery charger main supply switch was in off condition, corrected the same and also SPN/FMI: 100/3 (oil pressure Flt), checked Oil pressure sensor found ok,clear the DTC. | Closed | Kapil Solanki
1 | 211036595 | 2024-01-08 12:57 | 125.4 | 4H.8041.../2420005 | Display Issue Call By Â Customer Name :-Parveen Arora Mobile No :-9355524030 | Open | R C FOAMS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Rohtak |  | visit pending | Open | Kapil Solanki
2 | 211036576 | 2024-01-08 12:53 | 30 | 3H.8902.../2420334 | Under Speed Alarm Issue Call By KGD Name :-Pradeep Bhati Mobile No :-9911316001 | Open | CHAUDHARY NURSING HOME PVT. LTD. | Vidyut Engineers - Noida | 23.5 | Red lamp on showing on controller , checked DM1 ,DM2 , no DTC found , reset the alarm issue resolved . | Closed | Kapil Solanki | ECU log check
3 | 211036442 | 2024-01-08 12:27 | 500 | DV8.8501.C4../2320061 | Automation Issue Call By Customer Name :-Kishan . Number :-7906268082 | Task Start | Goodworth Electronics Private Limited | Vidyut Engineers - Noida | 70.9 | SPN/FMI -,523583/16 ,1761/15, 523584/15, 3465/1, clear the DTC issue resolved. | Closed | Kapil Solanki | Details required
4 | 211036191 | 2024-01-08 11:40 | 58.5 | T4.8941.../2420592 | Starting Issue Email By-Service Dealer Name:-Sanjeev Jain | Open | D. R. Corporation | Industrial Power Solutions - LUDHIANA |  | customer had not given appointment. Today Engineer will visit site. | Open | Ved Gupta | Detail required
5 | 211036121 | 2024-01-08 11:14 | 500 | DV8.8501.C4../2420059 | Tripping Issue Call By Customer Name :- Jasbir No :- 7060268476 | Task Start | Athens Life Sciences | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 30 | DEF level was low , top up the DEF and educated the customer about the same and over load | Closed | Kapil Solanki
6 | 211036094 | 2024-01-08 11:14 | 500 | DV8.8501.C4../2320039 | Voltage issue Call By Â Customer Name :-Harish Mobile No :-7838173625 | Task Start | Alphine Infra Projects Pvt. Ltd. | Vidyut Engineers - Noida | 35.3 | Customer side meter issue , DG side no issue found . | Closed | Kapil Solanki
7 | 211036071 | 2024-01-08 11:09 | 57 | T4.8941.../2320126 | Starting Issue Email By Service Dealer Name:-ARJUN PANWAR | Task Start | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 921 | starting issue due to battery voltage 7 volt , found battery terminal was loose condition tighten the same issue resolved , service due. | Closed | Kapil Solanki
1 | 211036995 | 2024-01-08 14:39 | 0 | 5H.5106.../2300001 | LUB OIL LEAKAGE | Task Start | Bull Machines Pvt Ltd | Electro Controls - Coimbatore | 624.7 | Oil leakage from oil filling cap because oil filling cap is broken | Closed | Mr. Nanda Gopal | to be share to industrial team
2 | 211036977 | 2024-01-08 14:33 | 40 | 3H.8951.../2420050 | I BOLT CUT PROBLEM Call by : Customer Name : MUHAMMED Contact : 9751342821 | Completed | AK Thanga Maaligai | Bharath Diesel Sales and Service - Dindigul | 50 | Charging alternator I bolt broken. Photo attached | Closed | Mr. Nanda Gopal | Failed part required
3 | 211036661 | 2024-01-08 13:09 | 250 | F6.8841.../2420160 | CSC HOSE CLAMP | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Pattanur | LR | CAC Hose clamp was found loose. Retightened the same. Issue Resolved | Closed | Mr. Nanda Gopal
4 | 211036114 | 2024-01-08 11:25 | 750 | DV2.8501.C4../2320016 | ECU red lamp issue Email By - Service Dealer Name -Geetha | Task Start | Recaero India (P) Ltd., | Surya Power Services - Billekahalli | 41 | ASE visited and checked harness.CAN communication circuit found normal. Problem is still persist same. So, Need help from HO engineering team to disable these kind of secondary and low priority fault codes through INCA software. | Closed | Mr. Prakash S
5 | 211036103 | 2024-01-08 11:18 | 40 | 3H.8951.../2320047 | Diesel Leakage Email By Service Dealer Name:- Sandhya M R | Task Start | THE MALAYALA MANORAMA CO. LTD. | Electro Controls - Kottayam | 2 | Diesel leakage from fuel filter piping crimping area.Photos attached | Closed | Mr Sanjaymon
6 | 211036068 | 2024-01-08 11:08 | 25 | GP3.8702.../2420224 | Engine Not Starting | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Visit Pending | Closed | Mr. Nanda Gopal | engine hunting in with out load and with load, and observed RPM variation 5to 10rpm, then checked the fuel line, then replaced new suction hose and removed the air lock, then started and tested the engine with load, no hunting observed,
7 | 211036041 | 2024-01-08 11:00 | 125.4 | 4H.8041.../2420253 | AMF Panel Problem Call by : Customer Name : Contact : | Task Start | VRK CONSTRUCTIONS | Madhu Engineering Sales & Service - Puzhal, Kavankarai, Chennai | 28.3 | Mains sensing wire found in loose condition, retightened the same. Issue resolved. | Closed | Mr. Nanda Gopal
8 | 211036056 | 2024-01-08 10:58 | 0 | 5H.8901.../2420115 | Water mixing with oil | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Visit pending | open | Mr. Nanda Gopal | efsr report is not available .
9 | 211035866 | 2024-01-08 10:08 | 125.4 | 4H.8041.../2320068 | Starting Problem And Control Panel Problem Call by : Customer Name : Akhilesh Kanth Contact : 8281258592 | Closed | Reserve Bank Staff Quarters | G-Care Diesels Private Limited - Ernakulam | 8 | Controller is not working. Fuse found faulty. | Closed | Mr Sanjaymon | Details required | Photos attached
1 | 211029482 | 31-07-2024 17:59 | 62.5 | T4.8941.../2420119 | Trip_Genset_Low_Voltage | Task Start | Jain Garments | M/s OM Diesels Pvt. Ltd. - HISAR | 54.56 | KRM Generated SR, Tripping issue with showing R,Y,B phase Under voltage alarm found Alternator Terminal plate Y,B phase burnt ,due to Unbalanced load, and also AVR faulty (Need to Replaced) | Open | Kapil Solanki | Cut-off and circular
2 | 211036600 | 2024-01-08 12:58 | 250 | F6.8841.../2420033 | Black Smoke issue Call By Â Service Dealer Name :-Poonam Singh Mobile No :-7722070569 | Open | Kids Clinic India Pvt Ltd | S. R Engines Sales And Service - LUCKNOW | 33 | SPN/FMI: 1761/16( Low DEF level ), top up and educated Customer about the same. | Closed | Sudhir Awasthi
3 | 211036595 | 2024-01-08 12:57 | 125.4 | 4H.8041.../2420005 | Display Issue Call By Â Customer Name :-Parveen Arora Mobile No :-9355524030 | Open | R C FOAMS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Rohtak | 136 | Fuel Sensor issue..Wrong fuel reading showing on display.(0 %) .checked Sensor found Stuck, refitted the same issue resolved. | Closed | kapil Solanki
4 | 211036567 | 2024-01-08 12:56 | 250 | F6.8841.../2420123 | Starting Issue Call By Â Service Dealer Name :-Poonam Singh Mobile No :-7722070569 | Open | Kids Clinic India Pvt Ltd | S. R Engines Sales And Service - LUCKNOW | 14.57 | Starting issue..SPN/FMI: 655/5 (Injector- open load on the power stage), Found Injector wiring was in push back condition, connected properly issue resolved.(photographs attached in EFSR ) | Closed | Sudhir Awasthi
5 | 211036576 | 2024-01-08 12:53 | 30 | 3H.8902.../2420334 | Under Speed Alarm Issue Call By KGD Name :-Pradeep Bhati Mobile No :-9911316001 | Open | CHAUDHARY NURSING HOME PVT. LTD. | Vidyut Engineers - Noida | 23.5 | Checked Event log found Under speed alarm was showing, then checked fuel line found ok , reset the alarm and kept in Under observation. | Closed | Kapil Solanki | KRM check
6 | 211036442 | 2024-01-08 12:27 | 500 | DV8.8501.C4../2320061 | Automation Issue Call By Customer Name :-Kishan . Number :-7906268082 | Task Start | Goodworth Electronics Private Limited | Vidyut Engineers - Noida | 70.9 | SPN/FMI: 1761/16, 3364/31 RELATED TO DEF property detection, 3364/27(related to DEF quality sensor)3364/10, checked LQT sensor found ok refited and clear the DTC issue resolved. | Closed | Kapil Solanki
7 | 211036191 | 2024-01-08 11:40 | 58.5 | T4.8941.../2420592 | Starting Issue Email By-Service Dealer Name:-Sanjeev Jain | Open | D. R. Corporation | Industrial Power Solutions - LUDHIANA | 50 | Over current alarm was showing , found DG running on overload, educated customer to applied load with in limit. | Closed | Ved Gupta
8 | 211036121 | 2024-01-08 11:14 | 500 | DV8.8501.C4../2420059 | Tripping Issue Call By Customer Name :- Jasbir No :- 7060268476 | Task Start | Athens Life Sciences | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 30 | Tripping issue with showing Overload alarm, found DG running on Overload, then balanced the load issue resolved and also Low DEF level alarm , top up and clear the DTC issue resolved. | Closed | Ved Gupta
9 | 211036093 | 2024-01-08 11:14 | 125.4 | 4H.8041.../2320087 | Alarm Issue Call By Customer Name :- Zakir No :- 8376811789 | Task Start | CIPL. Corporate Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 181.8 | SPN/FMI: 5461/0, Flashed latest cal file and clear the DTC issue resolved.. | Closed | Kapil Soalnki
10 | 211036094 | 2024-01-08 11:14 | 500 | DV8.8501.C4../2320039 | Voltage issue Call By Â Customer Name :-Harish Mobile No :-7838173625 | Task Start | Alphine Infra Projects Pvt. Ltd. | Vidyut Engineers - Noida | 35.3 | Customer side panel issue..No issue in DG. | Closed | Kapil Solanki
11 | 211036071 | 2024-01-08 11:09 | 57 | T4.8941.../2320126 | Starting Issue Email By Service Dealer Name:-ARJUN PANWAR | Task Start | Xpert Powergen Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 921 | Starting issue..Checked battery terminal found +ve terminal loose, tighten the same issue resolved. | Closed | Kapil Solnki
12 | 211035993 | 2024-01-08 10:46 | 125.4 | 4H.8041.../2420110 | Starting Issue Email By-Service Dealer Name:-SUNITA | Task Start | K-6 ENTERPRISES | R K Engineers - Meerut | 103 | Fuel Sensor issue.. Erratic fuel reading showing on Display, checked sensor found stuck ( Float not moving), removed and refitted the same issue resolved. | Closed | Sudhir Awasthi
13 | 211035986 | 2024-01-08 10:46 | 20 | GP3.1010.../2300003 | Low Speed Alarm Issue Call By Customer Name :-Ravinder . Mobile No :-9667939908 | Task Start | Hosexperts | Vidyut Engineers - Noida | 41.24 | Fuel Sensor issue..showing only 66 %, but actual fuel was 100 % in tank, checked sensor found Stuck, removed sensor and refitted the same issue resolved. | Closed | Kapil Solanki
14 | 211035980 | 2024-01-08 10:44 | 57 | T4.8941.../2420110 | Fuel Tank Issue Email By-Service Dealer Name:-SUNITA | Task Start | K-6 ENTERPRISES | R K Engineers - Meerut | 103 | Fuel Sensor issue..showing only 35%, but actual fuel was 100 % in tank, checked sensor found Stuck, removed sensor and refitted the same issue resolved. | Closed | Sudhir Awasthi
15 | 211035932 | 2024-01-08 10:38 | 25 | GP3.8702.../2420066 | Starting Issue Call By Â Customer Name :-Vikas Mobile No :-9991400055 | Task Start | Vikas Kataria. | Vishal Power Systems - PANIPAT | 37 | Sometimes DG was tripping with showing Under speed alarm checked fuel line found ok then tighten all panel connection and kept in Under observation for 2 days. | Open | Kapil Solanki | KRM check | KRM does not show any type of issue related under speed .
16 | 211035909 | 2024-01-08 10:25 | 25 | GP3.8702.../2420023 | Amf Panel Issue Email By KGD Name:-Pradeep Tyagi | Task Start | Braj Machines | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 23 | Tripping issue.. Emergency stop alarm was showing found Canopy emergency switch was in pressed condition, release the same issue resolved. | Closed | Kapil Solanki
17 | 211035786 | 2024-01-08 09:48 | 15 | GP3.8501.../2320002 | Red Lamp Alarm Issue Call By Customer Name :-Ajay Wadhawan Mobile No :-9810172765 | Task Start | Dr. Ajay Wadhawan | Vidyut Engineers - Noida | 51 | Low Fuel level, top up and educated Customer about the same. | Closed | Kapil Solanki
18 | 211035784 | 2024-01-08 09:48 | 82.5 | 5H.8901.../2420022 | Amber Lamp On Alarm Issue Call By Customer Name: BABLU SIR Number: 9315329529 | Open | C. L. ENTERPRISES | M/s OM Diesels Pvt. Ltd. - Rohtak | 48 | Low Fuel level, top up and educated Customer about the same. | Closed | Kapil Solanki
19 | 211035767 | 2024-01-08 09:40 | 750 | DV2.8501.C4../2320006 | Tripping issue Call By Customer Name :-Shambhu Kumar Sharma Mobile No :- 7982794922 | Task Start | PREM INDUSTRIES | Vidyut Engineers - Noida | 633 | Starting issue..SPN/FMI: 633/3 , checked fuel line found ok clear the DTC and kept in Under observation. | Open | Kapil Solanki
20 | 211035729 | 2024-01-08 09:10 | 15 | GP3.8501.../2420054 | Automation issue Call By Customer Name :-Vineet Tyagi Mobile No :- 9018674696 | Task Start | Mr. Vineet Tyagi | R K Engineers - Meerut | 18 | Tripping issue with showing Under speed alarm , updated Cal file and (ECU speed sensing disable) Kept in Under observation . | Closed | Sudhir Awasthi | Need to check
21 | 211035727 | 2024-01-08 08:59 | 750 | DV2.8501.C4../2420011 | Â Alarm Issue Call By Customer Name : -Parvesh Kumar No:-9720093797 | Open | Sleek Brake Products | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 487.3 | SPN/FMI :- 6301/2 related to water in fuel , found water in fuel filter , clean the filter issue resolved. | Closed | Kapil Solanki
22 | 211035722 | 2024-01-08 08:43 | 320 | F6.8802.../2420001 | Starting issue Call By Customer Name : -Dulat singh No:-8368574393 | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 100 | SPN/FMI :- 97/2 , found water in fuel tank , clean the tank and issue resolved. | Closed | Kapil Solanki
23 | 211033067 | 2024-01-08 00:28 | 250 | F6.8841.../2320017 | Starting Issue Call By Customer Name:-Rajnikant . No:-7717723481 | Open | SATVIK TECHZONE PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon | 155 | Rain Water entry in canopy . | Closed | Kapil Solanki
24 | 211037579 | 2024-01-08 16:36 | 250 | F6.8841.../2420146 | Battery Issue Call By Customer Name :-Anikit Guptaa Mobile No :-7838033529 | Open | ATLAS POWER & EQUIPMENTS | M/s OM Diesels Pvt. Ltd. - Sonipat | 19.21 | battery was discharge due to battery charger mains connection was broken , correct the same issue resolved | Closed | Kapil Solanki
25 | 211037518 | 2024-01-08 16:22 | 125.4 | 4H.8041.../2320192 | Urea level issue Call By Customer Name :-Arjun Arora Mobile No :-9369800903 | Task Start | Modern Springs | Paluck Technologies Ltd. - Faridabad | 53 | DEF level was low, top up the DEF issue resolved. | Closed | Kapil Solanki
26 | 211037228 | 2024-01-08 15:33 | 200 | 6H.8435.../2420003 | Ad Blue Alarm issue Call By Customer Name :-Mohammad Amjad Mobile No :-8865019331 | Task Start | UPPAL CHADHA HI-TECH DEVELOPERS [P] LTD | Paluck Technologies Ltd. - Ghaziabad | 48 | SPN/FMI:- 3364/8 related to DEF quality, found DEF concentration was 28.5% (need to checked with Refractometer) | Open | Kapil Solanki | Need details. And need to check with refractometer
27 | 211037169 | 2024-01-08 15:20 | 57 | T4.8941.../2420120 | Battery Issue Call By Customer Name :-Hardik Mobile No :-9911069067 | Task Start | ZEM ZIPPERS PRIVATE LIMITED | Vidyut Engineers - Noida | 34 | Battery was discharge due to battery charger mains connection was loose in DG panel , tighten the same issue resolved . | Closed | Kapil Solanki
28 | 211037145 | 2024-01-08 15:11 | 125.4 | 4H.8041.../2320024 | Red lamp alarm Issue Message By Customer Name : Manish Tyagi No : 9643313743 | Task Start | KW. Security & Services Pvt. Ltd. | Vidyut Engineers - Noida | 42.5 | SPN/FMI :- 3218/20,customer is not giving shutdown (Revisit required) | Open | Kapil Solanki | ECU fault check
29 | 211037043 | 2024-01-08 14:59 | 320 | F6.8802.../2420020 | Starting issue Call By Customer Name : -Sarin Khan No:-9650177488 | Task Start | Zenbuzz Cafe LLP. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 74 | As per customer voice Rain water entry in canopy. DG was running ok. | Closed | Kapil Solanki
30 | 211036819 | 2024-01-08 13:46 | 57 | T4.8941.../2320093 | Low Speed issue & Over Loading issue & Tripping issue Call By Customer Name : Rishav Gupta No: 9810539132 | Task Start | ROHIN STEEL INDUSTRIES | OVN Industries Private Limited - New Delhi | 79.26 | DG was tripping with showing over current alarm , found DG was running over load , educated the customer about the same . | Closed | Kapil Solanki
31 | 211036818 | 2024-01-08 13:46 | 125.4 | 4H.8041.../2420044 | Starting Issue call by customer : Name ;-Deepak Kumar No : -9416631031 | Task Start | Bharatiya Janata Party | M/s OM Diesels Pvt. Ltd. - Rohtak | 57 | Starting issue.. Due to emergency switch was pressed condition correct the same issue resolved. | Closed | Kapil Solanki
32 | 211036801 | 2024-01-08 13:45 | 500 | DV8.8501.C4../2320035 | Trip_Genset_Low_Voltage | Task Start | Sidhi International Metal Alloys P. Ltd. | Paluck Technologies Ltd. - Faridabad | 131 | KRM generated SR engineer did not found load related issue ,checked on load , SPN/FMI - 523576/0 clear the DTC , Issue resolved . | Closed | Kapil Solanki | KRM check
33 | 211036787 | 2024-01-08 13:42 | 250 | F6.8841.../2420004 | Starting Issue Email By Service Dealer Name:-ARJUN PANWAR | Task Start | TATA TELESERVICES LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 129 | Rain Water entry in canopy ,already SR open on GOEM portal | Closed | Kapil Solanki
34 | 211036737 | 2024-01-08 13:26 | 82.5 | 5H.8901.../2320033 | Starting Issue Email By-Service Dealer Name:-Shiv | Task Start | MIRA ENGINEERING PVT LTD | Vidyut Engineers - Noida | 33.1 | SPN/FMI :- 1761/18,1761/14,1761/17,3364/31,DEF level was not showing ,need to programming. | Open | Kapil Solanki
35 | 211036676 | 2024-01-08 13:10 | 500 | DV8.8501.C4../2320081 | Coolant and Oil Leakage Issue Call By Customer Name :-Rahul Kumar Mobile No :8227001150 | Task Start | Ozone Overseas Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | As previously disscussed,Oil coolar puncture, but cleaning not proper ,then suggested to SD team for cleaning with K clean, and also oil leakge from Oil Expension plug | Open | Gourav Sharma
36 | 211038988 | 2024-01-08 20:41 | 250 | F6.8841.../2320023 | Fuel Sensor Issue and Display Issue Call by Customer Name - Shamsher Singh Number - 9896901713 | Open | Haryana Police Housing Corporation Panchkula | Vishal Power Systems - Karnal | 20 | Customer want to know , fuel consumption and fuel tank capacity, no issue in DG side . | Closed | Kapil Solanki
37 | 211038528 | 2024-01-08 18:00 | 160 | 6H.8475.../2320015 | Amber Lamp Issue Call By Customer Name :- Vikash Sharma Mobile No :- 9812514442 | Open | Ambadi Enterprise | Vishal Power Systems - PANIPAT | 54 | DEF level was low topup the DEF and educated the customer about | Closed | Kapil Solanki
38 | 211037796 | 2024-01-08 17:22 | 250 | F6.8841.../2320039 | Tripping Â Issue Call By Customer Name :-Dinesh . Mobile No :-9968283648 | Task Start | Kendriya Vihar II Apartments Owners Association | Vidyut Engineers - Noida | 64.45 | customer complain about tripping issue ,engineer did not found issue ,checked event log found emergency stop alarm , checked emergency switch connection found ok . | Closed | Kapil Solanki
1 | 211028461 | 31-07-2024 16:05 | 25 | GP3.8702.../2420249 | Oil pressure flt-vlt high shown in controller | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | High lub oil pr. Shown, after replace the pump issue resolved | Closed | Jagdeep Saini | Need to check
2 | 211028432 | 31-07-2024 16:01 | 25 | GP3.8702.../2420297 | Oil pressure flt-vlt high shown in controller | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | High lub oil pr. Shown, after replace the pump issue resolved | Closed | Jagdeep Saini | Need to check
3 | 211027310 | 31-07-2024 12:32 | 125.4 | 4H.8041.../2420522 | JOB WORK | Task Start | Shreyas Hospital | Mahalaxmi Diesels - Kolhapur | 27 | 6595/0 ,4225/1 4095/ related to nox limit exceeds. Check all the connections found ok, observed chg. Alternator 40 amp. fuse burn so that battery set discharged replce the fuse and chared the battery issue resolved | 6595/0 ,4225/1 4095/ related to nox limit exceeds. Check all the connections found ok, observed chg. Alternator 40 amp. fuse burn so that battery set discharged replce the fuse and chared the battery issue resolved |  | Neec to check for CAL file update
4 | 211027510 | 31/07/2024 13:15:07 | 20 | GP3.1010.../2200002 | Starting Issue Call By Customer Name :- Prshant Pawar Mobile No :-8888880055 | Task Start | DICKSONS ENGINEERING CO.PVT.LTD. | Unique Techno Services Pvt Ltd. - Gandhidham | 2829 | Communication error showing in the controller.Checked the can line and ECU power supply found OK.CAN connector resistance 120 omh. | Open | Amit Shandilya | Drtails required
1 | 211040396 | 2024-02-08 07:37 | 58.5 | T4.8941.../2420778 | . | Task Start | RISHIPAL GUPTA & SONS | Pratap Diesels Pvt. Ltd. - Alwar | LR | Line rejection SR, DG in jakson plant Wiring harness issue.. EDO placed for the same. | Open | Gourav Sharma
2 | 211040431 | 2024-02-08 09:26 | 58.5 | T4.8941.../2420761 | Unstable Alarm | Closed | Brhamrishi Mission Sr Secondary School | Industrial Power Solutions - LUDHIANA | 16 | Unbalanced load on DG, Iniciated for Cancellation. | Cancelled | Ved Gupta
3 | 211040610 | 2024-02-08 10:30 | 30 | 3H.8902.../2320048 | Oil Issue Email By-Service Dealer Name:-Vidyut Engineers | Task Start | PARNAMI PUMP & PROJECT PVT.LTD | Vidyut Engineers - Noida | 1987 | Rain water entry (water mix in fuel tank ) celan the tank and change fuel filter issue resolveed. | Closed | Kapil Solanki | Site condition
4 | 211040917 | 2024-02-08 11:31 | 320 | F6.8802.../2420005 | Trip_Genset_Low_Voltage | Open | Alko Plus Technosafe Private Limited | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 110 | KRM Generated SR, found overload on DG, educated customer about the same. | Closed | Kapil Solanki
5 | 211040969 | 2024-02-08 11:43 | 500 | DV8.8501.C4../2320043 | Synchronization Call By Customer Name : Jitendra Kumar No : 9560025340 | Closed | S-CCI INDIA PVT LTD. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 5 | Synchronization issue..SR open for Droop CT installation. | Open | Gourav Sharma
6 | 211040987 | 2024-02-08 11:54 | 320 | F6.8802.../2320022 | Loading and Tripping and Voltage Issue Call By Customer Name :-Arpit Sukla Mobile No :-7217763009 | Closed | Vending Updates India P. Ltd. | Vidyut Engineers - Noida | 177.3 | Unbalanced load on DG, balanced the load and also SPN/FMI: 3031/14, 3364/8, 1761/16, 97/2 ,110/0, 520522/16, checked Water anf fuel sensor clean and refitted then Flashed latest cal file issue resolved. | Closed | Kapil Solanki
7 | 211041068 | 2024-02-08 12:08 | 160 | 6H.8475.../2320011 | Oil leakage Issue Call By Customer Name : Anit . No : 7011180879 | Closed | Kashish Plastic Industries | Paluck Technologies Ltd. - Ghaziabad | 85 | Oil Leakage from oil filter O ring,fitted properly issue resolved and also Low DEF level clear the DTC. | Closed | Kapil Solanki
8 | 211041074 | 2024-02-08 12:08 | 125.4 | 4H.8041.../2420240 | Red Lamp Alarm Issue Call By Customer Name :-Arjun Mobile No :-9416148211 | Task Start | Dhani Power Solutions | M/s OM Diesels Pvt. Ltd. - Rohtak | 25 | Low DEF level, top up and clear the DTC issue resolved. | Closed | Kapil Solanki
9 | 211041164 | 2024-02-08 12:33 | 15 | GP3.8501.../2420084 | Low Speed Alarm issue Call By Customer Name :-G. S. Sandhu. Mobile No :-9996610001 | Closed | G. S. Sandhu. | SAAN Royal Power Solutions Private Limited - Zirakpur | 49 | under speed alarm issue.. and adjust MPU gap and reset the alarm kept in Underobservation. | Open | Ved Gupta
10 | 211041200 | 2024-02-08 12:27 | 40 | 3H.8951.../2420022 | stating | Closed | BHARTI AIRTEL LIMITED | OVN Industries Private Limited - New Delhi | 12.33 | Auto starting issue.. Engineer visited site checked DG found ok. No issue in DG. | Closed | Kapil Solanki | KRM check | KRM does not send mail for KRMstarting.
11 | 211041288 | 2024-02-08 12:52 | 125.4 | 4H.8041.../2420068 | Starting Issue Call By Customer Name :-ilshDas Bhandari Mobile No :-8894106972 | Task Start | A. P. Associates | OVN Industries Private Limited - New Delhi |  | Battery was discharged, battery charger not connected | Closed | Kapil Solanki | Claim rejection
12 | 211041387 | 2024-02-08 13:08 | 125.4 | 4H.8041.../2420177 | Amber Lamp On alarm issue Call By Customer Name :- Chandra Mohan Mobile No :- 9911823339 | Task Start | P. V. L. Tag Factory INDIA Pvt. Ltd. | Vidyut Engineers - Noida | 28 | Starting issue..SPN/FMI: 3364/10 (DEF tank - Diagnostic fault check for connection invalied), 520527/18, 3364/27, 3031/14, found 2A1 to 2A8 fuse blown out, changed the same issue resolved. | Closed | Kapil Solanki
13 | 211041422 | 2024-02-08 13:25 | 125.4 | 4H.8041.../2420247 | Starting Issue Call By Customer Name :-Vicky Chaudhary Mobile No :-9891723444 | Task Start | SR. Power Engineers | Paluck Technologies Ltd. - Ghaziabad | 15 | Starting issue..SPN/FMI; 2802/4, found battery was discharged due to charger not connected to mains supply, connected properly issue resolved. | Closed | Kapil Solanki | SD claim reject
14 | 211041581 | 2024-02-08 14:13 | 40 | 3H.8951.../2320004 | Oil Consumption issue and Preventive Maintenance Call By Customer Name :-Bhavy Mobile No :-7087038415 | Closed | Waves Enterprises. | Vidyut Engineers - Noida | 94.25 | Fuel Sensor issue..erractic fuel reading showing on display camparing with tank, removed sensor and clean and refitted the same issue resolved. | Closed | Kapil Solanki
15 | 211041598 | 2024-02-08 14:20 | 125.4 | 4H.8041.../2420185 | Starting issue Call By Customer Name : Mancu .. No:- | Task Start | TSL. Electro Power Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 41 | Starting issue..battery was discharged 5 V, mains connection problem by customer end. (Kept in Under observation ) | Open | Kapil Solanki
16 | 211041793 | 2024-02-08 15:15 | 58.5 | T4.8941.../2420031 | Starting Issue Call By KGD Name:-Aashu Jeshwal Mobile No:-9718850143 | Task Start | Alluri Sitarama Raju Vignana Kendram | Vidyut Engineers - Noida | 84.2 | Oil leakage, but leakage source was not found, top up oil then DG running ok. No any leakage. | Closed | Kapil Solanki
17 | 211041874 | 2024-02-08 15:38 | 30 | 3H.8902.../2420194 | Starting Issue Call By Customer Name :-Rupesh Mobile No :-9773975364 | Task Start | Anand Auto Service. | OVN Industries Private Limited - New Delhi | 1.4 | Starting issue..battery was discharged 6 V, battery charger not connected to mains supply connected the same issue resolved. | Closed | Kapil Solanki
18 | 211041993 | 2024-02-08 15:54 | 82.5 | 5H.8901.../2320086 | Tripping Issue Call By Customer Name : Khaniyakumar . No : 8051626265 | Task Start | PSG. International | Paluck Technologies Ltd. - Faridabad | 99 | Low DEF level, top up and clear the DTC issue resolved. | Closed | Kapil Solanki
19 | 211042027 | 2024-02-08 16:02 | 57 | T4.8941.../2320065 | Starting issue Call By Customer Name VS TRIPATHI No:-9560781210 | Task Start | PIONEER ENGINEERING & AUTOMOTIVE CORPORATION | Paluck Technologies Ltd. - Faridabad | 355.52 | Starting issue checked event log SPN/FMI: 633/3 (Inlet metering valve 1- vlt high), checked fuel line no issue found after that By pass the Water seprater Filter assly issue resolved. | Closed | Kapil Solanki
20 | 211042428 | 2024-02-08 16:51 | 320 | F6.8802.../2320041 | Diesel Pump Issue Call By - Customer Name - Bunty No. - 8000289498 | Task Start | Mama Foods | Pratap Diesels Pvt. Ltd. - Alwar | 134 | Hand priming assly faulty, replaced the same issue resolved. | Closed | Gourav Sharma
21 | 211042544 | 2024-02-08 17:03 | 125.4 | 4H.8041.../2420098 | Tripping Issue Red Lamp On Alarm Issue Call By Customer Name :-Tarun Kumar Mobile No :-9205444606 | Task Start | SAAOL PHARMA PRIVATE LIMITED | Vidyut Engineers - New Delhi | 107 | Tripping issue..Panel Emergency switch pressed by customer end ,release it and educated customer about the same. | Closed | Kapil Solanki
22 | 211042644 | 2024-02-08 17:38 | 125.4 | 4H.8041.../2320086 | Load Issue Email By - Service Dealer Name - Saurabh Rajput | Task Start | Total Construction | Paluck Technologies Ltd. - Gurgaon | 1535 | Customer repoted Hunting issue.. But engineer did not found Such type of issue.. DG running ok and also both Filter to be change and kept in Under observation | Open | Kapil Solanki
1 | 211044697 | 2024-03-08 14:53 | 15 | GP3.8501.../ 2420170 | Starting Issue Call By Customer Name-Pappu Chouhan Mobile No- 9955927913 | Task Start | Alok Shyandan | United Machinery Sales And Service - Dhanbad | 2 | mains under voltage upto 160V,due to which customer complains that DG not stop even after mains available. | OPEN | Prabhakar Kumar
2 | 211044254 | 2024-03-08 12:44 | 25 | GP3.8702.../ 2420144 | High Voltage Issue Call By :- Customer Nmee :-Kanhaiya Kumar Number :- 6204991612 | Open | Basant Bahar Sweets | Globalline India Services Private Limited - Biharsharif | NA | visit pending | OPEN | Prabhakar Kumar
3 | 211044202 | 2024-03-08 12:35 | 58.5 | T4.8941.../ 2420312 | Automation Issue Call By Customer Name :-Supriya Sinha Mobile No :-9434031039 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | NA | Visit pending | OPEN | Prosanjit saha
4 | 211043616 | 2024-03-08 10:15 | 58.5 | T4.8941.../ 2420302 | Tripping Issue Call By Customer Name :-laddu ... Mobile No :-9934663577 | Task Start | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 169 | Mains over voltage upto 260 V AC,due to which DG remains on start even after mains available. | OPEN | Prabhakar Kumar
5 | 211036519 | 2024-01-08 12:40 | 20 | GP3.8604.../ 2420107 | INSTANCE ID :- 100741899 SITE ID :- I-BR-KJUL-ENB-G001 CALL BY CUSTOMER// DG ISSUE :- DG MAINS CONTACTOR HOLDING / SELF ALRAM FAULTY NAME :- RAAM NUMBER :- 6206296484 | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | 59.46 | Engineer visit the site found that mains contactors coil got burnt also the 11F8 MCB trip. No alarm/fault code on event log. suspected that it is due to mains under voltage. | OPEN | Prabhakar Kumar | Failed part
1 | 211043339 | 2024-03-08 09:14 | 160 | 6H.8475.../2420032 | Amber Alaram issue Call By Customer Name :- Amit kumar Mobile No :- 8447323227 | Closed | Airpack Compressor Teknologies P. Ltd. | Paluck Technologies Ltd. - Faridabad | 48 | DEF level was low , and SPN/FMI - 3364/8,1761/16,4094/1,516166/0 , customer stop the DG by double tap , educated the customer about the same issue resolved. | Closed | Kapil Solanki
2 | 211043347 | 2024-03-08 09:23 | 500 | DV8.8501.C4../2320030 | Tripping Issue Call By Customer Name - Bijendra Kumar Mo No -7633873576 | Closed | Sobha Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 206 | Emergency stop alarm was showing on controller , found override switch wire was open condition correct the same issue resolved | Closed | Kapil Solanki
3 | 211043407 | 2024-03-08 08:43 | 160 | 6H.8475.../2420025 | Coolant Consumption Issue Call By Customer Name :-Mustak Mobile No :-9058614379 | Closed | M/s. SHREERAM CONCRETE | OVN Industries Private Limited - New Delhi | 989.49 | Customer complain about high coolant consumption , v belt ok | Open | Kapil Solanki
4 | 211043550 | 2024-03-08 10:04 | 125.4 | 4H.8041.../2420116 | Fuel Tank Cap Faulty Issue Email By - Service Dealer Name -Amitabh Kushwaha | Task Start | GURU HARKRISHAN CASTING | Paluck Technologies Ltd. - Faridabad | 72 | Fuel tank cap faulty ( locking issue) replaced with new one issue resolve | Closed | Kapil Solanki
5 | 211043576 | 2024-03-08 10:08 | 20 | GP3.8601.../2320025 | Starting Issue Email By - Service Dealer Name -Rahul Sharma | Closed | Supreme Enterprises. | M/s OM Diesels Pvt. Ltd. - HISAR | 68 | Air lock issue , air release from water seperator filter issue resolved | Closed | Kapil Solanki
6 | 211043597 | 2024-03-08 10:08 | 58.5 | T4.8941.../2420172 | protection lamp warning & water in fuel self-start | Closed | Primus Emergency & Critical Care Hospital | Pratap Diesels Pvt. Ltd. - JAIPUR | 1 | Line Rejection SR, SPN/FMI: 97/5 (water in fuel sensor), found XDBK 2 and XDBK 4 connections were Interchanged, Connected properly issue resolved. | Closed | Gourav Sharma
7 | 211043728 | 2024-03-08 10:45 | 200 | 6H.8435.../2420005 | V- Belt Abnormal sound issue Call by customer Name:- Krishnanandan .. No:- 9540678513 | Closed | Rani Electrodes Limited Unit II. | Paluck Technologies Ltd. - Faridabad | 99 | abnormal sound from radiator side , found V belt was loose tighten the same issue resolved | Closed | Kapil Solanki
8 | 211043856 | 2024-03-08 11:14 | 125.4 | 4H.8041.../2420140 | Over Load issue Call BY Customer Name :- Manjay No :- 7982970631 | Open | BD. Enterprises | Paluck Technologies Ltd. - Faridabad |  | Customer side VMC and CNC machine was tripped, Joint visit with Jakson team and required AVR 150 SR will be cancel | cancelled | Kapil Solanki
9 | 211044111 | 2024-03-08 12:07 | 750 | DV2.8501.C4../2320006 | Tripping issue Call By Customer Name :-Shambhu Kumar Sharma Mobile No :- 7982794922 | Closed | PREM INDUSTRIES | Vidyut Engineers - Noida | 663.35 | SPN/FMI :- 97/2 ,6301/2, 4426/15 ,633/3, 1761/15, 523584/15, 110/0, 110/16, 523531/7, checked water separator found ok , clear the DTC issue resolved | Closed | Kapil Solanki | KRM check under observation
10 | 211044391 | 2024-03-08 13:21 | 125.4 | 4H.8041.../2420450 | Starting Issue Call By :- Customer Name :- Shibu Number :- 9610597553 | Closed | Minraj Sapling L.V.F. LLP. | OVN Industries Private Limited - New Delhi | 14.5 | Automation issue negative supply was from customer side , DEF level was low @49% , educated the customer about the same issue resolved . | Closed | Kapil Solanki
11 | 211044409 | 2024-03-08 13:28 | 30 | 3H.8902.../2320126 | Lighting Issue Call BY Customer Name :- Sazid No :- 9350483086 | Task Start | Sazid Spare Parts | Vidyut Engineers - New Delhi | 102 | Customer side light was blinking on load , found unbalance load ( 7A,6A,17A) also Power factor was 0.35 . | Closed | Kapil Solanki
12 | 211044552 | 2024-03-08 14:12 | 40 | 3H.8951.../2320050 | Exhaust Pipe issue Call By Customer Name:- Omveer Singh Mobile No :- 7011204885 | Closed | Chaudhary Generator Service | Vidyut Engineers - Noida | 1639.25 | As previous discussed (SPN/FMI:- 110/16 , found silencer expension bellow was broken) customer do not agree to purchase expansion bellow. | Closed | Kapil Solanki
13 | 211044597 | 2024-03-08 14:17 | 200 | 6H.8435.../2320024 | Error Code Issue Email By - Service Dealer Name - Paluck Technologies Limited | Task Start | AEW PROTECH PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad |  | SR will be cancel . Customer not giving shutdown | cancelled | Kapil Solanki | KRM check
14 | 211044694 | 2024-03-08 14:53 | 125.4 | 4H.8041.../2420189 | High voltage issue Call By Customer Name :-Ajit khtana Mobile No :-9828859584 | Task Start | M/s. Star Light Moulding Product Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | SR Will be cancel . Customer had not given appointment | cancelled |  | KRM check
15 | 211044773 | 2024-03-08 15:20 | 250 | F6.8841.../2420028 | Trip_Genset_Low_Voltage | Closed | Santokh Industries | Paluck Technologies Ltd. - Faridabad | 279 | KRM generate SR , checked on load found ok. | Closed | Kapil Solanki | KRM check
16 | 211044780 | 2024-03-08 15:20 | 40 | 3H.8951.../2320091 | Over Heating Issue Error Code Issue Call By Customer Name :-Shubham Mittal Mobile No :-9802626001 | Open | Tisha Agro Industries LLP. | M/s OM Diesels Pvt. Ltd. - Rohtak |  | Expension Below broken, (Need to replaced) | Open | Kapil Solanki
17 | 211044802 | 2024-03-08 15:26 | 160 | 6H.8475.../2320006 | Coolant Leakage Issue Call By Customer Name :pwan kumar . No 9354544627 | Closed | ENERDYNE DEVICES PVT. LTD. | Vidyut Engineers - Noida | 110.6 | Coolant leakage from radiator clamp , found clamp was loose condition , tighten the same issue resolved . | Closed | Kapil Solanki
18 | 211044980 | 2024-03-08 16:21 | 125.4 | 4H.8041.../2320073 | Starting issue Call By Customer Name : Ajish Gupta No:- 9818281453 | Task Start | GUPTA SAREES CENTRE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 263 | Starting issue..SPN/FMI :- 654/5 , found 4 no injector wire was broken , correct the same issue resolved | Closed | Kapil Solanki
19 | 211045698 | 2024-03-08 21:04 | 58.5 | T4.8941.../2420577 | Automation Issue Call By :- Customer Name :- Yuvraj Mittal Number :- 9873793114 | Open | Adworth Media Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | visit pending | Open | Kapil Solanki
20 | 211045718 | 2024-03-08 22:03 | 320 | F6.8802.../2320028 | Starting Issue Call By Customer Name :-Mahender . Mobile No :-9650384694 | Open | Arocon rainbow | Paluck Technologies Ltd. - Ghaziabad |  | starting issue with showing emergency stop alarm . Found the 4 pin connector was internally loose , bypass the supply issue resolved . | Open | Kapil Solanki | Communication to QA
1 | 211040653 | 2024-02-08 10:38 | 320 | F6.8802.../2420097 | Door lock Issue Email By - Service Dealer Name -MEERA DEVI | Closed | JOHNS | Electro Controls - Mavalikara | 32 | Door was not closing due to door lock liver loose condition, tighten the liver. Issue resolved. | Closed | Mr Sanjaymon | GOEM portal
2 | 211038860 | 2024-01-08 18:24 | 20 | GP3.8601.../2420126 | Starting Problem /Black smoke Call by : Customer Name :Saidulu Contact :9989648960 | Closed | Manula Ramasahaym Reddy. | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 2 | No abnormality found on site. No error code found in KRM. | Closed | Mr. Saleem | Under observation
3 | 211038853 | 2024-01-08 18:20 | 125.4 | 4H.8041.../2420262 | Error code problem Call by: Dealer Name : Prathab Contact :8870478403 | Closed | STANDARD SURFA CHEM INDIA PRIVATE LIMITED | Bharath Diesel Sales and Service - Pattanur | 22.03 | SPN: 516166,FMI: 0 Fault code which is related to Hot shutdown. Educated the customer | Closed | Mr. Nanda Gopal
4 | 211029604 | 31-07-2024 18:31 | 58.5 | T4.8941.../2420155 | DG ISSUE | Task Start | LG ELECTRONICS INDIA PRIVATE LIMITED | Sri Manjunath Technical Services - Vijaywada | LR | SPN : 1485 , FMI :4, SPN: 1485 , FMI:5 , SPN 97 FMI:5 , Monday again ASE planned to visit the site . | Closed | Mr. Saleem | XBD2 wiring harness connection interchanged with XBD4 during commissiong . customer deny to load at that time , it is under observation .
5 | 211044421 | 2024-03-08 13:27 | 40 | 3H.8951.../2420135 | Voltage Fluctuation Issue Email By-Service Dealer Name:- G-Care Diesels Pvt | Closed | Shijo George. | G-Care Diesels Private Limited - Muvattupuzha | 46 | found variable load due to maintenance work(welding, grinding,lift mainatanace, vaccum cleaning,and all other machineries).found voltage variation due to construction works.all machineries are connected to dg.found load 16A,1A,2A respectively.advice the customer to provide stable load. | Closed | Mr Sanjaymon
6 | 211043555 | 2024-03-08 09:58 | 82.5 | 5H.8901.../2420103 | Starting problem Call by : customer Name : Sridhar Contact : 9585551808 | Closed | Amman Veg Restaurant | Madurai Electro Controls - Ellis Nagar | 3.49 | Wiring issue in customer panel side panel and loose connection in relay board.Also Silencer bolt is missing. | Closed | Mr. Nanda Gopal | Underspeed Alarm & Fail to stop alarm | CC check
1 | 211048899 | 2024-05-08 18:39 | 15 | GP3.8501.../2420005 | DG ISSUE | Open | BHARTI AIRTEL LIMITED | United Machinery Sales And Service - Asansol | NA | Visit pending | open | Prosenjit saha
2 | 211047842 | 2024-05-08 14:16 | 30 | 3H.8902.../2420098 | Starting Issue Email By Service Dealer Name:-Prem Roy | Closed | A. K. Stone Products Pvt. Ltd. | United Machinery Sales And Service - Md. Bazar Branch | 15 | Engineer attend the site and clearly shows that there is the misalignment issue at the back door of the DG set, the rain water was entering the engine .The GOEM team visited the site for rectify the issue and aligned the door properly then problem resolved. | Closed | Prosenjit saha
3 | 211044202 | 2024-03-08 12:35 | 58.5 | T4.8941.../2420312 | Automation Issue Call By Customer Name :-Supriya Sinha Mobile No :-9434031039 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | NA | Visit pending | open | Prosenjit saha
4 | 211046736 | 2024-05-08 10:26 | 30 | 3H.8902.../ 2320171 | Power Supply Issue Call By Customer Name:- Raju Kumar Mo No:-8709638762 | Open | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | NA | visit pending | OPEN | Prabhakar Kumar
5 | 211044254 | 2024-03-08 12:44 | 25 | GP3.8702.../ 2420144 | High Voltage Issue Call By :- Customer Nmee :-Kanhaiya Kumar Number :- 6204991612 | Task Start | Basant Bahar Sweets | Globalline India Services Private Limited - Biharsharif | 19.1 | Unbalance load issue educate the customer to balance the load. | OPEN | Prabhakar Kumar
6 | 211043616 | 2024-03-08 10:15 | 58.5 | T4.8941.../ 2420302 | Tripping Issue Call By Customer Name :-laddu ... Mobile No :-9934663577 | Open | Novel Hospital | Globalline India Services Private Limited - Muzaffarpur | 169 | requested to cancel the SR | OPEN | Prabhakar Kumar
7 | 211036519 | 2024-01-08 12:40 | 20 | GP3.8604.../ 2420107 | INSTANCE ID :- 100741899 SITE ID :- I-BR-KJUL-ENB-G001 CALL BY CUSTOMER// DG ISSUE :- DG MAINS CONTACTOR HOLDING /SELF ALRAM FAULTY NAME :- RAAM NUMBER :- 6206296484 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | 56.46 | contactor will we changed along with VMR. | OPEN | Prabhakar Kumar
S.no | 211043876 | 2024-03-08 11:25 | 125.4 | 4H.8041.../2420581 | ENGINE LOAD ISSUE Email By - Service Dealer Name - SUNITA | Closed | Harish Chemical Products | R K Engineers - Meerut | 8 | Jerk load on DG , educated the customer about the same issue resolved. | Closed | Sudhir Awasthi
1 | 211043901 | 2024-03-08 11:34 | 30 | 3H.8902.../2320041 | Need to be expansion bellow change Email By Service Dealer Name:-Javed Khan | Task Start | Bhakoo Farm | Vidyut Engineers - New Delhi | 80 | Expansion bellow was damage , replace the same issue resolved. | Closed | Kapil Solanki | Failed part
2 | 211044489 | 2024-03-08 13:42 | 30 | 3H.8902.../2320170 | Under Speed Alarm Issue Call By Customer Name:Puneet .. Mobile No:9914556324 | Closed | Shri Ambey Steel Industries, | SAAN Royal Power Solutions Private Limited - Zirakpur | 18 | Air lock issue , air release from water separator filter , also unblace load educated the customer about the same issue resolved | Closed | Ved Gupta
3 | 211044780 | 2024-03-08 15:20 | 40 | 3H.8951.../2320091 | Over Heating Issue Error Code Issue Call By Customer Name :-Shubham Mittal Mobile No :-9802626001 | Open | Tisha Agro Industries LLP. | M/s OM Diesels Pvt. Ltd. - Rohtak |  | expansion bellow was damaged , expansion bellow will be change tomorrow. | Open | Kapil Solanki | Failed part
4 | 211044849 | 2024-03-08 15:37 | 40 | 3H.8951.../2420357 | Stopping Issue Call By Customer Name :-Rajesh . Mobile No :-6284449738 | Closed | Dr. Vineets Healtcare Centre | SAAN Royal Power Solutions Private Limited - Zirakpur | 11 | Automation issue , customer side panel issue (B phase was broken ) correct the same issue resolved. | Closed | Ved Gupta
S.no | 211045977 | 2024-04-08 10:08 | 160 | 6H.8475.../2420020 | Heating issue call by customer Name Manoj Kumar No9582943302 | Task Start | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad | 489 | Coolant overflow from recovery tank (DG temperature was normal 75 degree C ) | Open | Kapil Solanki | KRM check | Check KRM wire.
6 | 211046000 | 2024-04-08 11:23 | 30 | 3H.8902.../2420330 | Under Speed Alarm Call by customer Name - Nikil Number -9958901282 | Task Start | Vee Kay Industries. | Paluck Technologies Ltd. - Faridabad | 9 | Air lock issue , air release from water separator filter issue resolved , under observation. | Open | Kapil Solanki
7 | 211046024 | 2024-04-08 12:16 | 320 | F6.8802.../2320017 | Engine Overheating Email By Sevice Dealer Name:-Vikas Saini | Task Start | MT AUTOCRAFT | M/s OM Diesels Pvt. Ltd. - Rohtak | 249.17 | SPN/FMI - 110/16 related to high coolant temp , found radiator was choked ,clean the same and fuel level was not showing on controller and Air intake manifold gasket leak . Need to check . | Open | Kapil Solanki | One pager
8 | 211046073 | 2024-04-08 14:13 | 30 | 3H.8902.../2320075 | Under speed alarm issue Call by customer Name - Suresh Kumar Number -9891105818 | Task Start | GRACE POWER & ACOUSTICS | Vidyut Engineers - New Delhi | 3.52 | Customer complain about under speed alarm , engineer did not found any issue ,checked the fuel line and air line found ok , checked manual and auto started found ok. | Closed | Kapil Solanki
9 | 211046082 | 2024-04-08 14:47 | 500 | DV8.8501.C4../2320083 | Automation Issue Call By Customer Name: Sanjay Kumar Number:9068855090 | Task Start | Friction Metal Fibers (I) Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Automation issue , negative supply was missing from customer side , connect the same issue resolved . | Closed | Kapil Solanki
10 | 211046151 | 2024-04-08 16:54 | 40 | 3H.8951.../2320077 | Maintenance Due Alarm & Coolant issue Call By Customer Name :-Vipul Mobile No :-9557676767 | Task Start | Srinivas Creamics | Espiem Engines & Machines (P) Limited - Aligarh |  | SR will be cancel . Need to CSP | Cancelled | Sudhir Awasthi
11 | 211046205 | 2024-04-08 20:31 | 20 | GP3.8601.../2320050 | low Speed Issue And Starting Issue Call By Customer Name :-Neeraj Mongia Number :-9354299887 | Open | M/S. Muskan Cosmatics | Paluck Technologies Ltd. - Gurgaon |  | visit pending | Open | Kapil Solanki
S.no | 211047204 | 2024-05-08 12:25 | 62.5 | T4.8941.../2420124 | Starting Issue Call By Â Customer Name :-Arun Kumar Sharma Mobile No :-9811071219 | Task Start | Bhishma Bhatia | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 48 | Fuel sensor issue..erratic reading showing on display 65% ,and also showing 65 % in analog meter, but actual 100 % fuel was in tank, checked resistance found ok, removed sensor and refitted the same but issue not resolved. (As per engineer observation, flot was stuck ) | Open | Kapil Solanki
1 | 211047213 | 2024-05-08 12:25 | 62.5 | T4.8941.../2320245 | Door Loack issue Call By Customer Name :-Somveer Mobile No :- 8607043191 | Open | R. P. Stone Clinic Pvt. Ltd. | Vishal Power Systems - PANIPAT | 182 | Door lock issue... adjust the lock issue resolved. | Closed | Kapil Solanki
2 | 211047216 | 2024-05-08 12:25 | 320 | F6.8802.../2420061 | Overheating issue Call By Customer Name : -Birj mohan singh No:-8528596847 | Task Start | Reliance Fire Engineers | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 17 | Overheating issue..there is no Proper Ventilation , educated customer for ducting. | Closed | Kapil Solanki
3 | 211047434 | 2024-05-08 12:58 | 125.4 | 4H.8041.../2420380 | Amber lamp Alarm Issue Call By Customer Name :-Arvind Kumar Mobile No :-9810573785 | Task Start | Deepa Enterprises | Paluck Technologies Ltd. - Faridabad | 88 | SPN/FMI: 1761/16, 520528/31, low DEF level , top up and educated customer about the same. | Closed | Kapil Solanki
4 | 211047487 | 2024-05-08 13:09 | 57 | T4.8941.../2320014 | Starting Issue Call By Customer Name:- Rupesh Mo No:-8076486197 | Closed | Goel Selection | OVN Industries Private Limited - New Delhi | 8.18 | Starting issue.. Found suction line bolt loose , tighten the same issue resolved. | Closed | Kapil Solanki
5 | 211047816 | 2024-05-08 14:14 | 125.4 | 4H.8041.../2320137 | Red lamp issue Call By Customer Name :-Amarjeet Mobile No :- 9873530243 | Task Start | Kamal Enterprises | Vidyut Engineers - Noida | 25.44 | Low DEF level , top upand educated Customer about the same. | Closed | Ved Gupta
6 | 211047896 | 2024-05-08 14:33 | 30 | 3H.8902.../2320175 | Starting problem call by customer Name.: Bebo .. Mobile No.: 9650477626 | Task Start | Rajender Nagar Nursing Home | Paluck Technologies Ltd. - Ghaziabad | 42 | Tripping issue..DG runnning on Unbalanced load , educated customer about the same. | Closed | Kapil Solanki
1 | 211036104 | 2024-01-08 | 58.5 | T4.8941.../2420385 | DG not satarting | Task Start | Riddhi Green Power Solutions | Dicksons Engineering Co.Pvt.Ltd. - Latur | 0.37 | DG not Starting, Checked fuel line, fuel filter and NRV Valve all are found ok Checked engine wiring Harness and observed that 40 Amp fuse was missing and 2nd no injector Terminal connector lock was found Broken. Checked OBD connector and found that, ( OBD Connector 12 V supply wire (PIN No"A") wire interchage with Ground Wire (PIN No"B") Correct all wiring and start DG, DG Started no alram shown on Controller but Ikonnect not connected all work done but Need to replaced Control Paneel | Open | Jagdeep Saini
1 | 211041509 | 2024-02-08 13:56 | 500 | DV8.8501.C4../2320076 | ECU MOUNTING SPRING FAULT | Task Start | KGD Revamp Power Solutions | Prasad Power Engineers - Tumkur | 2.2 | Pending | Mr. Prakash S | Detail to be update | ECU mounting bracket spring found broken during commissioning.Photos attached
2 | 211047731 | 2024-05-08 14:08 | 320 | F6.8802.../2420090 | Starting Issue Email By-Service Dealer Name:-P.Santosh | Task Start | The Name of Nord Angilia Education Infrastructure Pvt. Ltd. | Laxmi Diesels - Visakhapatnam | 4.58 | SPN: 653, FMI :3 fault code shown on controller , enng. just refitted all the connection and issue resolved. | Mr Sanjaymon
3 | 211047277 | 2024-05-08 12:37 | 15 | GP3.8501.../2420142 | Starting Issue Call By Customer Name :- Sudhindra Rao Mobile No :- 9449025564 | Task Start | Ashwini Hospital. | Vijayshree Diesel Sales and Service - Hospet | 1 | Update pending | Mr. Prakash S
4 | 211047222 | 2024-05-08 12:25 | 25 | GP3.8702.../2420192 | Starting Problem Call by : Customer Name : Sreenivas Contact : 9177711555 | Task Start | Venkata Nagarjun Enterprises. | Prasad Power Engineers - Davangere | 6 | Customer run the DG without filling minimum fuel. | Mr. Prakash S | KRM check
1 | 211050310 | 2024-06-08 12:05 | 20 | GP3.1021.../2420195 | INSTANCE ID :- 100748732 SITE ID :- I-GJ-KSHD-ENB-G001 CALL BY CUSTOMER// DG ISSUE :- DG AUTOMATIN FAULTY NAME :-JEMIN NUMBER :-7016188790 | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Junagadh | 24h | Automation Issue. Checked and found the wires MR6,MR3,2N and 2H of relay bord was loose. | Closed | Amit Shandilya
2 | 211047526 | 2024-05-08 13:18 | 125.4 | 4H.8041.../2420207 | Starting Issue Email By Service Dealer Name:-SHILPA JAWALIKAR | Closed | Pragati Uddyog | Dhanashree Technocrats Pvt. Ltd. - Nasik |  | Amber alarm/ High coolant temp. in DM2 / adblue low level shown suggest to top up. | Closed | Jagdeep Saini
3 | 211037296 | 2024-01-08 15:41 | 20 | GP3.1021.../2420002 | DG issue | Open | Reliance Jio Infocomm Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Baramati |  | visit pending | Open | Jagdeep Saini
4 | 211037274 | 2024-01-08 15:40 | 20 | GP3.1021.../2420252 | dg Issue | Cancelled | Reliance Jio Infocomm Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune |  | no issue found, cancelled | Closed | Jagdeep Saini
5 | 211041911 | 2024-02-08 15:35 | 250 | F6.8841.../2420027 | Starting Issue Email By Service Dealer Name:-Mahalaxmi Diesels | Closed | TBK. India Private Limited | Mahalaxmi Diesels - Satara |  | low adblue top up and educate the customer | Closed | Jagdeep Saini
6 | 211052089 | 2024-06-08 20:55 | 125.4 | 4H.8041.../2420093 | Starting Issue Call by Customer Name - Vishal Tare Number - 9730711011 | Open | RHENUS CONTRACT LOGISTICS INDIA PVT LTD... | Transcreek Engineers Pvt. Ltd. - Bhiwandi |  | low adblue top up and educate the customer | Closed | Jagdeep Saini
7 | 211045168 | 2024-03-08 16:56 | 58.5 | T4.8941.../2420431 | Abnormal sound | Task Start | LP Logiscience LLP | Transcreek Engineers Pvt. Ltd. - Bhiwandi |  | Abnormal sound in main alternator, to be visit again with vendor person | Closed | Jagdeep Saini | Visit with vendor and confirm replcement of alternator after observing the sound.
8 | 211046033 | 2024-04-08 12:43 | 58.5 | T4.8941.../2420796 | Power Supply issue Call By Customer Name:- Mandar Thakur Number:- 7809696960 | Closed | A. R. Photoniccs | Transcreek Engineers Pvt. Ltd. - Navi Mumbai |  | Emergency stop,Educate the customer. | Closed | Jagdeep Saini
9 | 211046727 | 2024-05-08 10:23 | 250 | F6.8841.../2420120 | Water In Fuel Sensor | Task Start | Future Rock Technologies | Transcreek Engineers Pvt. Ltd. - Panvel | 2.5 | Water in fuel alarm shown the connection and supply fuond ok, presence of water is -ve observed loosen of sensor need to replace. | Open | Jagdeep Saini
10 | 211050005 | 2024-06-08 11:05 | 40 | 3H.8951.../2420158 | Automation Issue Call By Customer Name :- Amar Shah Mobile No :- 9699808393 | Task Start | Kanai Infra | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | 42 | Rpm continious varry 1499-1501 Engg. told that he did some setting in engine linkage, arrange the photographs for clearification. | Open | Jagdeep Saini
11 | 211046504 | 2024-05-08 07:43 | 400 | DV8.8542.C4../2320005 | Auto Stopping Issue Call By Customer Name :-Chetan . Mobile No :-9890004921 | Closed | TM. Automotive Seating Systems Private Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune |  | MR auto stop fuse burnt in panel, manual stop work properly | Closed | Jagdeep Saini
1 | 211050643 | 2024-06-08 13:23 | 20 | GP3.8604.../ 2420019 | INSTANCE ID-100740968 SITE ID- I-BR-SAUR-ENB-G001 CALL BY CUSTOMER \\ DG ISSUE-AUTOMATION ISSUE NAME-MOMHAD NUMBER-6204756283 | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | na | visitr pending | OPEN | Prabhakar Kumar
2 | 211050081 | 2024-06-08 11:26 | 20 | GP3.8604.../ 2420022 | INSTANCE ID:-100740957 SITE ID:-I-BR-JGDS-ENB-G002 CALL BY CUSTOMER \\ DG ISSUE:-UNDER BORD ALARM NAME:-Mrityunjay NUMBER:-7667904184 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | na | Visit Pending | OPEN | Prabhakar Kumar
3 | 211048899 | 2024-05-08 18:39 | 15 | GP3.8501.../ 2420005 | DG ISSUE | Task Start | BHARTI AIRTEL LIMITED | United Machinery Sales And Service - Asansol | 592 | after checking the connection it was found that the CAN high and CAN low wire at controller found loose, tighten the same issue resolved. | CLOSED | Prosanjit saha
4 | 211047842 | 2024-05-08 14:16 | 30 | 3H.8902.../ 2420098 | Starting Issue Email By Service Dealer Name:-Prem Roy | Closed | A. K. Stone Products Pvt. Ltd. | United Machinery Sales And Service - Md. Bazar Branch | 15 | Rain water entry inside canopy,GOEM person has visited and corrected the door alignment hence issue resolved. | CLOSED | Prabhakar Kumar
5 | 211046736 | 2024-05-08 10:26 | 30 | 3H.8902.../ 2320171 | Power Supply Issue Call By Customer Name:- Raju Kumar Mo No:-8709638762 | Open | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | na | Visit Pending | OPEN | Prabhakar Kumar
6 | 211044254 | 2024-03-08 12:44 | 25 | GP3.8702.../ 2420144 | High Voltage Issue Call By :- Customer Nmee :-Kanhaiya Kumar Number :- 6204991612 | Closed | Basant Bahar Sweets | Globalline India Services Private Limited - Biharsharif | 19.1 | guided the custopmer for balancing the load,and close the SR. | CLOSED | Prabhakar Kumar
7 | 211044202 | 2024-03-08 12:35 | 58.5 | T4.8941.../ 2420312 | Automation Issue Call By Customer Name :-Supriya Sinha Mobile No :-9434031039 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | 27 | after checking the connections found that the -ve missing from from battery at LVM hence connected the seperate -ve to the LVM and issue resolved. | CLOSED | Prosanjit saha
8 | 211036519 | 2024-01-08 12:40 | 20 | GP3.8604.../ 2420107 | INSTANCE ID :- 100741899 SITE ID :- I-BR-KJUL-ENB-G001 CALL BY CUSTOMER// DG ISSUE :- DG MAINS CONTACTOR HOLDING /SELF ALRAM FAULTY NAME :- RAAM NUMBER :- 6206296484 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | 59.4 | Mains Contactor burnt out. | OPEN | Prabhakar Kumar
1 | 211048631 | 2024-05-08 17:22 | 250 | F6.8841.../2320017 | Water Leakage Issue Email By - Customer Name - Satvik qc | Open | SATVIK TECHZONE PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon |  | Canopy leakage… Today Qualitiy and IEC team will visit the site. | Cancelled | Kapil Solanki
2 | 211048766 | 2024-05-08 17:54 | 82.5 | 5H.8901.../2320101 | Error Issue Call By: Customer Name :Sunil . No :9899859761 | Closed | Alliance Web Solution | Vidyut Engineers - Noida | 42 | SPN/FMI: 6595/0 ( Additional Dosing Chk err), checked dosing module found ok checked Pipe connections (SM TO DM) Found ok, clear the DTC issue resolved. | Closed | Kapil Solanki | Under observation
3 | 211049011 | 2024-05-08 20:14 | 125.4 | 4H.8041.../2420569 | Tripping Issue Call By Customer Name :-Shiva Kant Mobile No :-6393451258 | Task Start | Raj Ratan Company | Espiem Engines & Machines (P) Limited - KANPUR |  | Low DEF level, top up and educated customer issue resolved. | Closed | Sudhir Awasthi
1 | 211049671 | 2024-06-08 10:24 | 125.4 | 4H.8041.../2420138 | Starting Issue Email By - Service Dealer Name -Nimishesh Pandey | Task Start | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur | 454 | SPN/FMI: 516166/0, and low def top up and educated customer about the same. | Closed | Sudhir Awasthi
2 | 211049683 | 2024-06-08 10:16 | 125.4 | 4H.8041.../2420045 | VOC- loding issue trip issue highest RPM issue Customer Name Sukand Yadav Customer Number -9057201129 Mode- SR Generated through CDI calling. | Task Start | Shorya Auto Industries | Pratap Diesels Pvt. Ltd. - Alwar |  | Customer Side CNC machine was Tripped due to low power factor , Load side issue.. Initiated for Cancellation. | Cancelled | Gourav Sharma
3 | 211050205 | 2024-06-08 11:44 | 1000 | DV8.8502.C4../2420001. & 2420002. | Tripping issue Call by customer Name:-Anil shrma No:-9619226813 | Task Start | Tulip Infratech Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon |  | Tripping issue.. under voltage alarm was showing , Motarised MCCB was discharged, charged the same and also ECU Malfunctuning alarm was showing SPN/FMI; 523576/0 ( Intruption of Dosing group) checked and found Supply module pressure of Bank B was not Build up, found dosing module blocked (Bank B) , clean with hot water issue resolved. | Closed | Kapil Solanki | Update pending
4 | 211050211 | 2024-06-08 11:44 | 200 | 6H.8435.../2420020 | Automation Issue Call By Customer Name :-Mahendra Singh Mobile No :-9910567755 | Task Start | Shanti Prakash Associates. | Vidyut Engineers - New Delhi | 6 | Customer Side Panel issue (VMR Faulty ) No issue in DG. | Closed | Kapil Solanki
5 | 211050269 | 2024-06-08 12:01 | 62.5 | T4.8941.../2420261 | Voltage Issue Call By Customer Name :- Amandip . Mobile No :- 9878108868 | Task Start | Amson Transformers | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Voltage flickring issue.. Customer using 5hp Motor is ruuning on Load side, today Again engineer will visit the site and rectify the issue. | Open | Ved Gupta | Details pending
6 | 211050306 | 2024-06-08 12:05 | 125.4 | 4H.8041.../2420106 | Automation Issue Email By-Service Dealer Name:-Saurabh Rajput | Task Start | AVL36GURGAON Apartment Owners Association | Paluck Technologies Ltd. - Gurgaon | 8 | Customer Wants to DG oprate on Auto mode, Auto connection done. | Closed | Kapil Solanki
7 | 211050315 | 2024-06-08 12:07 | 160 | 6H.8475.../2420027 | Automation Issue Email By-Service Dealer Name:-Saurabh Rajput | Task Start | AVL36GURGAON Apartment Owners Association | Paluck Technologies Ltd. - Gurgaon | 80 | Customer Wants to DG oprate on Auto mode, Auto connection done. | Closed | Kapil Solanki
8 | 211050338 | 2024-06-08 12:14 | 82.5 | 5H.8901.../2320050 | Starting Issue Call By Customer Name:-Mahendra Tirpati No:-8736815975 | Task Start | NPP. Engineering | Paluck Technologies Ltd. - Ghaziabad | 237 | SPN/FMI: 157/13( pressure relief valve falut ), checked PRV count in Iknoonect toll found 50 correct the same and also DEF percentage was not showing ( KG 640 CE R00) ( Need to replaced) | Closed | Kapil Solanki
9 | 211050527 | 2024-06-08 12:55 | 20 | GP3.8601.../2420051 | High Fuel Consumption Issue Email By-Service Dealer Name:-Sandeep | Task Start | Shubham Hospital | Vishal Power Systems - PANIPAT |  | Visit Pending | Open | Kapil Solanki
10 | 211050751 | 2024-06-08 14:09 | 750 | DV2.8501.C4../2420043 | Starting Problem | Task Start | BVG. India Ltd. | Vidyut Engineers - Noida |  | SM TO DM pipe interchanged , correct the same and also Audio Buzzer relay Continuosly On, Checked and found wiring connection interchanged between emergency switch and buzzer , corrected the same issue resolved. | Closed | Kapil Solanki | GOEM issue
11 | 211050775 | 2024-06-08 14:20 | 58.5 | T4.8941.../2420671 | Starting issue Email By - OEM Name - Ashutosh Kumar Singh | Task Start | SR. Power Engineers | Vidyut Engineers - New Delhi | 4 | Emergency stop alarm was showing, found emergency switch was in pressed condition, release and educated customer about he same. | Closed | Kapil Solanki
1 | 211050492 | 2024-06-08 12:39 | 30 | 3H.8902.../2420234 | DG NOT STARTING | Task Start | Vamsi Eco Poultry Farm | Sri Manjunath Technical Services - Bhimavaram | LR | SPN:920 , charging alternator 40 Amp. fuse burn issue . they change the fuse , it is in under observation . | Closed | Mr. Saleem
2 | 211049000 | 2024-05-08 19:34 | 15 | GP3.8501.../2420404 | Starting Issue Call by KGD Name - Sanjay Number - 7022277052 | Task Start | Trapasol India Private Limited. | Vijayshree Diesel Sales and Service - Bellary | 1 | Emergency alarm. Released the emergency button issue resolved. | Closed | Mr. Prakash S
3 | 211048311 | 2024-05-08 16:15 | 320 | F6.8802.../2320001 | Fuel Guage Issue Call By Customer Name :-Sachin Kumar Mobile No :- 7338603759 | Task Start | Indian Institute of Science | Surya Power Services - J C Road, Bangalore | 20 | fuel level not shown in panel. Showing (++++) | Closed | Mr. Prakash S | change the GCU setting into % .
4 | 211046839 | 2024-05-08 10:54 | 500 | DV8.8501.C4../2420052 | Coolant Leakage Problem Call by : Customer Name : Kanan Contact : 9659173131 | Task Start | Vinayaka Missions Research Foundation | Bharath Diesel Sales and Service - Salem | 1 | Oil cooler puncture | open | Mr. Nanda Gopal | they replaced the oil cooler but still the oil & coolant mixture come out from the radiator , they wash radiator 4 times . and upcoming satuarday they going to do it again .
5 | 211046659 | 2024-05-08 09:38 | 40 | 3H.8951.../2420227 | EMERGENCY STOP PROBLEM | Task Start | Invictus Fitness LLP. | Bharath Diesel Sales and Service - Puducherry | LR | emergency button pressed , released the same , resolved . | Closed | Mr. Nanda Gopal
1 | 211058703 | 2024-07-08 15:45 | 125 | 4H.8041.../2420366 | Error Code Issue Â Call By Customer Name :-Mahendra Mobile No :-9016127747 | Closed | Arihant Machinery Store | Unique Techno Services Pvt Ltd. - Anand | 2 | SPN/FMI: 3031/14 , 1761/16,520528/31(Inducement) and flashed latest file issue resolved. | Closed | Amit Shandilya
2 | 211049749 | 2024-06-08 10:37 | 200 | 6H.9052.../2300003 | East zone | Completed | DINGANKAR CATERING SERVICES | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune |  | Water in fuel alarm shown, check distribution box find 8-9 loosen wire tighten the same, clear fault code and issue resolved. | Closed | Jagdeep Saini
1 | 211052096 | 2024-06-08 21:55 | 125.4 | 4H.8041.../2420419 | Amber lamp Issue and Charger Issue. Call by Customer Name - Shiv .. Number - 8585932580 | Task Start | OVN INDUSTRIES PVT LTD | OVN Industries Private Limited - New Delhi | 32 | Low DEF level, top up and educated customer about the same. | Closed | Kapil Solanki
2 | 211051480 | 2024-06-08 17:39 | 125.4 | 4H.8041.../2420068 | Tripping Issue & projector lamp issue Call By Customer Name:- Ashish Kumar No :- 7217755213 | Task Start | A. P. Associates | OVN Industries Private Limited - New Delhi | 45 | Battery charger mains connection missing from customer end. | Open | Kapil Solanki
3 | 211051414 | 2024-06-08 17:13 | 20 | GP3.8601.../2420428 | Electrical Issue Email By - Service Dealer Name -Javed Khan | Task Start | Anant Narain Haksar | Vidyut Engineers - New Delhi | 6 | Customer side panel contractor faulty(holding issue), suggested to customer to check panel. No issue in DG. | Closed | Kapil Solanki
4 | 211051292 | 2024-06-08 16:41 | 62.5 | T4.8941.../2420884 | KRM not Working Email By - OEM Name - Sushil Jaswal | Open | Hotel Green View. | Suraj Motor Store - Jammu |  | Vist Pending. | Open | Ved Gupta | Details pending
1 | 211057984 | 2024-07-08 13:57 | 125 | F6.9840.../2420006 | OIL LEAKAGE | Task Start | C. S. Export Noida Uttar Pradesh. | Vidyut Engineers - Noida |  | Line Rejection SR, Oil leakage issuee.. from flywheel end , dismentle the flywheel ( from ASM Aprrovel), today again engineer will visit site. | Open | Kapil Solanki
2 | 211057815 | 2024-07-08 13:14 | 62.5 | T4.8941.../2320056 | Tripping Issue Call By Customer Name :-Joganver Singh Mobile No :-9911146716 | Task Start | GAGAN GENERATORS | Vidyut Engineers - New Delhi | 366 | Emergency switch was in pressed condition, release the same issue resolved. | Closed | Kapil Solanki
3 | 211057688 | 2024-07-08 13:04 | 30 | 3H.8902.../2420428 | Tripping Issue Call By Customer Name - Sushanand Sir No : 9814700988 | Task Start | Mr. Sucha Nand. | SAAN Royal Power Solutions Private Limited - Zirakpur | 9 | Customer side mains Propblem, No issue in DG | Closed | Ved Gupta
4 | 211057167 | 2024-07-08 12:57 | 82.5 | 5H.8901.../2320101 | Error Code Issue Email By Service Dealer Name:-Shiv | Task Start | Alliance Web Solution | Vidyut Engineers - Noida | 43.15 | SR Open for 6595/0, Fault code, checked all dosing releted point but no abnormility found. | Closed | Kapil Solanki
5 | 211052648 | 2024-07-08 10:38 |  | GP3.8501.../2420587 | Coolant Leakage Issue | Task Start | Green Field Enterprises | Suraj Motor Store - kathua | 1 | Coolant leakage from water pump , O ring damage, it is in Kathua plant. | Open | Ved Gupta | Details pending
6 | 211052593 | 2024-07-08 10:34 | 125.4 | 4H.8041.../2320062 | Starting Issue Call by customer Name: Govind .. Mobile No. 7678504488 | Task Start | Shiv Industries | M/s OM Diesels Pvt. Ltd. - Sonipat | 272.5 | Customer complaint about Starting issue.. checked DG manual & load no abnormiliy found, and also Customer want to know, how to check Lube oil, educated the customer about the same. | Closed | Kapil Solanki
7 | 211052492 | 2024-07-08 10:06 | 125.4 | 4H.8041.../2320114 | Starting Issue Call By Customer Name :-Joganver Singh Mobile No :-9911146716 | Task Start | NEW GAGAN GENERATOR.. | Vidyut Engineers - New Delhi | 413 | Starting issue.. E- feed pump not Installed.CC- 17/05/2024 | Open | Kapil Solanki
8 | 211052434 | 2024-07-08 09:51 | 750 | DV2.8501.C4../2420021 | ECU Alarm call by customer name:Mukesh Pawar no:9996501023 | Task Start | Smartgen Electrical | Paluck Technologies Ltd. - Ghaziabad | 4 | SPN/FMI: 4386/2, 516166/0, 523576/0 releted to intrupption of dosing , checked and found pipe interchanged ( (DEF tank to Supply Module ) corrected the same but issue not resolved, then checked dosing module found chocked (Need to replaced) | Open | Kapil Solanki | GOEM issue
9 | 211052411 | 2024-07-08 09:39 | 320 | F6.8802.../2420016 | Canopy Door Issue call by customer name: Rahul Sing no :9810003918 | Closed | Aims Angel Infratech LLP. | Vidyut Engineers - Noida | 38 | Low DEF level and also Door Alignement issue.. Adjust and top up DEF issue resolved. | Closed | Kapil Solanki
10 | 211052314 | 2024-07-08 08:46 | 160 | 6H.8475.../2420020 | Heating issue call by customer Name- Manoj Kumar No-9582943302 | Task Start | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad | 493 | Coolant overflow from recovery bottle, coolant temp 74 degree C, checked thermostate found ok, but issue not resolved . | Open | Kapil Solanki | Update pending. Communication for part
1 | 211057685 | 2024-07-08 13:04 | 25 | GP3.8702.../2320006 | Diesel Filter Problem & Alarm Problem Call by : Customer Name :Deepa Mam Contact :9995548299 | Task Start | Ms. Deepa Nair | G-Care Diesels Private Limited - Ernakulam | 67.35 | Emergency stop alarm. Emergency alarm showing again and again. refitted all the connection. kept under observation. | Closed | Mr Sanjaymon
2 | 211054791 | 2024-07-08 11:49 | 82.5 | 5H.8901.../2420066 | Add Blue issue Call By Customer Name :- Daigasut Mobile No :- 8455055913 | Task Start | S. R. A. Contsructions. | Prasad Power Engineers - Tumkur | 20.16 | Low DEF level alarm. Refilled the DEF. Issue resolved. | Closed | Mr. Prakash S
3 | 211052629 | 2024-07-08 10:30 | 21HP | GP3.8501.../2420353 | TURBO CHARGER OIL SUPPLY HOSE DAMAGED | Task Start | Genlite Engineering Pvt. Ltd. | G-Care Diesels Private Limited - Ernakulam |  | Transit Damage. ( Turbo charger, intake manifold etc are found damaged). | Closed | Mr Sanjaymon
4 | 211050938 | 2024-06-08 15:02 | 625 | DV0.8501.C4../2320019 | water entry issue. | Task Start | HDFC Bank Limited | G-Care Diesels Private Limited - Ernakulam | 215.53 | Water entry case. Again SR raised by customer. | Closed | Mr Sanjaymon
3 | 211050081 | 2024-06-08 11:26 | 20 | GP3.8604.../ 2420022 | INSTANCE ID:-100740957 SITE ID:-I-BR-JGDS-ENB-G002 CALL BY CUSTOMER\\ DG ISSUE:-UNDER BORD ALARM NAME:-Mrityunjay NUMBER:-7667904184 | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | 176 | Under voltage alarm | CLOSED | Prabhakar Kumar
4 | 211046736 | 2024-05-08 10:26 | 30 | 3H.8902.../ 2320171 | Power Supply Issue Call By Customer Name:- Raju Kumar Mo No:-8709638762 | Open | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | NA | issue in customer side panel mains contactor found faulty. | CLOSED | Prabhakar Kumar
1 | 211062765 | 2024-08-08 16:31 | 20 | GP3.8604.../ 2420034 | Starting Issue | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Arrah | NA | Visit pending. | OPEN | Prabhakar Kumar
2 | 211062222 | 2024-08-08 15:47 | 20 | GP3.8604.../ 2420182 | CAPACITOR FAULTY | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Gaya | 0 | At the time of comissioning capacitor found faulty output voltage is 0V even after connecting input 48 V DC , Also found Under voltage alarm | OPEN | Prabhakar Kumar
3 | 211061939 | 2024-08-08 14:29 | 320 | F6.8802.../ 2420027 | Starting Issue Email By KGD Name :- Mayur Vira | Open | Bhartiya Reserve Bank Note Mudran Private Limited | DIVERSE TECHNO SERVICES PRIVATE LIMITED - MIDNAPUR | NA | Visit pending. | OPEN | Prosanjit saha
4 | 211058948 | 2024-07-08 16:35 | 82.5 | 5H.8901.../ 2320031 | Tripping Issue Email By OEM Name:-Shobha Gurung | Closed | Vinay Yadav. | Pratap Diesels Private Limited - Guwahati | 0 | Due to loose connection of -ve wire in controller ,controller getting off continuously, thats why dg is not starting tighten the connection issue resolved. | CLOSED | Subhrajit Roy | GEOM issue
1 | 211061701 | 2024-08-08 13:29 | 49 HP | T4.5201.../2300002 | DPF weight measurement Email By Koel Person Name:-Nandhakumar Venkatesan | Open | AJAX ENGINEERING PRIVATE LIMITED | Surya Power Services - Chikkaballapur | 613 | DPF weight measurement | closed | Mr. Prakash S
2 | 211061047 | 2024-08-08 11:19 | 160 | 6H.8475.../2420121 | Charging alternator issue | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | update pending at ASE end. | Closed | Mr. Nanda Gopal | charging alternator output voltage is not coming, then changed the another one charging alternator from stock engine(6H.8475/2420196),after that start and checked the engine checked the charging alternator output voltage, problem resolved .
1 | 211060157 | 2024-07-08 22:20 | 62.5 | T4.8941.../2420109 | Starting Issue Call By Customer Name :- Saroj No :- 7380439198 | Open | Sunita Gupta | SAAN Royal Power Solutions Private Limited - Zirakpur | 214 | Starting issue.. Found ECU connector was in loose codition, tighten the same issue resolved. | Closed | Ved Gupta
2 | 211059417 | 2024-07-08 18:43 | 40 | 3H.8951.../2420086 | Low Speed Alarm Call By Customer Name - Navtreet Singh Mobile No. -9988889053 | Task Start | Navpreet | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Maintenance due alarm,(service due) | Cancelled | Ved Gupta
3 | 211059238 | 2024-07-08 17:42 | 30 | 3H.8902.../2420546 | Starting Issue Call BY Customer Name :- Ayush No :- 9540017016 | Task Start | A. G. Contractor and Erectors | Paluck Technologies Ltd. - Faridabad | 9 | Starting issue.. Checked fuel line found ok, then found ECU Connector was in loose condition, tighten the same issue resolved. | Closed | Kapil Solanki
4 | 211059177 | 2024-07-08 17:27 | 160 | 6H.8475.../2420032 | Starting issue Call By Customer Name : -Amit kumar No:-8447323227 | Task Start | Airpack Compressor Teknologies Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 99.53 | As per VOC , Starting issue.. Engineer visited site and found DG running on load, Customer has not giving shutdown , to check DG set, then confirm wih customer what is the issue.. he said no issue.. in DG. | Closed | Kapil Solanki
5 | 211059094 | 2024-07-08 17:09 | 15 | GP3.8501.../2420042 | Battery issue Call by customer Name:- Ayushi .. No:- 7007479856 | Closed | Dr. Akshay Prasad | S. R Engines Sales And Service - Gorakhpur | 6 | SPN/FMI: 190/8 alarm accurs , then Checked Crank sensor and clean it then refitted the same issue resolved. | Closed | Sudhir Awasthi
6 | 211058951 | 2024-07-08 16:38 | 62.5 | T4.8941.../2320245 | Door Loack issue Call By Customer Name :-Somveer Mobile No :- 8607043191 | Task Start | R. P. Stone Clinic Pvt. Ltd. | Vishal Power Systems - PANIPAT | 183.8 | Canopy Door lock issue.. Adjust the lock issue resolved. | Closed | Kapil Solanki
7 | 211058784 | 2024-07-08 15:57 | 62.5 | T4.8941.../2420290 | Di seal High Consumption issue & Preventive Maintenance Call by customer Name:- Kapil ... No:- 9354859224 | Task Start | Green Energy Diesel Engines Private Limited. | M/s OM Diesels Pvt. Ltd. - Sonipat | 140.1 | Maintenance due alarm was showing, clear the DTC issue resolved. | Closed | Kapil Solanki
8 | 211061003 | 2024-08-08 11:14 | 15 | GP3.8501.../2420293 | Automation Issue Call By Customer Name :- Ram Nivas Malik Mobile No :- 9518893867 | Open | Dr. Sandeep Malik. | M/s OM Diesels Pvt. Ltd. - HISAR |  | Visit Pending. | Open | Kapil Solanki
9 | 211060852 | 2024-08-08 10:45 | 160 | 6H.8475.../2320032 | Red Lamp On Alarm Issue Call By Customer Name :-Jay Ram Mobile No :-8586025886 | Task Start | Nirupam Vatika Society | Vidyut Engineers - Noida | 63.27 | SPN/FMI: 1761/16, 97/2, 516166/0 , then top up DEF and clear the DTC then checked and found V- belt loose and Charging alternator maounting bolt broken, replace with new one , then start DG for load trail, found high blow by coming from breather suggested to engineer measure blow by . | Open | Kapil Solanki
10 | 211060796 | 2024-08-08 10:30 | 250 | F6.8841.../2320050 | Starting issue Call By Customer Name : Pradeep Yadav No:8368321282 | Task Start | H. P. Power Solution | Paluck Technologies Ltd. - Ghaziabad | 123 | Service done ( Sent Mail Communication to SD team ) | Closeed | Kapil Solanki
11 | 211060747 | 2024-08-08 10:16 | 57 | T4.8941.../2320120 | Automation Issue Call By Customer Name :-Alokh .. Mobile No :- 9873633154 | Task Start | Acidaes Solutions Pvt. Ltd. | Vidyut Engineers - Noida | 191 | Stoping issue.. Fail to Stop alarm was showing, and 100/3 (oil pressure flt ) in DM 2 found Oil pressure sensor Connector was in loose condition, connected properly issue resolved. | Closeed | Kapil Solanki
12 | 211060656 | 2024-08-08 09:50 | 160 | 6H.8475.../2320014 | Urea Leakage Issue Email by Service Dealer Name - SUNITA | Task Start | Swarup Steel Industries Ltd. | R K Engineers - Muzaffarnagar | 500 | DEF filter changed. | Closeed | Sudhir Awasthi
13 | 211060614 | 2024-08-08 09:26 | 125.4 | 4H.8041.../2420138 | Starting Issue Email By Service Dealer Name:-Nimishesh Pandey | Task Start | VD. Power Solution | S. R Engines Sales And Service - Gorakhpur |  | Starting issue..checked all basic parameter and checked ECU unswitched supply found ok, but issue.. still there, decided changed FIP . | Open | Sudhir Awasthi
14 | 211061723 | 2024-08-08 13:30 | 320 | F6.8802.../2420049 | Load Issue Call By Customer Name :-Binay Kumar Mobile No :-9555895552 | Task Start | Vasant Valley School | Vidyut Engineers - New Delhi | 259 | High oil consuption issue.. oil seepage from 1st cyliender , (Need to dismetle and check) but customer not giving shutdown. | Open | Kapil Solanki
15 | 211061660 | 2024-08-08 13:30 | 30 | 3H.8902.../2320126 | Lighting Issue & RPM Issue Call BY Customer Name :- Sazid No :- 9350483086 | Task Start | Sazid Spare Parts | Vidyut Engineers - New Delhi | 102.2 | Customer side light flickring issuee.. P.F - 0.3 (today again koel team will visit site) | Open | Kapil Solanki
1 | 211063606 | 2024-08-08 21:59 | 15 | GP3.8501.../2420586 | Trial | Open | HS. Enterprises | Suraj Moters Stores - Leh |  | SR open for only Cold Starting trail | Closed | Ved Gupta
2 | 211063597 | 2024-08-08 21:28 | 30 | 3H.8902.../2420177 | Error Code Issue Call By Customer Name :-S.K. Bajaj Mobile No :-8233604489 | Task Start | U. M. A. Bajaj | Pratap Diesels Pvt. Ltd. - Alwar | 579.2 | Service Done ( Sent mail Communication to SD team for claim Rejection) | Closed | Gourav Sharma
3 | 211062346 | 2024-08-08 16:18 | 750 | DV2.8501.C4../2420044 | Synchronization Issue Call By Customer Name :-Jaswant Singh Mobile No :-8979131986 | Closed | Rajhans Infratech Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Agra | 20 | SR open for only Synchronizaion purpose ( 750 &500 KVA) | Closed | Sudhir Awasthi
4 | 211062228 | 2024-08-08 15:52 | 160 | 6H.8475.../2420031 | Air Lock Issue Call By service Dealer Name : Ashish No : 9335012037 | Closed | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 397.2 | Air lock issue..Fuel filter loose,tighten the same issue resolved. | Closed | Kapil Solanki
5 | 211062113 | 2024-08-08 15:25 | 25 | GP3.8702.../2420077 | FUEL LEVEL SENSOR PROBLEM | Task Start | BAWA TOTAL SOLUTION | M/s OM Diesels Pvt. Ltd. - HISAR | 41 | Fuel sensor issue..Erratic reading showing on display only 60 % and same as manual meter but actual fuel was 100 % in tank, then removed sensor found float crack , (Need to replaced) | Open | Kapil Solanki
6 | 211061635 | 2024-08-08 13:06 | 15 | GP3.8501.../2420392 | Automation Issue Call By Customer Name :-Mangal Sing Mobile No :-9779103868 | Open | Dr. Manjitpal Singh. | Megatron Engineers - Pathankot |  | Automation isssue.. Customer select manual mode , guided customer on call. | Cancelled | Ved Gupta
7 | 211061622 | 2024-08-08 13:02 | 57 | T4.8941.../2420605 | Door Lock Issue Email By - KGD Name - Devendra Kumar Saxena | Task Start | Kedar Hospitaltity. | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 16.1 | Door lock issue..applied oil for the same issue resolved. | Closed | Sudhir Awasth
8 | 211061735 | 2024-08-08 13:43 | 30 | 3H.8902.../2320009 | Low Oil Pressure Alarm Issue Call By Customer Name :-Sidhant Mahajan Mobile No :-9897017000 | Task Start | ZX. Sporting Pvt. Ltd. | R K Engineers - Meerut | 55 | DG running on overload, now balance the load. issue resolved. | Closed | Sudhir Awasthi
1 | 211063673 | 2024-09-08 05:33 | 25 | GP3.8702.../2420098 | Trial | Task Start | SURAJ MOTOR STORE | Suraj Moters Stores - Leh |  | SR open for only Cold Starting trail | Closed | Ved Gupta
2 | 211063882 | 2024-09-08 05:13 | 10 | GP3.8301.../2420159 | L3 Trial | Task Start | HS. Enterprises | Suraj Moters Stores - Leh |  | SR open for only Cold Starting trail | Closed | Ved Gupta
3 | 211063883 | 2024-09-08 05:19 | 20 | GP3.8601.../2420550 | Trial | Task Start | SURAJ MOTOR STORE | Suraj Moters Stores - Leh |  | SR open for only Cold Starting trail | Closed | Ved Gupta
4 | 211063918 | 2024-09-08 08:02 | 125.4 | 4H.8041.../2420236 | Fuel Sensor not working & Tripping issue Call By Customer Name: Ranjit Kumar Number: 9560164522 | Closed | Arya Hospital | OVN Industries Private Limited - New Delhi | 9 | Fuel sensor issue.. Low fuel level alarm was showing but actual 100 % fuel on tank and as wel as manual meter , then checked resistance found ok, then removed the sensor and clean then refitted the same issue resolved. | Closed | Kapil Solanki
5 | 211064004 | 2024-09-08 09:45 | 500 | DV8.8501.C4../2320089 | Starting Issue & ECU Alarm Issue Email by Service Dealer Name - Akanksha | Closed | THEMIS MEDICARE LTD. | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 105 | Low DEF level in both bank, top up DEF and clear the DTC issue resolved. | Closed | Sudhir Awasthi
6 | 211064137 | 2024-09-08 10:20 | 40 | 3H.8951.../2420421 | Starting Issue Email By - Service Dealer Name -Nimishesh Pandey | Task Start | RPM Academy | S. R Engines Sales And Service - Gorakhpur | 3 | Customer complaint starting issue..But engineer did not found any issue.. DG running ok on load. | Closed | Sudhir Awasthi | KRM check
7 | 211064281 | 2024-09-08 10:55 | 20 | GP3.8601.../2420231 | Starting Issue Call By Â OEM Name :-Gurmeel Mobile No :-9041030276 | Closed | M/s. Kuber Rice Mills | Gen Powers - PATIALA | 7 | Under speed alarm was showing, checked fuel line found ok, reset the alarm issue resolved. | Closed | Kapil Solanki | KRM check
8 | 211064368 | 2024-09-08 11:08 | 82.5 | 5H.8901.../2320009 | Urea level not showing Email By Service Dealer Name:-Shiv | Closed | ARSH LADIES SUIT PRIVATE LIMITED | Vidyut Engineers - Noida | 90.2 | DEF percentage was not showing ( KG 640C E ) reprogramme the same and also 516166/0 alarm was activated, clear the DTC issue resoleved. | Closed | Kapil Solanki
9 | 211064416 | 2024-09-08 11:19 | 20 | GP3.8601.../2420063 | Alternator Issue Email by OEM Name - Rahul Siwach | Task Start | Posh Fragrances Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 37.11 | light flickering issuee. Due to customer side UPS connected, then disconnected ups and found no flickring . | Closed | Kapil Solanki
10 | 211064522 | 2024-09-08 11:39 | 30 | 3H.8902.../2420215 | Tripping issue Call By Customer Name:- Divya Mo No:-9582914040 | Closed | Gee Kay Services | Vidyut Engineers - New Delhi | 6.25 | Customer complaint about tripping issue.. Engineer visited site but no issue found DG ruuning ok. | Closed | Kapil Solanki | KRM check
11 | 211064585 | 2024-09-08 11:51 | 30 | 3H.8902.../2320103 | Disply issue Call By Customer Name :- Vikas Mobile No :-Â 9871111419 | Closed | Nav Durga Enterprises | Paluck Technologies Ltd. - Faridabad | 101 | Display did not turn on, found +ve, -ve connector loose at controller end, tighten he same issue resolved. | Closed | Kapil Solanki | update pending
12 | 211064672 | 2024-09-08 12:06 | 40 | 3H.8951.../2420075 | Error Code Issue Call By Customer Name:-Mukesh No:-9896075884 | Task Start | Nandini Bawaseer Hospital | M/s OM Diesels Pvt. Ltd. - Rohtak | 2 | Customer complaint about error code issue.. But engineer did not found any issue..DG running ok. | Closed | Kapil Solanki | KRM check
13 | 211064698 | 2024-09-08 12:20 | 320 | F6.8802.../2420022 | Display and Starting Issue Call By Customer Name:Upendra Gupta Mobile:9813664371 | Task Start | Karan Power System | Vishal Power Systems - Karnal | 94 | Starting issuee…battery discharged (22V),checked mains voltage (230 V) and charger output voltage 0V , then changed battery charger issue resolved. | Closed | Kapil Solanki | Failed part
14 | 211064722 | 2024-09-08 12:20 | 125.4 | 4H.8041.../2420265 | Diesel % not showing Call By Customer Name :-Lalit Tyagi Mobile No :- 9810138700 | Task Start | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad | 18 | Fuel sensor issue..Erratic reading showing on display..comparing with tank checked sensor found direction changed, correct and refitted the same issue resolved. | Closed | Kapil Solanki
15 | 211064728 | 2024-09-08 12:20 | 57 | T4.8941.../2320181 | Indicator Lamp issue Call By Customer Name :- Vimal Poddar Mobile No :- 9899800330 | Closed | Vimal Poddar | Vidyut Engineers - Noida | 551.2 | KRM related issue..Educated customer for the same. No issue in DG | Closed | Kapil Solanki
16 | 211064745 | 2024-09-08 12:29 | 58.5 | T4.8941.../2420761 | Tripping Issue Call By Customer Name :-Parmod Mittal Mobile No :-9356484007 | Open | Brhamrishi Mission Sr Secondary School | Industrial Power Solutions - LUDHIANA |  | Unbalanced load, on DG , inciated for Cancellaion. | Cancelled | Ved Gupta
17 | 211064806 | 2024-09-08 12:41 |  | 3H.8902.../2420438 | STARTING ISSUE | Task Start | Electro Equipments | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar |  | ECU faulty in Goem Plant , EDO placed . | Closed | Sudhir Awasthi | GEOM issue
18 | 211064969 | 2024-09-08 13:23 | 500 | DV8.8501.C4../2420007 | ECU Amber issue Call By Customer Name :- Kaushlesh Singh Mobile No :-Â 9599081124 | Closed | Divy Power Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 24 | Low DEF level,@ 37 %, top up and clear the DTC issue resolved. | Closed | Kapil Solanki
19 | 211065044 | 2024-09-08 13:54 | 500 | DV8.8501.C4../2420017 | Voltage Issue Email By Service Dealer Name:-Shiv | Task Start | PG Electroplast Limited | Vidyut Engineers - Noida | 44.15 | High load variation, due to hunting issue.. Then perform load trail with load analyzer, customer side servo motor triped, (no tripping in DG) | Closed | Kapil Solanki
20 | 211065823 | 2024-09-08 15:19 | 82.5 | 5H.8901.../2320042 | Error Code Issue Email by Service Dealer Name - SUNITA | Closed | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar | 124 | SPN/FMI: 6595/0 ( Nox system monitoring ) 4375/19(Urea pump motor speed deviation error),clear the DTC issue resolved. No any abnormility found. | Closed | Sudhir Awasthi | details requried
21 | 211065891 | 2024-09-08 15:45 | 125.4 | 4H.8041.../2320134 | Error Code Issue Email By Service Dealer Name:-SUNITA | Closed | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar | 600 | SPN/FMI: 1761/16, 516166/0 , top up DEF and clear the DTC issue resolved. | Closed | Sudhir Awasthi
22 | 211065981 | 2024-09-08 16:00 | 82.5 | 5H.8901.../2420009 | Red Lamp Alarm Issue Call By Customer Name: Praveen Number: 9811226395 | Task Start | ANAND PRAYAG UDYOG | Paluck Technologies Ltd. - Faridabad | 68 | Tripping issue.. With showing Under speed alarm found Customer applied jerk load on DG, educated customer for step loading. | Closed | Kapil Solanki
23 | 211066637 | 2024-09-08 17:50 | 250 | DV8.9863.../2320022 | Automation Issue Email By - Customer Name - Rohin Lohat | Task Start | PROCALL SERVICES | Vidyut Engineers - New Delhi | 47.5 | Customer complaint about Automation issue.. Engineer checked DG on manual and auto mode DG running ok, but customer said in morning DG was not started in First crank. todaay engineer will visit site again and checked DG in morning. | Open | Kapil Solanki | update req.
24 | 211066784 | 2024-09-08 18:39 | 25 | GP3.8702.../2420016 | ENGINE NOT STARTING | Task Start | Classic Construction Company | BSES (I) Pvt. Ltd. - Udaipur |  | Line Rejection SR, During Commissioning Starting issue..due to low fuel level (13 % ) and SPN/FMI: 97/5 in DM 2 , and found battery terminal loose , tighten the same issue resolved. | Closed | Gourav Sharma
1 | 211067388 | 2024-10-08 07:21 | 320 | F6.8802.../2320022 | Loading and Tripping and Voltage Issue Call By Customer Name :-Arpit Sukla Mobile No :-7217763009 | Closed | Vending Updates India P. Ltd. | Vidyut Engineers - Noida | 182.59 | Customer complain about load issue and tripping issue , Engineer did not found load related issue , found radiator was choke , suggest to customer clean the radiator. | Closed | Kapil Solanki | KRM check | Check KRM data but does not show any type of issue.
2 | 211067402 | 2024-10-08 08:57 | 62.5 | T4.8941.../2320024 | Stopping Issue Call By Customer Name :-Prince Mittal Mobile No :-8059800411 | Task Start | Wisdom World School | Vishal Power Systems - Kurukshetra | 153 | Automation issue , customer side mains fuse was blown (customer side panel issue ) , correct the same issue resolved. | Closed | Kapil Solanki
3 | 211067427 | 2024-10-08 09:17 | 250 | DV8.9863.../2300002 | Voltage issue Call By Customer Name : -Manish Kumar No:-8800788532 | Task Start | Devyani Jaipuria | Vidyut Engineers - New Delhi |  | CPCB IV | Closed | Kapil Solanki
4 | 211067572 | 2024-10-08 10:04 | 82.5 | 5H.8901.../2320034 | KRM Issue Email By - Service Dealer Name -Priyanshu Singhal | Closed | RX Infotech Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 316 | KRM faulty, PCB change , PCB was sent by KRM team. | Closed | Kapil Solanki
6 | 211067630 | 2024-10-08 10:24 | 15 | GP3.8501.../2420437 | Starting Issue Email by Service Dealer Name - Vijay Singh | Closed | Colonel Jayant Vij | SAAN Royal Power Solutions Private Limited - Zirakpur | 4 | Starting issue due to battery positive terminal was loose , tighten the same issue resolved. | Closed | Ved Gupta
7 | 211067640 | 2024-10-08 10:29 | 125.4 | 4H.8041.../2420019 | Tripping Issue Call By Customer Name :- Aman .B Badhan Mobile No :-9954477358 | Task Start | Rahee Infratech Ltd. | Vidyut Engineers - New Delhi | 1712 | DG was tripping with showing under voltage alarm , found DG was produced only 45 found , checked AVR found AVR fuse was blown , replace the same issue resolved. | Closed | Kapil Solanki
8 | 211067666 | 2024-10-08 10:29 | 40 | 3H.8951.../2420043 | Automation issue Call by customer Name:- Manu .. No:- 8284814444 | Task Start | Impact Coaching & Educational Services | SAAN Royal Power Solutions Private Limited - Zirakpur | 295 | Automation issue due to customer mains supply connection was loose in auto panel , correct the same issue resolved. | Closed | Ved Gupta
9 | 211068163 | 2024-10-08 12:07 | 160 | 6H.8475.../2420105 | Self Starter not working | Task Start | Jassons Sales | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Self starter was not working , EDO the same , GOEM scope | Open | Gourav Sharma
10 | 211068445 | 2024-10-08 13:06 | 125.4 | 4H.8041.../2420206 | Add Blue Alarm Call By Customer Name :-Shiv . Mobile No :-9990863639 | Task Start | United Power Solution. | OVN Industries Private Limited - New Delhi | 9 | DEF level was low top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
11 | 211068449 | 2024-10-08 13:06 | 125.4 | 4H.8041.../2420189 | Loading Issue Call By Customer Name :-Sham Mobile No :-9509232205 | Task Start | M/s. Star Light Moulding Product Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Customer need to synchronization. | Cancelled | Gourav Sharma
12 | 211068525 | 2024-10-08 13:30 | 320 | F6.8802.../2320057 | Oil leakage issue Call By Customer Name : -Jogindar No:-9873867764 | Task Start | Medsource Ozone Biomedicals Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 161 | Oil leakage from fan belt side , HP pump casing , tighten the HP pump casing bolt , and keep under observation 7 bay | Open | Kapil Solanki
13 | 211068996 | 2024-10-08 13:36 | 125.4 | 4H.8041.../2320086 | VOC- hunting issue and sound issue Customer Name Om Prakash Customer Number -9718594293 Mode- SR Generated through CDI calling. | Open | Total Construction | Paluck Technologies Ltd. - Gurgaon |  | SR will be cancel , unbalance load. | Cancelled | Kapil Solanki
West Zone
1 | 211069904 | 2024-10-08 17:51 | 0 | GP3.8702.../2420123 | STARTING ISSUE | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Surat | Na | Many fault codes were showing in the controller.After ecu flashing problem was solved. | Open | Amit Shandilya
2 | 211069893 | 2024-10-08 17:48 | 400 | DV8.8542.C4../2420065 | THORTTLE VALVE ISSUE | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Surat | Na | Throttle valve position is showing 46 % instead of 0 % on load (Bank 2) | Closed | Amit Shandilya
3 | 211069035 | 2024-10-08 13:58 | 0 | F6.8841.../2420249 | RADIATOR FAN ISSUE | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Surat | Na | Radiator fan hub bolt broke due to loosening | Open | Amit Shandilya
4 | 211063306 | 2024-08-08 17:46 | 20 | GP3.1021.../2420119 | Air Locking And Mains Contractor Faulty | Open | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Ahmedabad | NA | SR given for cancellation | Open | Amit Shandilya
1 | 211070586 | 2024-11-08 14:07 | 125.4 | 4H.8041.../ 2420312 | Load Issue Abnormal Sound Issue Call By Customer Name :- Rmakant Mobile No :- 7463931985 | Open | Jai Mata Di Infrapromoters Private Limited. | Globalline India Services Private Limited - Arrah | na | visit pending | OPEN | Prabhakar Kumar
2 | 211068291 | 2024-10-08 12:37 | 82.5 | 5H.8901.../ 2420166 | Starting problem | Task Start | powerline Industries | Hibreed Engineering Pvt. Ltd. - Nagaon | 0 | found starter negative wire loose,due to which DG not starting tighten the same issue resolved. | OPEN | Subhrajit Roy
3 | 211067826 | 2024-10-08 10:51 | 15 | GP3.8501.../ 2420311 | Oil leakage | Task Start | North East Powerline Industries | Pratap Diesels Private Limited - Guwahati | 0 | oil leakage from flywheel oilseal ,change the oil seal problem resolved | OPEN | Subhrajit Roy
1 | 211065898 | 2024-09-08 15:46 | 901 hp | DV2.8501.C4../2420060 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | Engine cranks but it was not started, Checked the Electrical feed pump that was not working, then checked its harness and relay module then found ECU command was not coming then flash the ECU then problem got resloved . | Closed | Mr. Nanda Gopal
2 | 211065845 | 2024-09-08 15:32 | 20 | GP3.1021.../2420035 | INSTANCE ID:-100744218 SITE ID:-I-KL-MPPM-ENB-9106 CALL BY CUSTOMER\\ DG ISSUE:-STARTING PROBLEM NAME:-AJIT NUMBER:-7722070524 | Closed | Reliance Jio Infocomm Limited | G-Care Diesels Private Limited - Malappuram | 28 | 1.3 litre difference shown on controller with respect to actual amount of fuel , flash the ECU but same problem is there . | Closed | Mr Sanjaymon
3 | 211064285 | 2024-09-08 10:56 | 20 | GP3.8601.../2420108 | Starting Issue Email By Service Dealer Name:-Genearth Services, BM | Closed | Unique Collection. | Genearth Services - Marthandam | 14 | Battery Low error - due to Battery Charger not being connected (Battery Charger and AMF Both are not in our scope outside purchase) | Closed | ---
4 | 211064215 | 2024-09-08 10:40 | 25 | GP3.8702.../2420412 | OIL SENDOR PROBLEM | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | 0.53 | pressure is not building up , so they replaced the sensor . | Closed | Mr. Nanda Gopal
5 | 211063605 | 2024-08-08 21:59 | 30 | 3H.8902.../2320113 | Power Supply Issue Call By Â Service Dealer Name :-Wasim Mobile No :-7899015698 | Closed | Mr. Lokesh N. | Vijayshree Diesel Sales and Service - Hospet | 2 | DG MCB TRIP | Closed | ---
6 | 211063238 | 2024-08-08 17:37 | 0 | 3H.8951.../2420401 | ENGINE NOT STARTING | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | pending at ASE end | Closed | Mr. Nanda Gopal | engine is not starting without error code, also found ECU is not communicate to ikonnect tool,checked the starting circuit, and removed the air lock found ok.checked the cables, wires found ok.checked the ECU pins and connectors found ok.then changed the another one ECU from stock engine found ok. found control panel assembly is problem.then changed the another one control panel, start and checked the engine, found ok.
7 | 211062372 | 2024-08-08 16:21 | 40 | 3H.8951.../2420067 | Canopy door problem Call by : Dealer Name : Ravi Contact : 9154225965 | Closed | Glow & Style Unisex Salon and Makeup | Sri Manjunath Technical Services - Guntur | 1.37 | door lock stuck apply the oil check the door locks condition is ok | Closed | Mr. Saleem
8 | 211062287 | 2024-08-08 16:02 | 25 | GP3.8702.../2420361 | Engine Not starting | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | pending at ASE end | Closed | Mr. Nanda Gopal | engine is not starting due to error code 100/4, checked the cables and wires found ok.due to emergency for customer side,then changed the oil pressure sensor from stock engine (GP3.8702/2420341).after that start and checked the engine, checked the charging alternator, checked the smoke, no abnormal noise, no leakages found . problem resolved .
9 | 211068275 | 2024-10-08 12:36 | 500 | DV8.8501.C4../2420015 | ECM failure Issue Email By Service dealer Name :-surya.dsc-indiranagar | Task Start | SHOBA LIMITED | Surya Power Services - Bangalore | 244.37 | SR raise for claim purpose . | Closed | ---
10 | 211067952 | 2024-10-08 11:22 | 40 | 3H.8951.../2420114 | BATTERY DICHARGE Email By Service Dealer Name:-Laxmi Diesels, BM | Task Start | Dr. Reddys Foundation | Laxmi Diesels - Srikakulam | 22 | pending at ASE end | open | Mr Sanjaymon | charging alternator failure , no output voltage found . there no charging alternator in stock .
11 | 211067573 | 2024-10-08 10:04 | 0 | GP3.8301.../2420218 | ABNORMAL NOISE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | LR | today engg. visit the site . | Closed | Mr. Nanda Gopal | QA team is following up on updates that need to get from Mr. Kalishwar.
1 | 211069267 | 2024-10-08 15:14 | 125.4 | 4H.8041.../2420224 | Starting Issue Email by KGD Name - Neeraj Saini | Task Start | Ajanta Electric Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi | 26.4 | Battery was discharged , battery charger not connected to mains supply during commissioning , connected the same issue resolved. | Cancelled | Kapil Solanki
2 | 211069543 | 2024-10-08 16:23 | 62.5 | 6H.9860.../2320007 | Maintenance Due Alarm Issue Call By Customer Name :-Ankit Mobile No :-8800976918 | Closed | Aeolus Engineering And Technologies Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 212 | Maintenance due alarm was showing, clear the alarm. | Closed | Kapil Solanki
3 | 211069774 | 2024-10-08 17:23 | 40 | 3H.8951.../2420270 | Power supply Call By Customer Name :-Satendra . Mobile No :-9990085351 | Closed | Har Shree Nath Service Station | OVN Industries Private Limited - New Delhi | 11.4 | Battery was discharge , battery charger mains supply was off from customer side , correct the same issue resolved. | Closed | Kapil Solanki
4 | 211069910 | 2024-10-08 17:54 | 250 | DV8.9863.../2420006 | Over Heating Issue Email By GOEM Name :-rakesh koul | Open | Nippon Paints India Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 6 | A bank turbo side turn red hot , checked air line found ok. | Closed | Kapil Solanki
5 | 211069917 | 2024-10-08 18:00 | 15 | GP3.8501.../2420018 | Voltage Fluctuation Issue Call By OEM Name :-Rajesh Surendar Varma Mobile No :-9996788584 | Task Start | Keshav S/o. Rajender Kumar | M/s OM Diesels Pvt. Ltd. - Sirsa | 25 | Customer side mains voltage fluctuations , educated the customer about the same issue resolved. Also coolant level was low top up the coolant. | Closed | Kapil Solanki
6 | 211070029 | 2024-10-08 19:31 | 30 | 3H.8902.../2420066 | STARTING PROBLEM AND LOW SPEED ERARE Email By KGD Name:-Sanjeev Jain | Task Start | B. S. E. Cranes | SAAN Royal Power Solutions Private Limited - Zirakpur | 37 | Starting issue with showing fuel level was low ,top up the same and educated the customer about the same issue resolved. | Closed | Ved Gupta
7 | 211070509 | 2024-11-08 11:17 | 58.5 | T4.8941.../2420810 | Starting Issue Call By Customer Name :-Vijay Kumar Mobile No :-7011507427 | Task Start | aggarwal sabha trust. | OVN Industries Private Limited - New Delhi | 3.2 | starting issue with SPN/FMI - 157/14 ,2804/2 , tighten the distribution box connection , issue resolved. | Closed | Kapil Solanki | GEOM issue
8 | 211070588 | 2024-11-08 14:13 | 40 | 3H.8951.../2420285 | KRM Issue Call By Customer Name :-Balvindra Kumar Mobile No:-8053458790 | Task Start | Asger Agro Pvt. Ltd. | Vidyut Engineers - New Delhi | 11.35 | KRM live data was not showing , checked the KRM connection found ok . Need to checked , no issue in DG. | Open | Kapil Solanki | KRM check | Check KRM light because data does not show in dashboard logine.
9 | 211070631 | 2024-11-08 16:46 | 250 | F6.8841.../2420069 | Starting Issue Call by Customer Name - Agarwal .. Number - 9056588870 | Task Start | Innova Captab Limited. | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Rain Water Entry in Canopy, SR open on GOEM portal. | Open | Ved Gupta
10 | 211070650 | 2024-11-08 17:54 | 20 | GP3.8601.../2420025 | Over voltage Email By Customer Name:-Rajesh Kumar Sangal | Closed | Aviral Sangal Huf. | Vidyut Engineers - Noida | 28.57 | Customer Side Panel issue.. VMR faulty No issue in DG. | Closed | Kapil Solanki
11 | 211070653 | 2024-11-08 18:05 | 1000 | DV8.8502.C4../2420001 & 2420002 | Fuel Sensor Issue Call by Customer Name - Amandeep ... Number - 6283342341 | Open | SRG. Developers & Promoters | SAAN Royal Power Solutions Private Limited - Zirakpur |  | fuel level was showing incorrect, showing 110 % actual was 75 % percentage on display..checked Fuel setting on controller found ok, as per HO and Zonel RRT caleberated File to resolved this issue.. | Open | Ved Gupta
1 | 211071684 | 2024-12-08 11:10 | 750 | DV2.8501.C4../2320048 | Tripping issue Call By Customer Name : -Akash No:-8273237145 | Task Start | Jai Mata DI. Generator Service | Vidyut Engineers - Noida | 31.28 | Low DEF level, Bank A @ 37%, top up clear the DTC issue resolved. | Closed | Kapil Solanki
2 | 211071678 | 2024-12-08 11:10 | 160 | 6H.8475.../2420032 | Alram issue Call By Customer Name : -Rakesh kumar No:-9310296441 | Task Start | Airpack Compressor Teknologies Pvt Ltd | Paluck Technologies Ltd. - Faridabad | 103.5 | Low DEF level, top up and clear the DTC issue resolved. | Closed | Kapil Solanki
3 | 211071584 | 2024-12-08 10:47 | 57 | T4.8941.../2320042 | Errol code Call By Customer Name :-Ashwini Chavan Mobile No :-7027099266 | Task Start | Sceptre Medical India Pvt Ltd | M/s OM Diesels Pvt. Ltd. - Sonipat | 169.1 | SPN/FMI: 97/2(Water in Fuel ), checked Fuel filter and cean it then refitted the same and also Unbalanced load on DG , educated customer for balanced load. | Closed | Kapil Solanki
4 | 211071152 | 2024-12-08 09:27 | 125.4 | 4H.8041.../2420156 | Starting Issue Call By Customer Name :-Kaushal Kishore Mobile No :-9717408124 | Closed | MOHANS COMPREHENSIVE HEALTH SOLUTIONS PRIVATE LIMITED | Vidyut Engineers - Noida | 74.42 | Battery was discharged, checked battery charger found output (14 V) but not get to battery (need to check wiring) | Open | Kapil Solanki
5 | 211072066 | 2024-12-08 12:34 | 320 | F6.8802.../2320037 | Trip_Genset_Low_Voltage | Open | KPC FLEXI TUBES PVT LTD | Paluck Technologies Ltd. - Faridabad |  | KRM Generated SR, SD team confirm with Customer , as per customer voice no issue in DG Initiated for Cancellation. | Cancelled | Kapil Solanki | KRM CHECK | Check KRM data and found it the GENSET low voltage .
6 | 211071877 | 2024-12-08 11:55 | 200 | 6H.8435.../2320015 | Load Issue And Black Issue Call By Customer Name:-Shahnawaz . No:-9927161998 | Task Start | TCI Supply Chain Solutions - A division of Transport Corporation of India Limited | Paluck Technologies Ltd. - Ghaziabad | 191 | Tripping issue.. When Applied Load , checked and found Fuel mix with Oil , found HP line crack, (Need to replaced) | Open | Kapil Solanki
1 | 211070586 | 2024-11-08 14:07 | 125.4 | 4H.8041.../ 2420312 | Load Issue Abnormal Sound Issue Call By Customer Name :- Rmakant Mobile No :- 7463931985 | Open | Jai Mata Di Infrapromoters Private Limited. | Globalline India Services Private Limited - Arrah | 21 | customer complains Abnormal sound during DG start, engineer visit the site check the engine no such problem found. | CLOSED | Prabhakar Kumar
2 | 211074015 | 2024-12-08 18:07 | 20 | GP3.8604.../ 2420055 | Mains contractor faulty | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | NA | visit pending | OPEN | Prabhakar Kumar
3 | 211073749 | 2024-12-08 17:18 | 30 | 3H.8902.../ 2320171 | contractor issues call by customer name :mukesh no :8340795164 | Task Start | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | NA | Visit pending | OPEN | Prabhakar Kumar
4 | 211072182 | 2024-12-08 12:46 | 125.4 | 4H.8041.../ 2420278 | Tripping Issue Call By Customer Name:- Lalu No :- 9433156597 | Closed | M/s. Hotel Beach Bengal | Gangpur Sales and Services - Puri | 4 | ECU and ITV related Fault code was showing ,after doing a flash and clear DTC issue resolved. | CLOSED | Ujjwal Das
1 | 211072508 | 2024-12-08 14:18 | 500 | DV8.8501.C4../2420027 | Starting problem | Task Start | Swastik Electrotech Private Limited | Transcreek Engineers Pvt. Ltd. - Mumbai | Na | Coolant sensor fault & oil pr. Sensor fault shown in controller, try to connect the tool but override command not taken by controller, instruct to flash the controller. | CLOSED | Jagdeep Saini | Flash the controller with cpcb iv file
2 | 211070682 | 2024-11-08 19:27 | 20 | GP3.8601.../2420309 | Underspeed Alarm Issue Call by Customer Name - Sandesh Kumbhar Number - 9892078960 | Closed | Prajakta Dnyaneshwar Mali. | Transcreek Engineers Pvt. Ltd. - Panvel |  | emergency stop Showing, teporarily bypass the emg. Switch. | CLOSED | Jagdeep Saini
3 | 211073999 | 2024-12-08 18:09 | 400KVA | DV8.8542.C4../2420064 | DCU FAULTY | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Surat | NA | Changed the DCU. | CLOSED | Jagdeep Saini
4 | 211073359 | 2024-12-08 16:02 | 25 | GP3.8702.../2420180 | Oil Leakage and Coolant Leakage Issue Call By Customer Name :- Pradip Kumar Shelar Mobile No :- 8983196943 | Task Start | Malpani Retails Private Limited. | Dicksons Engineering Co.Pvt.Ltd. - Ahmednagar | 11 | Visit Today | CLOSED | Jagdeep Saini | found o-ring cut of oil filter, replace the filter, issue resolved.
1 | 211072042 | 2024-12-08 12:26 | 40 | 3H.8951.../2420210 | AMF panel problem Call by : Customer Name : Mahantesh Contact :8971115519 | Task Start | Neovision Lasik Centre. | Vijayshree Diesel Sales and Service - Bellary | 1 | update pending . | Closed | -- | main alternator burnt issue sent to service centre.
2 | 211071844 | 2024-12-08 11:47 | 250 | F6.8841.../2320025 | Starting Problem Call by : Customer Name : rajadra Contact : 9703591628 | Task Start | Goravigere Education Society (INDIA) | Surya Power Services - Bangalore | 356 | Water entry issue | Closed | --
3 | 211071758 | 2024-12-08 11:23 | 15 | GP3.8501.../2420053 | Diesel pump problem & Display problem & Automatically switching off Call by : Customer Name : Mahesh Contact :9578274149 | Completed | S. R. A. Agencies | Bharath Diesel Sales and Service - Pudukottai | 102 | sweep stuck issue | Closed | Mr. Nanda Gopal
4 | 211071706 | 2024-12-08 11:11 | 160 | 6H.8475.../2420041 | Starting Issue Call By Service Dealer Name:- Kanimori No:-9894798582 | Task Start | Novitium Labs Pvt. Ltd. | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 2 | Pending at ASE end | Closed | Mr. Nanda Gopal | battery fitting work carried out , engine not start due to weak battery .so recharged the battery and start the engine with load found ok.
5 | 211070082 | 2024-10-08 21:40 | 160 | 6H.8475.../2420106 | DIFFICULTY IN CREATING SR REQUEST. pLEASE COMMISSION THE DG SET | Open | Durga Industries | Powerlinks Infra Tech Pvt Ltd - Secunderabad | - | Today engg. visit the site . | Closed | Mr. Saleem | KGD just put DG on site , they are not doing any connections .
1 | 211075841 | 13-08-2024 14:13 | 160 | 6H.8475.../2420068 | V BELT SOUND Issue Email By - Service Dealer Name - Dharmendrasinh Zala | Task Start | Hotel Surabhi | Unique Techno Services Pvt Ltd. - Gandhidham | 26.35 | The fan belt was loose and was making abnormal sounds. | CLOSED | Amit Shandilya | Under observation
2 | 211075144 | 13-08-2024 11:08 | 20 | GP3.1021.../2420177 | INSTANCE ID- 100748389 SITE ID-I-GJ-JPVG-ENB-G002 CALL BY CUSTOMER\\ DG ISSUE:-DG PROBLEM NAME-CHIRAG BHATT NUMBER-8160629620 | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Rajkot | 26.1 | The relay of the mains contactor has burnt out. | open | Amit Shandilya
3 | 211075873 | 13-08-2024 14:16 | 320 | F6.8802.../2320019 | Water in Fuel Issue Email by Service Dealer Name - Santosh Kharat | Task Start | Knest Manufacturers Private Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Talegaon Dabhade, Pune | 154 | water in fuel alarm check fuel tank found water in tank drain the fuel+water clean tank and fill with fuel | CLOSED | Jagdeep Saini
4 | 211075282 | 13-08-2024 11:40 | 125.4 | 4H.8041.../2420258 | Starting issue Call By Customer Name : - Shekar gri Number :-8329000294 No:-8329000294 | Closed | Thermotech Engieenring & Services Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chinchwad-Pune | 11 | Battery charger mains connection not available, connect the same and educate the customer. Issue resolved | CLOSED | Jagdeep Saini
1 | 211071800 | 2024-12-08 11:36 | 58.5 | T4.8941.../2420761 | Automation Issue Email By Service Dealer Name:-KAJAL | Task Start | Brhamrishi Mission Sr Secondary School | Industrial Power Solutions - LUDHIANA |  | Unbalanced load on DG, educated customer about the same. | Cancelled | Ved Gupta
2 | 211071804 | 2024-12-08 11:36 | 30 | 3H.8902.../2320002 | Starting issue Call By Customer Name :- Mukesh Mobile No :- 8586926583 | Task Start | RAJESHWARI CHEMICALS | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Starting issue due to battery was discharge . Customer side battery charger faulty ,connect the KOEL Battery charger connection , issue resolved. | Closed | Kapil Solanki
3 | 211071810 | 2024-12-08 11:38 | 30 | 3H.8902.../2420164 | Starting Issue Email By KGD Name:-Sanjeev Jain | Closed | Dogra Builders | Industrial Power Solutions - LUDHIANA | 14.3 | Starting issue with showing under speed alarm , checked fuel line found ok , checked air line found ok , reset the alarm issue resolved . | Closed | Ved Gupta
4 | 211071845 | 2024-12-08 11:47 | 62.5 | 6H.9860.../2320040 | Tripping Issue Call BY Customer Name :- Shukla No :- 8076249715 | Closed | JK. Lakshmi Cement Ltd. | Vidyut Engineers - New Delhi | 92 | Hunting issue on load , checked gas line found ok , and checked air line found , DG ventilation problem , fitted exhaust fan , and checked on load found ok , no hutting found . | Closed | Kapil Solanki
5 | 211072251 | 2024-12-08 13:02 | 250 | F6.8841.../2420135 | Oil Leakage Issue Call By Customer Name :- Vikas Laphagpal Mobile No :- 7703944343 | Task Start | Garg Builders and Promoters LLP | SAAN Royal Power Solutions Private Limited - Zirakpur | 16.54 | oil leakage from oil filter tighten the same issue resolved. | Closed | Ved Gupta
6 | 211072381 | 2024-12-08 13:37 | 125 | F6.9860.../2320084 | Red Lamb Ala ram issue Call By:- Customer Name:- Shravan Kumar No:- 8384077487 | Task Start | ADITYA POWER GROUP | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 122 | Starting issue , SPN/FMI - 102/0 , clear the same issue resolved. | Closed | Kapil Solanki
7 | 211072424 | 2024-12-08 13:45 | 750 | DV2.8501.C4../2420016 | Tripping issue Call By Customer Name : -Akash No:-8273237145 | Task Close | Jai Mata DI. Generator Service | Vidyut Engineers - Noida | 28.25 | Multiple fault code on controller , related to communication error , Found A bank DEF percentage was not showing ,then clear the DTC and checked interface box connection found ok, issue resolved. | Closed | Kapil Solanki
8 | 211072425 | 2024-12-08 13:46 | 125.4 | 4H.8041.../2420030 | Protect Lamp on alarm and At blew level low Call by Customer Name: Nitin .. Number: 8740919191 | Closed | Kamal Wire | Pratap Diesels Pvt. Ltd. - Bhiwadi | 36 | starting issue , found DEF level was low @0% , top up the DEF and educated the customer about the same issue resolved. | Closed | Gourav Sharma
9 | 211072478 | 2024-12-08 14:02 | 125 | F6.9860.../2320033 | Starting Issue Email By - Service Dealer Name - SUNITA | Task Start | M/S KHANNA SPORTS INDUSTRIES PRIVATE LIMITED | R K Engineers - Meerut |  | CPCB II | Open | Sudhir Awasthi
10 | 211072517 | 2024-12-08 14:23 | 125.4 | 4H.8041.../2320108 | Amber Lamp error Call By Customer Name :- Vijay Kumar Mobile No :-9829973147 | Task Start | SSSP. Speciality Packagings Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 111 | SPN/FMI - 1761/16,516166/0(DM2) ,other brand DEF use by customer. Educated the same issue resolved. | Closed | Gourav Sharma
11 | 211072518 | 2024-12-08 14:23 | 125 | F6.9860.../2320082 | Red Lamp Alarm issue Call By Customer Name :-Falak Mobile No :-9910748875 | Closed | National coaters | Pratap Diesels Pvt. Ltd. - Bhiwadi | 90 | Customer complain about red lamp on , engineer did not found any issue checked on load found ok . | Closed | Gourav Sharma
12 | 211072609 | 2024-12-08 14:58 | 500 | DV8.8501.C4../2420017 | VOC- voltage fluctuation issue Customer Name Ajay Chudhari Number -9555954016 Mode- SR Generated through CDI calling. | Task Start | PG Electroplast Limited | Vidyut Engineers - Noida | 44.16 | Customer complain about voltage fluctuation issue , customer did not allow check the DG | Closed | Kapil Solanki
13 | 211072692 | 2024-12-08 15:13 | 62.5 | 6H.9860.../2320032 | Red Lamp Alarm Issue Call By Customer Name:Bal Krishna Mobile:9813446718 | Task Start | FOUR STAR REALTY PVT LTD | Vidyut Engineers - Noida | 91.3 | CPCB II | Open | Kapil Solanki
14 | 211072695 | 2024-12-08 15:13 | 500 | DV8.8501.C4../2320081 | Coolant Leakage Issue Call BY Customer Name :- Rahul No :- 8227001150 | Task Start | Ozone Overseas Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi | 79.44 | Coolant leakage from coolant hose, change the coolant hose and clean Radiator with K clean issue resolved. | Closed | Kapil Solanki
15 | 211073277 | 2024-12-08 15:53 | 15 | GP3.8501.../2420006 | DG automation not working | Task Start | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 3 | DG was not start in 1 crank , checked fuel line found ok. Keep under observation. | Closed | Kapil Solanki
16 | 211073288 | 2024-12-08 15:47 | 57 | T4.8941.../2420068 | Display issue & Automation timing issue Call By Customer Name : -Avinash No:-9992734206 | Open | Mutlivac Laraon India Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Joint visit plan with customer side panel supplier. | Cancelled | Gourav Sharma
17 | 211073290 | 2024-12-08 15:47 | 125.4 | 4H.8041.../2320133 | Starting Issue and Loading Issue Call by Customer Name: Aakash. Number: 9044754131 | Closed | Jai Balaji Industries..... | Espiem Engines & Machines (P) Limited - Aligarh | 442 | DG was tripping with showing Under speed alarm, found Jerk load on DG ,educated customer for applied load gradually. | Closed | Sudhir Awasthi
18 | 211073322 | 2024-12-08 15:55 | 40 | 3H.8951.../2420025 | DG automation not working | Task Start | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Air locking issuee.. | Closed | Kapil Solanki
19 | 211073698 | 2024-12-08 17:08 | 125.4 | 4H.8041.../2420241 | startin isssu | Task Start | MALABAR GOLD PRIVATE LIMITED | OVN Industries Private Limited - New Delhi |  | Line Rejection SR, Air lock issue.. Found fuel filter loose, tighten the same issue resolved. | Closed | Kapil Solanki | update required
20 | 211073735 | 2024-12-08 17:12 | 125 | F6.9860.../2320039 | Engine oil leakage Email By - Customer Name - Umang Goel | Task Start | ASEPACK [P] LTD | Paluck Technologies Ltd. - Ghaziabad | 129 | PNG CPCB II | Open | Kapil Solanki
21 | 211074063 | 2024-12-08 18:19 | 125.4 | 4H.8041.../2420419 | Amber lamp Alarm Issue Call By Customer Name :- Aayush .. Mobile No :- 7903029346 | Task Start | OVN INDUSTRIES PVT LTD | OVN Industries Private Limited - New Delhi |  | SPN/FMI: 516166/0, clear DTC and also reduce cooling time from 5 min to 2 min (as per customer demand) | Closed | Kapil Solanki
22 | 211074150 | 2024-12-08 18:49 | 250 | F6.8841.../2320024 | Starting issue Call by KGD Name:-Gurpreet Kaur No:-9311523743 | Task Start | BESTONE | OVN Industries Private Limited - New Delhi | 2.38 | Starting issue.. Air lock in fuel line , removed air issue resolved. | Closed | Kapil Solanki
23 | 211074191 | 2024-12-08 19:20 | 125 | F6.9860.../2320068 | Maintenance Due Alarm Call By Customer Name : Sunil Kumar Mobile No : 9871808947 | Open | Phoenix Contact India Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 363 | CPCB II PNG , Maintenance due alarm was showing , clear the DTC and change setting . | Closed | Kapil Solanki
24 | 211074269 | 2024-12-08 20:14 | 125.4 | 4H.8041.../2420010 | Tripping Issue Call By Customer Name :- Durgesh Shukla Mobile No :-7678256535 | Task Start | Gopa Chanda | Vidyut Engineers - New Delhi | 13 | Canopy Emergency switch was in pressed condition, release the same issue resolved. | Closed | Kapil Solanki
25 | 211074286 | 2024-12-08 21:39 | 58.5 | T4.8941.../2420739 | Automation Issue Call By Customer Name :-Pawan Mobile No :-9990058661 | Open | PA POWER PROJECT ENGINEERING | Vidyut Engineers - Noida |  | AMF Panel (supplied by jakson team ), fuse & relay card faulty, replaced the same issue resolved. | Closed | Kapil Solanki
1 | 211075536 | 13-08-2024 12:38 | 40 | 3H.8951.../2320004 | Starting Issue, Stopping Issue, High Voltage Issue Call By Customer Name :- CK.. Mobile No :-9910412117 | Closed | Waves Enterprises. | Vidyut Engineers - Noida | 108.39 | Customer complaint about stating issue.. But engineer checked DG on manuual and auto found ok. No issue in DG. | Closed | Kapil Solanki
2 | 211075410 | 13-08-2024 12:09 | 57 | T4.8941.../2320165 | Panel Burnt Issue Email By - Service Dealer Name - Amitabh Kushwaha | Task Start | Frank Metal Recyclers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 111.1 | As previously discussed, panel burnt, new panel installed issue resolved. Now DG running ok. | Closed | Kapil Solanki
3 | 211075267 | 13-08-2024 11:39 | 15 | GP3.8501.../2420183 | Error Code issue Email By - OEM Name - Shiv | Closed | CIPL. Corporate Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 89.32 | Maintenance due alarm was showing,reset alarm. | Closed | Kapil Solanki
4 | 211075178 | 13-08-2024 11:20 | 750 | DV2.8501.C4../2420007 | Fail to stop Issue Email By - Koel Person Name - Nitin Shekhar Singh | Task Start | VIBRACOUSTIC INDIA PRIVATE LIMITED | SAAN Royal Power Solutions Private Limited - Zirakpur | 127 | DG shutdown whenever command is given, and showing Fail to Stop alarm,then disabled prior to starting oil pressure saftey . Now DG running ok . | Closed | Ved Gupta
5 | 211075150 | 13-08-2024 11:12 | 125.4 | 4H.8041.../2320002 | Alternator Burnt. Issue Email By Service Dealer Name:-Amitabh Kushwaha | Task Start | Accord Automation Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad |  | SR open for Alternator Installation. | Closed | Kapil Solanki
6 | 211074902 | 13-08-2024 10:05 | 500 | DV8.8501.C4../2320058 | Coolant Leakage Issue Call By Customer Name:-Rajveer No:-9354145442 | Task Start | ARORA POLYFAB INDIA PRIVATE LIMITED. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 253 | Coolant Leakage from coolant pipe, (Need to changed) | Open | Kapil Solanki
7 | 211074821 | 13-08-2024 09:42 | 20 | GP3.8601.../2420289 | Tripping Issue Call By Customer Name:-Arjun Kapoor No:-9811063070 | Closed | SR. Power Engineers | Vidyut Engineers - Noida | 41.44 | Customer side panel sensing issue..No issue in DG. | Closed | Kapil Solanki
8 | 211074797 | 13-08-2024 09:30 | 125.4 | 4H.8041.../2420044 | Automation Issue Email by Service Dealer Name - Vikas Saini | Task Start | Bharatiya Janata Party | M/s OM Diesels Pvt. Ltd. - Rohtak | 70 | Customer want to remote starting , connectione done. | Closed | Kapil Solanki
9 | 211074763 | 13-08-2024 09:01 | 58.5 | T4.8941.../2420928 | Under Speed Alarm Call By Customer Name:-Yogender Nagar No:-9711006032 | Closed | Sanskar Public School | Vidyut Engineers - Noida | 10.25 | DG was tripping with showing Under speed alarm found Unbalanced load on DG and also jerk load, educated customer about the same. | Closed | Kapil Solanki
1 | 211076535 | 13-08-2024 16:30 | 125.4 | 4H.8041.../ 2420557 | Starting Issue Email by KGD Name - Kartick | Open | Heto Yeptho. | M/s Hindustan Powerkraft - Dimapur | NA | visit pending | OPEN | Subhrajit Roy
2 | 211075438 | 13-08-2024 12:17 | 15 | GP3.8501.../ 2420187 | Shut Down Alarm Issue Call By Customer Name :-Himanshu Kumar Mobile No :-6205060476 | Closed | Apna Dream Saakaar Developers. | Globalline India Services Private Limited - Patna | 2.24 | Red lamp alarm Emergency switch is activated, release the PB issue resolved. | CLOSED | Prabhakar Kumar
3 | 211074015 | 2024-12-08 18:07 | 20 | GP3.8604.../ 2420055 | Mains contractor faulty | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | NA | visit pending | OPEN | Prabhakar Kumar
4 | 211073749 | 2024-12-08 17:18 | 30 | 3H.8902.../ 2320171 | contractor issues call by customer name :mukesh no :8340795164 | Task Start | Government Engineering College Nawada Bihar | Globalline India Services Private Limited - Biharsharif | 58 | Contact with kirloskar team and decided to change the AMF pannel mains contactor in warranty. | OPEN | Prabhakar Kumar
1 | 211075493 | 13-08-2024 12:33 | 20 | GP3.8601.../2420270 | Fuel leakage-fuel leakage problem | Task Start | S. S. Logistics. | Bharath Diesel Sales and Service - Puducherry | 0.5 | pending at ASE end | Closed | Mr. Nanda Gopal | fuel filter found loose in condition . tightend the same .
2 | 211074922 | 13-08-2024 10:08 | 20 | GP3.8601.../2420314 | Starting Issue Call By service dealer Name :-Sandesh Mobile No :-7022277053 | Task Start | V. Thirumalesh. | Vijayshree Diesel Sales and Service - Bellary | 3 | pending at ASE end | Closed | -- | emergency fault code shown on controller , loose connection found , tightend the same .
3 | 211074755 | 13-08-2024 09:35 | 125.4 | 4H.8041.../2420322 | starting problem | Task Start | Rathnakala Jewellery | Electro Controls - Thiruvananthapuram | 2 | pending at ASE end | Closed | Mr. Saleem | there is continous supply received to starter motor from the relay board so replaced the relay .
4 | 211073856 | 2024-12-08 17:36 | 250 | F6.8841.../2420083 | Diesel Leakage Issue Email By Service Dealer Name:-P.RADHIKA | Closed | Urban Sanctuary LLP. | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 24.15 | no fuel/oil leakage found . | Closed | Mr. Saleem
5 | 211073282 | 2024-12-08 15:47 | 125.4 | 4H.8041.../2320060 | Votage And Tripping Issue Call By Customer Name:Ranjan Kumar Mobile No:7735655402 | Closed | FUREIN CONSTRUCTION ENGINEERING PRIVATE LIMITED | Ultimate Power Source - Krishnagiri | 51 | Adblue level low recommend the adblue top up clear the Eaorr code s | Closed | Mr. Saleem
1 | 211066304 | 2024-09-08 17:26 | 0 | GP3.8702.../2420447 | Diesel level not shown accurate in controller | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | check the fuel level sensor conn. And resistance value found ok, flash the controller , issue remain same, replace the controller , issue resolved | Close | Jagdeep Saini
2 | 211061774 | 2024-08-08 13:44 | 40 | 3H.8951.../2420414 | Oil leakage from turbo pipe | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | turbo oil drain pipe leakage, replace the same issue resolved. | Close | Jagdeep Saini
3 | 211061771 | 2024-08-08 13:42 | 25 | GP3.8702.../2420472 | Oil Pressure | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | sernsor found faulty, fitted another sensor, dg run ok | Close | Jagdeep Saini
4 | 211076652 | 13-08-2024 17:01 | 160 | 6H.8475.../2420129 | injector no 6 open circuit fault alarm shown | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | spn-656/5 found open circuit injector 6 conn. | Close | Jagdeep Saini
5 | 211076579 | 13-08-2024 16:45 | 160 | 6H.8475.../2420135 | Old revision engine wiring harness received post cut off - Feed pump connection provision missing | Task Start | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | feed pump connection missing in wiring harness replace with new revision, issue resolved | Close | Jagdeep Saini
6 | 211070032 | 2024-10-08 19:33 | 250 | F6.8841.../2420093 | Starting issue and Preventive Maintenance Call By Customer Name :-Shiva Kumar Mobile No :-7729940323 | Open | Dongyang Engineering & Construction Indial Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Lonavala | na | sr open for service send for cancellation | Close | Jagdeep Saini
7 | 211064649 | 2024-09-08 12:06 | 750 | DV2.8501.C4../2320018 | Starting Issue Email By - GOEM Name - Ashvini sonpitre | Closed | Taco EV. Component Solutions Private Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 23 | Interuption of dosing Check all the connections interchange T4 and T6. | Close | Jagdeep Saini | Dosing module failure part
8 | 211081943 | 15-08-2024 12:43 | 82.5 | 5H.8901.../2420020 | Tripping Issue Call By Customer Name: Jay Kumar Number: 7888099685 | Open | Baba International | Transcreek Engineers Pvt. Ltd. - Ambernath | na | Visit pending | open | Jagdeep Saini
9 | 211059311 | 2024-07-08 18:02 | 20 | GP3.1021.../2420130 | Manual to Auto Pending | Closed | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Vadagam | 23 | Genset not starting issue.The problem was solved by removing and reinstalling the 19RB6 relay coil (Starting Relay Coil ). | Closed | Amit Shandilya
10 | 211075691 | 13-08-2024 13:30 | 20 | GP3.8601.../2420485 | OIL LEAKAGE FROM LLOP | Task Start | Goel Power Engineers | Unique Techno Services Pvt Ltd. - Surat | Na | Coolant leakage from coolant gallery due to loose of core plug. | Closed | Amit Shandilya
1 | 211078496 | 14-08-2024 11:18 | 125.4 | 4H.8041.../ 2320003 | Starting Issue Call By Customer Name : Laksh Deka No:-7002690283 | Open | N.K. CONSTRUCTION & SUPPLIERS | Pratap Diesels Private Limited - Guwahati | 36.2 | earlier charging alternator was change as it was not giving output, after new chaging alternator battery voltage was dropping continuously change the battery issue resolved. kept under observation. | OPEN | Subhrajit Roy | Details required
2 | 211076535 | 13-08-2024 16:30 | 125.4 | 4H.8041.../ 2420557 | Starting Issue Email by KGD Name - Kartick | Task Start | Heto Yeptho. | M/s Hindustan Powerkraft - Dimapur | NA | Visit pending | OPEN | Subhrajit Roy
3 | 211074015 | 2024-12-08 18:07 | 20 | GP3.8604.../ 2420055 | Mains contractor faulty | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Biharsharif | 39 | the contactor will change into KOEL AMC. | CLOSED | Prabhakar Kumar
4 | 211072182 | 2024-12-08 12:46 | 125.4 | 4H.8041.../ 2420278 | Tripping Issue Call By Customer Name:- Lalu No :- 9433156597 | Closed | M/s. Hotel Beach Bengal | Gangpur Sales and Services - Puri | 4 | This issue has repeated for the third time in which ECU and ITV related Fault code was showing , engineer found ITV was not freely opening and closing after changed the ITV and clear DTC issue resolved. | CLOSED | Ujjwal Das | Failed part
5 | 211079099 | 14-08-2024 13:39 | 58.5 | T4.8941.../2420312 | Automation Issue Call By Customer Name:- Supriya Sinha Mo No:-9434644598 | Open | Kabita Maternity and Nurshing Home. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - BERHAMPORE | 32 | SR open due to GOEM pannel issue. | OPEN | Prosanjit saha
1 | 211077042 | 13-08-2024 18:14 | 125.4 | 4H.8041.../2420625 | Under Speed Alarm Issue Email By - Service Dealer Name -Saurabh Rajput | Task Start | Rao Scaffolding. | Paluck Technologies Ltd. - Gurgaon |  | Visit pending | Open | Kapil Solanki
2 | 211076996 | 13-08-2024 18:07 | 125.4 | 4H.8041.../2420121 | Door Lock Problem Email by Service Dealer Name - Saurabh Rajput | Task Start | D. V. M. Public School | Paluck Technologies Ltd. - Gurgaon | 85 | Door lock issue..adjust the lock issue resolved. | Closed | Kapil Solanki
3 | 211076641 | 13-08-2024 16:55 | 250 | F6.8841.../2420135 | Oil leakage Issue Message by customer Name : Abhishek . No : 9729254725 | Open | Garg Builders and Promoters LLP | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Wrong SR open by customer, SR will be cancel | Cancelled | Ved Gupta
4 | 211076575 | 13-08-2024 16:43 | 20 | GP3.8601.../2420022 | Auto Stopping Issue Email By KGD Name:-Sanjeev Jain | Open | Jagmohan Singh | Industrial Power Solutions - LUDHIANA | 66 | Auto Stopping issue..Mains fuse faulty, replaced the same issue resolved. | Closed | Ved Gupta
5 | 211076447 | 13-08-2024 16:16 | 15 | GP3.8501.../2420042 | Starting Issue Call By Customer Name :-Honey Srivastava Mobile No :-9838038880 | Task Start | Dr. Akshay Prasad | S. R Engines Sales And Service - Gorakhpur | 8.3 | Tripping issue..SPN/FMI: 244/8, found lop connector was in loose condition, tighten the same issue resolved. | Closed | Sudhir Awasthi
6 | 211076125 | 13-08-2024 15:18 | 750 | DV2.8501.C4../2420018 | Diesel Leakage Issue Call By Customer Name :-Nikhil Mobile No :-8368899197 | Task Start | Void Fire Consultants | OVN Industries Private Limited - New Delhi | 23.5 | Customer Complaint Fuel leakage issue.. But engineer did not found any type of leakage, Tank was Overfilled and low DEF level @ 49 % , educated customer for the same. | Closed | Kapil Solanki
7 | 211076096 | 13-08-2024 15:16 | 125.4 | 4H.8041.../2320004 | AMF Panel Issue Call By Customer Name:Indersen Yadavji Mobile No.8826817371 | Closed | ARIHANT INDUSTRIAL EQUIPMENT | Vidyut Engineers - New Delhi | 162 | Customer side panel issue(KOEL panel ) selector switch select on DG . So DG does not stop in auto mode, Educated the customer about the same issue resolved. | Closed | Kapil Solanki
8 | 211075875 | 13-08-2024 14:18 | 200 | 6H.8435.../2320024 | Abnormal Sound Issue Call By Customer Name:-Param Dhan No:-9661089533 | Closed | AEW PROTECH PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 188 | Abnormal sound from loose V belt, tighten the same issue resolved. | Closed | Kapil Solanki | Belt need to verify
9 | 211075716 | 13-08-2024 13:34 | 20 | GP3.8601.../2420043 | Automation issue Call By Customer Name : Amandeep Singh No : 9878717180 | Task Start | Gagandeep Singh Hayer | Megatron Engineers - Pathankot | 15 | Automation issue.. Customer side changeover issue.. No issue in DG. | Closed | Ved Gupta
10 | 211075602 | 13-08-2024 13:04 | 750 | DV2.8501.C4../2320007 | Thermal shield fixing and wiring harness to be changed Email by Service Dealer Name - Raman | Closed | Merino Industries Ltd. | Paluck Technologies Ltd. - Ghaziabad | 165 | Sometimes Tripping issue.LLOP sensor issue.. Then Replace the Wiring harness to ECU and covered exhaust manifold with thermal Insulation jacket | Closed | Kapil Solanki
11 | 211075590 | 13-08-2024 12:58 | 30 | 3H.8902.../2320009 | Voltage and Tripping Issue Call By Customer Name :-Sohan Mobile No :-7906155033 | Closed | ZX. Sporting Pvt. Ltd. | R K Engineers - Meerut | 57 | Unbalanced load on DG , educated the Customer about the same. | Closed | Sudhir Awasthi
12 | 211075538 | 13-08-2024 12:38 | 30 | 3H.8902.../2420158 | Coolant leakage Issue Call By Customer Name :- Ajay Kumar No :- 9810898097 | Closed | Mr. A. K. Nigam | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 28 | Coolant leakage from coolant galeries allen key bolt , tighten the same issue resolved . | Closed | Kapil Solanki
13 | 211075439 | 13-08-2024 12:17 | 62.5 | T4.8941.../2320097 | Hunting Issue Call By Customer Name:-Surendra .. No:-7988586645 | Task Start | Bhajana Home Dacor Private Limited | Vishal Power Systems - PANIPAT | 252.2 | Hunting issue found . Water separator filter was loose tighten the same issue resolved . Also radiator was choke and top up coolant (0.5L) | Closed | Kapil Solanki
14 | 211075139 | 13-08-2024 11:07 | 125 | F6.9860.../2320031 | Abnormal Sound Issue Call By Customer Name :-Deepak . Mobile No :-9991906821 | Closed | Phoenix Contact India Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 285 | CPCB II | Closed | Kapil Solanki
15 | 211074900 | 13-08-2024 10:05 | 125.4 | 4H.8041.../2420050 | on call done with dealer Red Lamp Alarm issue Call By Customer Name :-Raghuvi Kumar Mobile No :- 8076404542 | Closed | International Automotive Components | Paluck Technologies Ltd. - Faridabad | 563 | SPN/FMI - 6875/0,4095/1 , checked DEF backflow line found ok , Clear the DTC issue resolved | Closed | Kapil Solanki | Under observation
16 | 211074801 | 13-08-2024 09:30 |  | GP3.8702.../2420408 | Rpm Fluctuation and black Smoke issue at 85% load | Task Start | Western Consolidated Private Ltd. | Deep Jyoti Electricals and Services - Haldwani | 2.3 | Line Rejection SR, in 15 KW , rpm Fluctuation and black smoke, then found CAC turbo hose pipe clamp was in loose condition, tighten the same issue resolved. | Closed | Sudhir Awasthi
1 | 211079981 | 14-08-2024 15:35 | 82.5 | 5H.8901.../2320084 | Add Mobil Call by Customer Name:Sahil Rana Number: 7300651325 | Task Start | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi | 1680 | Emergency switch was in pressed condition, relase the same then DG ruuning and found 516166/0 and 633/3 related to rail metering unit, checked fuel line found ok,Suggested to engineer checked water seprator water in fuel sensor O Ring ( Revisit Required) | Open | Kapil Solanki
2 | 211079315 | 14-08-2024 14:34 | 25 | GP3.8702.../2420110 | Starting Issue Call By Â Customer Name :-Vivek Kumar Agrawal Mobile No :-9971719027 | Task Start | The Wash Club | M/s OM Diesels Pvt. Ltd. - Sonipat | 17 | Starting issue.. Low Fuel level, before reaching engineer Customer top up the fuel . | Closed | Kapil Solanki
3 | 211079001 | 14-08-2024 13:16 | 82.5 | 5H.8901.../2420054 | Starting Issue Call By Customer Name:-Pravin No:-9728886777 | Open | Colour Tex Industries Pvt. Ltd. | Vishal Power Systems - PANIPAT |  | Visit Pending. | Open | Kapil Solanki
4 | 211078714 | 14-08-2024 12:08 | 40 | 3H.8951.../2320058 | Sound Issue Call By Customer Name :- Surendra No :- 9871932703 | Closed | STRIKER INDUSTRIES PVT LTD | OVN Industries Private Limited - New Delhi | 76.16 | Abnormal sound from Silencer side , but DG was in running condition that’s why engineer not checked proper, but as per engineer observation, alignement ok, and also overload on DG educated customer about the same. | Open | Kapil Solanki | Details required
5 | 211078079 | 14-08-2024 10:52 | 250 | F6.8841.../2420129 | Error code issue Email By - Service Dealer Name -Bharat Singh | Task Start | Tng Exploration JV. Pvt. Limited. | Rajdhani Diesels and Electricals - Jodhpur | 70 | Low DEF level, top up DEF and educated the customer about the same . | Closed | Gourav Sharma
6 | 211078071 | 14-08-2024 10:49 | 40 | 3H.8951.../2420099 | oil Leakage issue Call By Customer Name :-Ashish .. Mobile No :-7500008259 | Task Start | Aaryash Broiler Farms Pvt. Ltd. | R K Engineers - Saharanpur | 112 | Oil leakage from Oil filter assly..Lnkey bolt loose, tighten the same issueresolved. | Closed | Sudhir Awasthi
7 | 211078002 | 14-08-2024 10:26 | 250 | F6.8841.../2420208 | Starting issue Call By Customer Name : Ajay Kumar No:- 8950003651 | Task Start | Sawaraj Overseas | Vishal Power Systems - PANIPAT | 3 | Update Pending | Open | Kapil Solanki
8 | 211077929 | 14-08-2024 10:12 | 125.4 | 4H.8041.../2320054 | Tripping Issue Call BY Customer Name :- Rajesh No ;- 9953102701 | Task Start | THERMADYNE PVT. LTD. | Paluck Technologies Ltd. - Faridabad | 307 | Exhaust manifold braket bolt broken and fan drive broken and also found braket bolt in head, after welding , tighten the same and also Oil leakage from oil header assly plug, and canopy door form was damage tighten the plug issue resolved. | Closed | Kapil Solanki | Campaign need to confirm
9 | 211077843 | 14-08-2024 09:57 | 250 | F6.8841.../2420069 | Starting Issue Call by Customer Name - Lekhraj . Number -9816901527 | Task Close | Innova Captab Limited. | SAAN Royal Power Solutions Private Limited - Zirakpur | 58 | As priviously discussed, Rain Water entry in Canopy, and waterin fuel alarm, SR open for clear the fault code and cleaning Fuel tank. | Closed | Ved Gupta
10 | 211077839 | 14-08-2024 09:57 | 200 | 6H.8435.../2320031 | Starting issue & belt Broke issue Call By Customer Name :- Aditya Aryan No:-8839388441 | Task Start | OIL INDIA LTD. | Rajdhani Diesels and Electricals - Jodhpur | 734 | As priviously disccused, fan belt broken, replaced the same issue resolved. | Closed | Gourav Sharma
11 | 211077738 | 14-08-2024 07:18 | 250 | F6.8841.../2320015 | Starting Issue Call By Customer Name:-Abhishek Kumar No:-7903795913 | Task Start | HIND TERMINALS [P] LTD | Paluck Technologies Ltd. - Faridabad | 398 | Update Pending | Open | Kapil Solanki
1 | 211079211 | 14-08-2024 14:07 | 25 | GP3.8702.../2420122 | Oil leakage Call by : Customer Name : Srinivasulu Contact : 9849554400 | Open | Prasad Trading Company | Ultimate Power Source - Kurnool | 3 | Sump crack case , they replaced the sump with new one . | Closed | Mr Sanjaymon
2 | 211078440 | 14-08-2024 11:07 | 500 | DV8.8501.C4../2420070 | NOT START | Task Start | Nesto Hypermarket | G-Care Diesels Private Limited - Malappuram | LR | Checked the ITV harness (SPN51/FMI1) and supply voltage it was normal so suspected on ITV and Then checked Fuel pressure and pressure sensor was found External damage which was the cause of 2 Faultcodes (1. 2980/3 2. 5785/3), Both the parts are Placed EDO Related Photos are attached in 16-Aug-2024 Folder. | Closed | Mr Sanjaymon | material received at SD end planned tomorrow
3 | 211078099 | 14-08-2024 10:59 | 25 | GP3.8702.../2320016 | Automation Issue Email By KGD Name:-Srinivas | Task Start | Mr. Srinivasa G. K. | Surya Power Services - Bommasandra, Bangalore | 6 | emergency fault code shown on controller , loose connection found , tightend the same . | Closed | --
1 | 211087721 | 17-08-2024 15:17 | 58.5 | T4.8941.../ 2420624 | Error Code Issue Call By Customer Name:- Divakar Kumar Mo No:-9199703022 | Closed | Yadav Tent House | Globalline India Services Private Limited - Darbhanga | 35 | customer open the SR due to water in fuel alarm, engineer viist the site open the filter nad drain the water, hence issue resolved. | CLOSED | Prabhakar Kumar | ECU DTC check | KRM show DTC 5838/1 ,2802/3 in this asset.
2 | 211082834 | 16-08-2024 11:06 | 20 | GP3.8604.../ 2420026 | DG capacitor found faulty DG ISSUE | Closed | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | 55 | DG shutdown by high canopy temp. alarm engineer vist the site and check all the connection and then start after 30 min, no such issue found again. | CLOSED | Prabhakar Kumar | Needc to share alarm details logic
3 | 211076535 | 13-08-2024 16:30 | 125.4 | 4H.8041.../ 2420557 | Starting Issue Email by KGD Name - Kartick | Cancelled | Heto Yeptho. | M/s Hindustan Powerkraft - Dimapur | NA | Heto Yepto. Customer asked to visit on monday. Site is in remote location. Today SE will visit | OPEN | Subhrajit Roy | KRM check | Data does not capature so requried to check internet connection of KRM.
1 | 211080311 | 14-08-2024 16:41 | 750 | DV2.8501.C4../2320011 | Tourba issue Call by Service Dealer Name:Kapil Number: 9953742728 | Closed | Merino Industries Ltd. | Paluck Technologies Ltd. - Ghaziabad | 124 | SR Open for fixed thermal shield jacket | Closed | Kapil Solanki
2 | 211080592 | 14-08-2024 17:27 | 320 | F6.8802.../2320031 | Adblue Issue Email by Service Dealer Name - SUNITA | Completed | Sanspareils Greenlands Pvt. Ltd. | R K Engineers - Meerut | 330 | DEF level was low ,top up the DEF and educated the customer about the same issue resolved. | Closed | Sudhir Awasthi
3 | 211080600 | 14-08-2024 17:29 | 15 | GP3.8501.../2420567 | Low RPM Issue Call By KGD Name :- Faiyazul Hasan Mobile No :- 9451547084 | Closed | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW | 35 | Customer side change over issue , mains voltage obtained 100 volt , Educated the customer about the same issue resolved. | Closed | Sudhir Awasthi
4 | 211080939 | 14-08-2024 21:16 | 57 | T4.8941.../2320261 | Starting Issue Call By Customer Name :- Ashok Mobile No :- 7678512026 | Open | Kalina Overseas Pvt. Ltd. | Vidyut Engineers - Noida |  | SR will be cancel | Cancelled | Kapil Solanki
5 | 211081838 | 15-08-2024 09:58 | 30 | 3H.8902.../2420177 | Error Code Issue Call By Customer Name :-S.K. Bajaj Mobile No :-8233604489 | Open | U. M. A. Bajaj | Pratap Diesels Pvt. Ltd. - Alwar | 579.3 | Error code issue , engineer did not checked the DTC just clear the DTC , revisit required | Open | Gourav Sharma | krm CHECK | Check KRM data but does not show any type of fault code.
6 | 211081875 | 15-08-2024 10:54 | 500 | DV8.8501.C4../2420062 | Error code issue Call by customer Name:-O P SINGH Number :-8708612594 | Task Start | HL. Residency Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | customer complain about fuel level low showing on KRM , engineer did not found any issue , checked the event log found ok , checked sensor found ok . | Closed | Kapil Solanki
7 | 211081895 | 15-08-2024 10:57 | 125.4 | 4H.8041.../2320131 | Alarm Issue Email By Customer Name:-rewfbd2 | Task Start | Yogesh Engineering Works | Paluck Technologies Ltd. - Faridabad | 70.23 | SPN/FMI - 1761/14 DEF level was low @0%. Educated the customer about the same issue resolved. | Closed | Kapil Solanki
8 | 211082189 | 15-08-2024 22:01 | 200 | 6H.8435.../2320030 | Starting Issue Call By Customer Name:-Monika No:-8851404360 | Open | Usis Infra Solution | Vidyut Engineers - Noida | 42.35 | Customer side panel issue , DG contractor was not hold , educated the customer about the same issue resolved. | Closed | Kapil Solanki
1 | 211091096 | 19-08-2024 15:26 | 625 | DV0.9031.../2300002 | Water leakage Issue Email By KGD Name:-Anil Wagh | Completed | Avante Spaces Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | Na | Water entry in canopy, taken up with goem. | Closed | Jagdeep Saini
2 | 211091095 | 19-08-2024 15:25 | 500 | DV8.9312.../2300002 | Water leakage & Rain guard not supplied Email By KGD Name:-Anil Wagh | Completed | Avante Spaces Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | Na | Water entry in canopy, taken up with goem. | Closed | Jagdeep Saini
3 | 211089014 | 18-08-2024 09:54 | 200 | 6H.8435.../2420028 | Ad blue Leakage issue Email By KGD Name:- ROHIT KAMBLE | Task Start | Shri Ram Infra | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 94 | def leakage in pipe from supply module to dosing module | Closed | Jagdeep Saini | Communication to west team
4 | 211082841 | 16-08-2024 11:10 | 20 | GP3.8601.../2420560 | Starting Issue Call By Service Dealer Name :Payal Sahu No:-7415232771 | Closed | Om Prakash Verma. | Shree Engineering Service - Raipur | Na | Amf panel issue | Closed | Vijay Patil
5 | 211087967 | 17-08-2024 16:18 | 82.5 | 5H.8901.../2420100 | Oil leakage issue Call By Customer Name : -Parshant No:-9130726109 | Closed | GRN Constructions Pvt. Ltd. | Dicksons Engineering Co.Pvt.Ltd. - Yavatmal | 460 | Minute oil lekage from breather joint engine side | Closed | Jagdeep Saini
6 | 211089413 | 18/08/2024 15:36:07 | 200 | 6H.8435.../2420035 | Under Speed Alaram call by customer Name - Virendra Kumar number - 9725270303 | Closed | Ashish Brass Components Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Jamnagar | 7 | Genset not stating issue. The 2C wire was out of the feed pump relay. | Closed | Amit Shandilya
7 | 211080797 | 14-08-2024 18:07 | 57 | T4.8941.../2420373 | WARRANTY SERVICE CHECKS / CSP CC | Closed | Rituma Clinic. | Unique Techno Services Pvt Ltd. - Baroda | 1 | Genset not starting issue.SPN/FMI-157/14 and 920/5 was showing in the DM2. Checked the main relay and start relay found ok. Checked the PRV count through the I Konnect which was 9. | Closed | Amit Shandilya | Under obs
8 | 211090656 | 19/08/2024 12:16:13 | 30 | 3H.8902.../2420502 | Under Speed Alarm Issue Call By GOEM Name:Dhruv Mistry Mobile No:9099905622 | Task Start | Jignesh Dhirubhai Patel | Unique Techno Services Pvt Ltd. - Anand | Na | Visit Pending | Open | Amit Shandilya
9 | 211082544 | 16-08-2024 09:44 | 160 | 6H.8475.../2320007 | Coolant Level Low Alarm Call By Service Dealer Name :-Manoj Mobile No :-9879616348 | Closed | BOCHASANWASI SHRI AKSHAR PURUSHOTTAM PUBLIC TRUST | Unique Techno Services Pvt Ltd. - Baroda | 83 | Coolant Consumption | Closed | Amit Shandilya | Under obs
1 | 211082330 | 16-08-2024 08:59 | 250 | DV8.9863.../2320013 | Abnormal Sound Â Issue Call By Customer Name :-Gorakh Nath Yadav Mobile No :-9650765511 | Task Start | ADECO ENERGY INDIA PVT. LTD. | Vidyut Engineers - Noida | 517.38 | Abnormal sound from exhaust side, found exhaust gas leakage from exhaust manifold joint , replace the bolt and gasket issue resolved | Closed | Kapil Solanki
2 | 211082472 | 16-08-2024 07:34 | 160 | 6H.8475.../2420031 | MIL Lamp On Alarm Abnormal Sound & Fan Belt Issue Call By Â Customer Name :-Rohit Malik Mobile No :-9999637245 | Closed | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 506.8 | SPN/FMI - 5461/0 flash the cal file And fan belt was loose tighten the same issue resolved | Closed | Kapil Solanki
3 | 211082739 | 16-08-2024 10:40 | 40 | 3H.8951.../2420421 | Starting Issue Email By - Service Dealer Name - NIDHI | Task Start | RPM Academy | S. R Engines Sales And Service - Gorakhpur | 5 | Starting issue , checked Fuel line found ok , just pressed the hand feed pump issue resolved. | Closed | Sudhir Awasthi
4 | 211082764 | 16-08-2024 10:41 |  | T4.8941.../2420812 | Lube oil leakage | Task Start | Green Field Enterprises | Suraj Motor Store - kathua |  | oil leakage from breather , some modification of breather issue resolved | Closed
5 | 211082853 | 16-08-2024 11:06 | 750 | DV2.8501.C4../2420011 | maintenance due Alarm issue Call By Customer Name : -Parvesh Kumar No:-9720093797 | Task Start | Sleek Brake Products | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | SR will be cancel , need to CSP | cancelled | Kapil Solanki
6 | 211083021 | 16-08-2024 11:45 | 125.4 | 4H.8041.../2320139 | Starting Issue Email By - Service Dealer Name - | Task Start | Vijay Lakshmi Transoltions Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 37 | DEF level was low , Educated the customer about the same issue resolved | Closed | Kapil Solanki
7 | 211083074 | 16-08-2024 11:46 | 15 | GP3.8501.../2420081 | Starting Issue Call By Customer Name :- Karan . Mobile No :-9646699552 | Task Start | Espana Tex | Industrial Power Solutions - LUDHIANA | 19 | SPN/FMI - 970/31 Related emergency stop engineer checked wiring found 4 PIN Connector was loose tighten the same issue resolved. | Closed | Gourav Sharma
8 | 211083102 | 16-08-2024 11:59 | 500 | DV8.8501.C4../2320073 | Rain water leakage Issue Call By Customer Name : Pradip . No : 7988465905 | Task Start | A C POLYCOATERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Visit pending | Open | Kapil Solanki
9 | 211083136 | 16-08-2024 12:04 | 125.4 | 4H.8041.../2320153 | Starting Issue Email By - KGD Name - BNP Enterprises | Task Start | B. N. P. Enterprises | OVN Industries Private Limited - New Delhi | 12 | Starting issue due to battery was discharge , Customer NON KOEL battery charger use , connected KOEL battery charger and educated the customer about the same issue resolved. | Closed | Kapil Solanki
10 | 211083145 | 16-08-2024 12:13 | 15 | GP3.8501.../2420507 | Voltage Issue And Automation Issue Call By Customer Name :-Monu ... Mobile No :-9219656825 | Task Start | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
11 | 211083146 | 16-08-2024 12:13 | 125.4 | 4H.8041.../2320033 | Fan belt issue Call By Â Customer Name :-Santan Singh Mobile No :-9868488469 | Open | Kumar Generator House | Paluck Technologies Ltd. - Ghaziabad | 308 | abnormal sound from fan side ,found Fan belt support guard was broken , and minor damage on fan (need to replace support guard) | Open | Kapil Solanki | One pager and part nos to be share
12 | 211083154 | 16-08-2024 12:13 | 57 | T4.8941.../2420173 | fuel sensor issue & Door lock issue Call By Customer Name:- Manoj Pande Mo No:-9810411059 | Task Start | SUNLIGHT ENGINEERS | OVN Industries Private Limited - New Delhi |  | controller side Door lock issue..adjust the lock , Engineer did not found any issue related to fuel sensor. | Closed | Kapil Solanki
13 | 211083187 | 16-08-2024 12:21 | 40 | 3H.8951.../2420083 | Starting Issue Call By KGD Name :- Bharat Mobile No :-9729814012 | Open | PREEMIER AGENCIES | M/s OM Diesels Pvt. Ltd. - Rohtak | 20 | Battery side door alignment issue , door not closing properly, need to checked. | Open | Kapil Solanki
14 | 211083240 | 16-08-2024 12:38 | 58.5 | T4.8941.../2420718 | Starting issue Call By Customer Name : Manish . No:-7318309730 | Task Start | Akhilesh Enterprises | S.S. Enterprises - Allahabad | 42 | starting issue due to DC MCB (2A ) wire was loose condition tighten the same issue resolved . | Closed | Sudhir Awasthi
15 | 211083320 | 16-08-2024 12:52 | 125.4 | 4H.8041.../2420150 | Starting Issue Email By Service Dealer Name:- VINAY KUMAR | Task Start | Anshuman Jain HUF | Vidyut Engineers - New Delhi | 8 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
16 | 211083475 | 16-08-2024 13:31 | 125.4 | 4H.8041.../2420283 | Abnormal Sound Call by customer Name:-Pavan Rajput No:-9971445699 | Task Start | Vijay Sales (India) Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 61 | Customer complain about abnormal sound issue , engineer did not found any issue , also customer want to know who to checked DEF level and consumption of DEF | Closed | Kapil Solanki
17 | 211083578 | 16-08-2024 13:54 | 15 | GP3.8501.../2420555 | Voltage Issue And Automation Issue Call By Customer Name:-Monu ... No:-9219656825 | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
18 | 211083671 | 16-08-2024 14:29 | 15 | GP3.8501.../2420571 | Automation issue & Voltage issue Call By Customer Name :- Monu Mobile No :-Â 9219656825 | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
19 | 211083675 | 16-08-2024 14:29 | 62.5 | T4.8941.../2420291 | Oil leakage issue Call by customer Name:-Amit bawa No:-Amit bawa | Task Start | Designers Terracotta Collection By Sheetal | Vishal Power Systems - PANIPAT | 23.55 | Coolant leakage from EGR outlet supply line, tighten the same issue resolved , and oil leakage but engineer could not find where the leakage , need to check | Open | Kapil Solanki
20 | 211083682 | 16-08-2024 14:20 | 750 | DV2.8501.C4../2320028 | Overheating-TURBO CHARGER RED ISSUE | Closed | Merino Industries Ltd. | Paluck Technologies Ltd. - Ghaziabad | 116 | SR Open for fixed thermal shield jacket | Closed | Kapil Solanki
21 | 211083947 | 16-08-2024 15:18 | 125.4 | 4H.8041.../2320137 | Starting Issue Call By Customer Name :-Amarjeet Mobile No :-9873530243 | Closed | Kamal Enterprises | Vidyut Engineers - Noida | 29.42 | DEF level was low , top up the DEF and educated the customer about the same . | Closed | Kapil Solanki
22 | 211084679 | 16-08-2024 15:58 | 125.4 | 4H.8041.../2420076 | Coolant issue. Email By Service Dealer Name:-akash | Task Start | RS. Industries | Espiem Engines & Machines (P) Limited - Aligarh | 417 | Coolant leakage from coolant hose pipe tighten the same and SPN/FMI - 5461/0 flash the file issue resolved . | Closed | Sudhir Awasthi
23 | 211084868 | 16-08-2024 16:09 | 58.5 | T4.8941.../2420656 | Door Lock Call By Customer Name : Rahul Saini No:-7838129362 | Task Start | WOW EQUIPMENT & INFRA PVT LTD | Vishal Power Systems - PANIPAT | 6 | Door lock issue , Need to change lock | Open | Kapil Solanki | GOEM portal
24 | 211084939 | 16-08-2024 16:32 | 500 | DV8.8501.C4../2320027 | Radiator Cleaning Issue Email by Service Dealer Name - ARJUN PANWAR | Closed | MULBERRY PROJECTS PRIVATE LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 160 | Clean the radiator under warranty. | Closed | Kapil Solanki
25 | 211085338 | 16-08-2024 17:55 | 750 | DV2.8501.C4../2420003 | Starting problem & Alarm Issue. Email By - Service Dealer Name -Pratap Diesels Pvt. | Closed | Bhabani Colors Pvt. Ltd. | Pratap Diesels Pvt. Ltd. - Alwar | 117 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Gourav Sharma
26 | 211085410 | 16-08-2024 18:15 | 15 | GP3.8501.../2420570 | KRM Issue Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
27 | 211085413 | 16-08-2024 18:16 | 15 | GP3.8501.../2420489 | KRM Issue Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
28 | 211085416 | 16-08-2024 18:17 | 15 | GP3.8501.../2420502 | VOLTAGE PROBLAM Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
29 | 211085418 | 16-08-2024 18:18 | 15 | GP3.8501.../2420500 | VOLTAGE PROBLAM Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
30 | 211085419 | 16-08-2024 18:19 | 15 | GP3.8501.../2420490 | VOLTAGE PROBLAM Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
31 | 211085420 | 16-08-2024 18:20 | 15 | GP3.8501.../2420498 | VOLTAGE PROBLAM Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled | Sudhir Awasthi
33 | 211085442 | 16-08-2024 18:21 | 15 | GP3.8501.../2420467 | VOLTAGE PROBLAM Email By Customer Name:- Faiyaz | Open | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW |  | SR Will be Cancel , need to service activity , SR opened on CSP . | cancelled
34 | 211085498 | 16-08-2024 19:08 | 40 | 3H.8951.../2320086 | Low voltage Alarm issue Call By Customer Name :-Rawat Mobile No :-9911002256 | Task Start | MEHAR WING SERVICES PRIVATE LIMITED | Vidyut Engineers - New Delhi | 38 | DG was tripping with showing over current alarm , DG running on over load educated the customer about the same issue resolved. | Closed | Kapil Solanki
1 | 211086386 | 17-08-2024 09:34 | 125.4 | 4H.8041.../2420135 | Starting issue Call By Customer Name : Rahul Kumar No:7250957856 | Closed | B & B GROWING PROMOTERS PRIVATE LIMITED | Paluck Technologies Ltd. - Faridabad | 150 | DEF level @0% top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
2 | 211086633 | 17-08-2024 10:38 | 125.4 | 4H.8041.../2320013 | Abnormal sound issue Call By Service Dealer Name:- Dharmesh Mo No:- 7027820034 | Task Start | JAYCEE CASTALLOYS (P) LTD. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Visit pending | Open | Kapil Solanki
3 | 211086765 | 17-08-2024 11:06 | 400 | DV8.8542.C4../2420010 | Filter Change Issue Call By Customer Name :-Rashid .. Mobile No :-9891324384 | Closed | MCAM. Surion India Ltd. | Paluck Technologies Ltd. - Ghaziabad | 84 | fuel filter change , at CSP time filter was not available | Closed | Kapil Solanki
4 | 211086797 | 17-08-2024 11:19 | 125.4 | 4H.8041.../2420180 | Filter Change Issue Call By Customer Name :-Rashid .. Mobile No :-9891324384 | Closed | SURLON ADVANCE MATERIALS PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 43 | fuel filter change , at CSP time filter was not available , battery charger was not connected ,educated the customer about the same issue resolved. | Closed | Kapil Solanki
6 | 211086877 | 17-08-2024 11:38 | 625 | DV0.8501.C4../2320010 | Error code issue Call By Customer Name :-Sanjiv Kumar Mobile No :-8814828270 | Task Start | Forech Mining & Construction International LLP | M/s OM Diesels Pvt. Ltd. - Sonipat | 174.5 | DG was tripping with showing negative phase sequence alarm , need to revisit with KOEL team . | Open | Kapil Solanki | KRM check | Check data and found genset trip R phase sudunly with zero load.
7 | 211086950 | 17-08-2024 11:45 | 20 | GP3.8601.../2320063 | TrippingÂ Issue Call By Customer Name :-Bharat Bhushan Mobile No :-9810314268 | Task Start | ASHA NAND SR. SEC. SCHOOL | Paluck Technologies Ltd. - Faridabad | 41 | starting issue with showing emergency stop alarm , found emergency switch was pressed condition , correct the same and educated the customer about the same issue resolved. | Closed | Kapil Solanki
8 | 211086973 | 17-08-2024 11:58 | 125.4 | 4H.8041.../2420289 | Starting Issue Call By Â Customer Name :-Indra Pal Mobile No :-9813020097 | Task Start | Supreme Mobile Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - HISAR |  | DEF level was low . Top up the DEF educated the customer about the same issue resolved. | Closed | Kapil Solanki
9 | 211087027 | 17-08-2024 12:09 |  | T4.8941.../2421519 | Starting Issue | Task Start | Green Field Enterprises | Suraj Motor Store - kathua |  | Charging alternator side fuse and wiring harness was burnt , EDO the wiring harness | Open
10 | 211087088 | 17-08-2024 12:27 | 45 | 3H.8951.../2420277 | Tripping & Load Issue Email by KGD Name - Neeraj Saini | Task Start | Sarvodaya Bal Bharti Sr. Sec. School | Pratap Diesels Pvt. Ltd. - Alwar | 32 | DG was running unbalance load (R=16Amp,Y=70Amp,B=6 Amp) Educated the customer about the same issue resolved . | Closed | Kapil Solanki
12 | 211087271 | 17-08-2024 12:58 | 25 | GP3.8702.../2420082 | starting issue | Task Start | Gurjeet Singh | OVN Industries Private Limited - New Delhi |  | DG Was tripping with showing under speed alarm , reset the alarm , checked fuel line found ok. | Closed | Kapil Solanki
13 | 211087324 | 17-08-2024 13:03 | 250 | F6.8841.../2320017 | Water Leakage Issue Email By - Customer Name - Satvik qc | Open | SATVIK TECHZONE PRIVATE LIMITED | Paluck Technologies Ltd. - Gurgaon |  | water entry in canopy , SR open on GOEM portal | cancelled | Kapil Solanki
14 | 211087578 | 17-08-2024 14:39 | 40 | 3H.8951.../2320028 | Starting issue Call By KGD Name : Vipin No:9999762509 | Task Start | St. Marks World School | OVN Industries Private Limited - New Delhi |  | DG Was tripping with showing under speed alarm , reset the alarm , checked fuel line or air line found ok , and checked control panel wiring found ok. | Closed | Kapil Solanki | KRM check | KRM does not start send mail for KRM starting.
15 | 211087580 | 17-08-2024 14:39 | 40 | 3H.8951.../2320064 | Tripping & Overload Call by Service Dealer Name:-Raj No:-8595491685 | Task Start | Tounetsu India Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 244 | DG Was running over load and jerk load , educated the customer about the same issue resolved. | Closed | Kapil Solanki
16 | 211087681 | 17-08-2024 14:54 | 82.5 | 5H.8901.../2320073 | Amber lamp alarm Call By Customer Name : MP Shukla No: 9811540438 | Open | S.B.INDUSTRIES SEATS PRIVATE LIMITED | Vidyut Engineers - Noida | 75.55 | DEF Level was low @47% top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
17 | 211087720 | 17-08-2024 15:17 | 320 | F6.8802.../2420101 | Red Lamp On Alram Issue Call By Customer Name :-Anis Mobile No :-9569285157 | Open | CHANDIGARH EDUCATION TRUST | SAAN Royal Power Solutions Private Limited - Zirakpur | 104 | DEF low related fault code , customer top up the DEF , need to clear the code. | Closed | Kapil Solanki
19 | 211087727 | 17-08-2024 15:07 | 57 | T4.8941.../2320040 | Tripping Issue Call By Customer Name :Umesh Dhavan Mobile No :9213428845 | Closed | Hariom Tools | Paluck Technologies Ltd. - Faridabad |  | Customer side CNC machine was Tripp ,DG was running on jerk load (13 kw to 35 kw) Educated the customer about the same issue resolved. | Closed | Kapil Solanki
20 | 211087879 | 17-08-2024 15:53 | 160 | 6H.8475.../2420006 | fuel Sensor Issue Call By Customer Name : Shubahm Kumar No:- 6306784581 | Closed | India Shine Technologies | Paluck Technologies Ltd. - Faridabad | 467 | incorrect fuel level showing on controller , sometime showing 74% and 60 % , then removed the sensor and clean then refitted. Need to checked | Open | Kapil Solanki
21 | 211087921 | 17-08-2024 16:06 | 40 | 3H.8951.../2420027 | Fuel Sensor issue Call By Customer Name :-Rajendra Kumar Mobile No :-7876723618 | Task Start | Aksh Lights India | Vishal Power Systems - Karnal |  | Visit pending | Open | Kapil Solanki
22 | 211088825 | 17-08-2024 18:03 | 160 | 6H.8475.../2420006 | fuel Sensor Issue Call By Customer Name : Shubahm Kumar No:- 6306784581 | Open | India Shine Technologies | Paluck Technologies Ltd. - Faridabad |  | SR Will be cancel , SR opened by mistake | cancelled | Kapil Solanki
23 | 211089016 | 18-08-2024 10:04 | 58.5 | T4.8941.../2420289 | On off SWICH issue call by customer Name :-Bhart . Number :-7879001370 | Task Start | Geeta Kanwar. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 22 | Customer complain about starting issue , engineer did not found any issue . | Open | Kapil Solanki
24 | 211089311 | 18-08-2024 09:50 | 750 | DV2.8501.C4../2320005 | Air leak issue Call By Customer Name :- Anup kumar yadav Number :-9429459334 | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 280.22 | Exhaust gas leakage from exhaust manifold and turbo joint , need to replace gasket and turbo turning read hot , | Open | Kapil Solanki
26 | 211089333 | 18-08-2024 11:06 | 57 | T4.8941.../2320261 | Starting issue call by customer Name :-Sanjeev Kumar Number :-9717092665 | Task Start | Kalina Overseas Pvt. Ltd. | Vidyut Engineers - Noida | 113.25 | Starting issue due to start relay not working properly , press on the relay issue resolved . | Closed | Kapil Solanki
27 | 211089354 | 18-08-2024 11:42 | 125.4 | 4H.8041.../2420124 | Automation Issue Call By Customer Name:-Pashupati No:-9990056848 | Task Start | Venus CGHS. Ltd. | OVN Industries Private Limited - New Delhi | 15.8 | DG was not start in auto mode Due to customer side AMF panel selector switch select on manual mode correct the same and educated the customer about the same issue resolved. | Closed | Kapil Solanki
28 | 211089456 | 18-08-2024 16:01 | 320 | F6.8802.../2320013 | Under Voltage Alarm & ECE Amber issue Call By Customer Name:- Roshanlal Number:- 9672175373 | Open | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar |  | Visit pending | Open | Kapil Solanki
29 | 211089457 | 18-08-2024 16:06 | 500 | DV8.8501.C4../2320062 | Starting issue Call By Customer Name : Janardan . No:- 9818701730 | Task Start | A C POLYCOATERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Visit pending | Open | Kapil Solanki
30 | 211089514 | 18-08-2024 21:31 | 125.4 | 4H.8041.../2420011 | Starting Issue Call By Customer Name:Sudha Yadav Mobile No:7015649774 | Open | Sweta Medicose | Paluck Technologies Ltd. - Gurgaon | 387 | DEF level was low , before Engineer reached at site customer top up the DEF , Engineer just clear the DTC and educated the customer about the same issue resolved | Closed | Kapil Solank
8 | 211083102 | 16-08-2024 11:59 | 500 | DV8.8501.C4../2320073 | Rain water leakage Issue Call By Customer Name : Pradip . No : 7988465905 | Task Start | A C POLYCOATERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Rain water entry in canopy , rain guard was not fitted , | Open | Kapil Solanki
1 | 211086633 | 17-08-2024 10:38 | 125.4 | 4H.8041.../2320013 | Abnormal sound issue Call By Service Dealer Name:- Dharmesh Mo No:- 7027820034 | Task Start | JAYCEE CASTALLOYS (P) LTD. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh | 105 | DEF level was low top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
2 | 211087921 | 17-08-2024 16:06 | 40 | 3H.8951.../2420027 | Fuel Sensor issue Call By Customer Name :-Rajendra Kumar Mobile No :-7876723618 | Task Start | Aksh Lights India | Vishal Power Systems - Karnal |  | fuel level was not showing (circuit open ) showing , found fuel level sensor input wire was loose condition , tighten the same issue resolved. | Closed | Kapil Solanki
3 | 211089327 | 18-08-2024 10:58 | 82.5 | 5H.8901.../2320084 | Tripping Issue Call by customer Name:-Sahil Rana No:- 7300651325 | Closed | AMBITION RETAILS ALLIANCE LLP | OVN Industries Private Limited - New Delhi | 1729.58 | SPN/FMI - 633/3 (DM2), 516166/0 (DM1) clear the DTC issue resolved . | Closed | Kapil Solanki | Under observation
4 | 211089456 | 18-08-2024 16:01 | 320 | F6.8802.../2320013 | Under Voltage Alarm & ECE Amber issue Call By Customer Name:- Roshanlal Number:- 9672175373 | Open | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar |  | visit pending | Open
5 | 211089457 | 18-08-2024 16:06 | 500 | DV8.8501.C4../2320062 | Starting issue Call By Customer Name : Janardan . No:- 9818701730 | Task Start | A C POLYCOATERS PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Self starter was not working , under repair. | Open | Kapil Solanki
6 | 211090259 | 19-08-2024 10:20 | 125.4 | 4H.8041.../2420119 | Automation Issue Call By Customer Name :- Sunil ... Mobile No :-8708273237 | Open | Masyc Projects Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Automation issue , DG was not started in auto mode , found negitive sensing was missing from customer side panel, correct the same issue resolved. | Closed | Kapil Solanki
7 | 211090404 | 19-08-2024 10:57 | 40 | 3H.8951.../2420222 | Air Lock Issue Email By Koel Person Name:-Nitin Shekhar Singh | Open | Rajiv Auto Power. | Industrial Power Solutions - LUDHIANA | 8 | Starting issue , DG start after press hand feed pump , every time ,Fuel filter assembly with hand primer to be changed | Open
8 | 211090963 | 19-08-2024 13:53 | 125.4 | 4H.8041.../2320124 | Starting Issue Call By Customer Name :-puran Mobile No 7303207112 | Task Start | Nanak Sai Estate LLP. | Vidyut Engineers - Noida | 52.8 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
9 | 211091417 | 19-08-2024 17:20 | 125.4 | 4H.8041.../2420008 | Load Issue Email by Service Dealer Name - Junaid | Task Start | Leighton India Contractors Private Limited | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 1814 | Air filter and primary fuel filter was choke , fuel filter was not available (constriction side ) | Closed | Kapil Solanki
10 | 211092197 | 20-08-2024 10:13 | 82.5 | 5H.8901.../2320086 | Under Speed Alaram issue Call By Customer Name :- Gaurav .. Mobile No :- 9911909109 | Task Start | PSG. International | Paluck Technologies Ltd. - Faridabad | 104 | Starting issue found battery voltage was 11.7 volt , checked battery charger found battery charger was not working ( Battery charger AC input was 225 volt , battery charger output was 0 volt ) also mains MY1 fuse was blown , need to change battery charger | Open | Kapil Solanki | Failure part
11 | 211092252 | 20-08-2024 10:23 | 40 | 3H.8951.../2320078 | Display Issue Call By Customer Name:Aashu Jeshwal Mobile No:9718850143 | Task Start | PSG ELECTRICALS | Vidyut Engineers - Noida | 147.35 | incorrect fuel level showing on controller , showing @100%, then removed the sensor and clean then refitted. After that the fuel level isshowing@93% after refitting , issue resolved | Closed | Kapil Solanki
12 | 211092291 | 20-08-2024 10:40 | 62.5 | T4.8941.../2420119 | Voltage Issue Email By Service Dealer Name:-Rahul Sharma | Task Start | Jain Garments | M/s OM Diesels Pvt. Ltd. - HISAR | 55 | DG was tripping with showing under voltage alarm . Found AC alternator terminal bar plate was burned , replace the same issue resolved. | Closed | Kapil Solanki
13 | 211092459 | 20-08-2024 11:24 | 250 | F6.8841.../2420063 | Controller off problem | Task Start | The Kidney Hospital | Vishal Power Systems - PANIPAT | 5 | Sometime Controller did not turn OFF , found DC supply ON off switch wire(2B3) was loose tighten the same issue resolved. | Closed | Kapil Solanki | Detail required
14 | 211092490 | 20-08-2024 11:37 | 750 | DV2.8501.C4../2420037 | UREA LEAKAGE ISSUE Email By Service Dealer Name:-SUNITA | Completed | WIN MEDICARE PVT. LIMITED | R K Engineers - Meerut | 10.43 | customer complain about DEF leakage ,engineer did not found any issue ,customer wanted to show DG parameters , customer side controller. Correct the same. | Closed | Kapil Solanki
15 | 211092660 | 20-08-2024 12:12 | 125.4 | 4H.8041.../2420705 | Starting Issue Call By Customer Name :- Kapil .. Mobile No :- 9811620375 | Task Start | LIBRA DIESEL ENGINEERS... | Vidyut Engineers - Noida | 29.2 | Starting issue with showing on controller 9.8 volt also fuel level was showing incorrect , found XDBK3 (1C2 ) all wire was loose condition , tighten the same issue resolved. | Closed | Kapil Solanki
16 | 211092808 | 20-08-2024 12:48 | 160 | 6H.8475.../2320010 | Power Supply issue Call By Customer Name :-Ravinder Rana Mobile No :-9811811139 | Task Start | Surinder Filling Station | M/s OM Diesels Pvt. Ltd. - Sonipat | 341 | Customer side panel issue (KOEL panel) mains contactor not hold (KOEL panel) , VMR faulty need to change. | Closed | Kapil Solanki
17 | 211092809 | 20-08-2024 12:48 | 125.4 | 4H.8041.../2420179 | Starting Issue Call By Customer Name :Sushil No:9812682231 | Task Start | Shree Shivam Co. Opgroup Housing Society Ltd. | M/s OM Diesels Pvt. Ltd. - Sonipat | 1.55 | starting issue with showing emergency stop alarm , found emergency switch was pressed condition , correct the same also connect the battery charger connection , educated the customer about the same issue resolved. | Closed | Kapil Solanki
18 | 211092812 | 20-08-2024 12:48 | 125.4 | 4H.8041.../2420265 | Diesel % not showing Call By Customer Name :-Lalit Tyagi Mobile No :- 9810138700 | Task Start | SGS DIESEL POWER AND HEAVY ELECTRICAL | Paluck Technologies Ltd. - Ghaziabad | 32 | Incorrect fuel level showing on controller , need to check. | Open | Kapil Solanki
19 | 211092938 | 20-08-2024 13:18 | 57 | T4.8941.../2320250 | Canopy Door lock Issue Call By Customer Name :- Sanjana . Mobile No :- 8585944939 | Task Start | Shivmani Hospital | Paluck Technologies Ltd. - Faridabad | 151 | controller side Door lock issue , controller side Door lock issue..adjust the lock , issue resolved. | Closed | Kapil Solanki
1 | 211092815 | 20-08-2024 12:48 | 320 | F6.8802.../ 2320052 | Maintenance Due Alram issue Call By Customer Name: Umesh Kumar Number: 8873900917 | Open | Sharan Nursing Home | Globalline India Services Private Limited - Motihari | NA | Visit pending | OPEN | Prabhakar Kumar
2 | 211092524 | 20-08-2024 11:41 | 20 | GP3.8604.../ 2420107 | Mains Contactor failure | Cancelled | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Darbhanga | 55 | SR cancelled for opening AMC SR. | CANCELLED | Prabhakar Kumar
3 | 211092063 | 20-08-2024 08:27 | 125.4 | 4H.8041.../ 2420557 | ENGINE NOT STARTING Email By - Service Dealer Name -PANKAJ KUMAR HAZARIKA | Task Start | Heto Yeptho. | M/s Hindustan Powerkraft - Dimapur | NA | Today engineer will visit. | OPEN | Subhrajit Roy
1 | 211092241 | 20-08-2024 10:38 | 0 | GP3.8501.../2420296 | CHARGING ALT FAILURE | Task Start | JAKSON & COMPANY | Sahyadri Diesels - Silvassa | Na | Replaced the charging alternator | OPEN | Amit Shandilya
2 | 211090656 | 19-08-2024 12:16 | 30 | 3H.8902.../2420502 | Under Speed Alarm Issue Call By GOEM Name:Dhruv Mistry Mobile No:9099905622 | Closed | Jignesh Dhirubhai Patel | Unique Techno Services Pvt Ltd. - Anand | 2h | SPN/FMI- 2802/4 (DM1) and 920/5 (DM2) was showing .Checked the battery voltage and charging alternator wiring found OK.1C2 wire of relay RL1(12RB1) found loose. | Closed | Amit Shandilya
3 | 211092716 | 20-08-2024 12:27 | 20 | GP3.1021.../2420171 | INSTANCE ID- 100748369 SITE ID- I-GJ-BYAD-ENB-G003 CALL BY CUSTOMER\\ DG ISSUE-DG AUOTATION FAULTY NAME- Varun Patel NUMBER- 9265579987 | Open | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Vadagam | Na | Visit Pending | OPEN | Amit Shandilya
1 | 211092153 | 20-08-2024 09:54 | 0 | 4H.8041.../2420444 | Abnormal noise | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai |  | Pending at ASE end | Closed | Mr. Nanda Gopal | checked the engine oil level and coolant level found ok. checked the abnormal sound due to compression leakage. removed the rocker cover box and cylinder head. checked the piston and liner condition found ok. checked the crank case and cylinder head surface found ok. then replaced the new cylinder head gasket. tightness the torque for 18kgm for all cylinder hean bolt. checked the tappet settings. reassembled the all parts. load test not done yet . | load test done .
2 | 211091218 | 19-08-2024 16:28 | 82.5 | 5H.8901.../2320046 | Error code Issue Email by Service Dealer Name - Sudha | Task Start | Vasavi Kalyana Mantapa. | Surya Power Services - Billekahalli | 18.23 | engine fail to stop , calibrate the GCU problem resolved . | Closed | -- | Neec to check
3 | 211091159 | 19-08-2024 15:50 | 25 | GP3.8702.../2420189 | Starting Issue Email by KGD Name - Samadhan Payghan | Task Start | M/s. AMP. Power Solution | Vijayshree Diesel Sales and Service - Bijapur | 64 | Pending at ASE end | Closed | -- | Emergency stop Wiring contions loose, tighetend the same
4 | 211090711 | 19-08-2024 12:36 | 20 | GP3.8601.../2420375 | Starting Problem Call by : Customer Name : Basha Contact : 9963875720 | Closed | Syed Sarfaraz Ahammed. | Ultimate Power Source - Kurnool | 2 | Customer Expecting to start the DG in Auto mode then Engineer visited and Inspect6ed then found there was no AMF panel in site so recommended to buy the panel. | Closed | Mr Sanjaymon
5 | 211089508 | 18-08-2024 21:00 | 82.5 | 5H.8901.../2320035 | Starting Issue Call By Customer Name:Rajshekhar Sir Mobile No:9611726271 | Open | SLV Projects | Surya Power Services - Kalyan Nagar | 1.3 | MIL warning lamp issue & When we do override then only Engine get start, MIL issue got resolved by calibrating the ECU by i-Konnect, but that Override issue is still open. | Closed | -- | KRM check. Under observation
6 | 211087919 | 17-08-2024 16:06 | 25 | GP3.8702.../2420174 | Starting issue Call BY Customer Name :- Harikrishnan No ;- 9606114234 | Task Start | Brigade Enterprises Limited | MULTIVISTA GLOBAL PVT LIMITED - Karapakkam |  | Pending at ASE end | Open | Mr. Nanda Gopal | the Engine is started surprisingly, as per ASE inputs Couldn't able to know the root cause,
7 | 211086531 | 17-08-2024 10:15 | 320 | F6.8802.../2420106 | ECU INTERNAL FAULT ERROR. Email By - Service Dealer Name - AFREEN MS | Task Start | Lotus Enterprises | Vijayshree Diesel Sales and Service - Hospet |  | Pending at ASE end | Closed | -- | Low ad blue level , also silencer is not connected properly . photo not available .
8 | 211086400 | 17-08-2024 09:45 | 250 | F6.8841.../2420083 | Rain Water Entered Issue Email by Customer Name - M.N.Sastry / Naveen | Task Start | Urban Sanctuary LLP. | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 45.23 | rain water entry . | Closed | Mr. Saleem | rain guard is available , water entry from the canopy top .
9 | 211084936 | 16-08-2024 16:29 | 40 | 3H.8951.../2420210 | Under Speed Alram issue Call By KGD Name :-Anil Kumar Mobile No :-9448146897 | Task Start | Neovision Lasik Centre. | Vijayshree Diesel Sales and Service - Bellary |  | Pending at ASE end | Closed | -- | Under Speed Alram issue, one link fuse fail replaced that one .
10 | 211084870 | 16-08-2024 16:09 | 160 | 6H.8475.../2420091 | Display Showing "Ad blue Low" Problem | Task Start | SOWPARNIKA PROJECTS AND INFRASTRUCTURE (P) LTD., | Electro Controls-Coimbatore 2 | 1 | In Supply module outlate union found damage ,photo atteched . | Closed | Mr Sanjaymon
11 | 211083180 | 16-08-2024 12:24 | 200 | 6H.8435.../2320021 | Coolant Leakage Problem Call by : Customer Name : Vignesh Contact : 9790459003 | Task Start | NOVA LIFE SPACE PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | 23.32 | pending | Closed | Mr. Nanda Gopal | coolant leakage due to radiator bottom hose clip loose tension. tightend the same
12 | 211082626 | 16-08-2024 10:09 | 58.5 | T4.8941.../2420459 | Starting Problem Call by : Customer Name : Seshu Contact : 9885420012 | Open | Parvathi. | Powerlinks Infra Tech Pvt Ltd - Madinaguda | 6.5 | EMG pressed by customer , air lock issue , release the same problem resolved . | Closed | Mr. Saleem
13 | 211081841 | 15-08-2024 10:07 | 15 | GP3.8501.../2420404 | Starting issue Call by service dealer Name :-Sandesh NUmber :-7022277053 | Task Start | Trapasol India Private Limited. | Vijayshree Diesel Sales and Service - Bellary | 4 | Pending at ASE end | Closed | -- | dealer not responding , efsr report is also not available .
14 | 211080883 | 14-08-2024 18:44 | 25 | GP3.8702.../2420093 | Starting Problem Call by : Customer Name :Ismail Sir Contact :8921101219 | Task Start | S.B.J. Associates. | G-Care Diesels Private Limited - Thrissur | 9 | engine not start ,controller shown 13 V supply but in I- connect it show 10V , SO check the all connections , RL2 not getting supply , resolved it , than 157/14 alram shown , flash the ECU than refitted the all connection , start the engine , now engine is in normal condition . | Closed | Mr Sanjaymon
15 | 211080821 | 14-08-2024 18:17 | 25 | GP3.8702.../2420174 | Starting Issue Call By Customer Name :- Harikrishnank ... Mobile No :- 9606114234 | Task Start | Brigade Enterprises Limited | Net Work Diesels - Potheri | 16 | pending | Closed | Mr. Nanda Gopal | engine crank but not start , all fuel line remove and refitted , problem got resolved .
16 | 211079422 | 14-08-2024 15:00 | 30 | 3H.8902.../2420269 | Flickering Issue Email by Service Dealer Name - Genearth Services | Task Start | T. M. B. Tirunelveli | Genearth Services - Tirunelveli | 10 | Discussed the SAE 1 type high mass inertia Flywheel recommended to replace, | Open
17 | 211093425 | 20-08-24 15:18 | 20 | GP3.8601.../2420062 | Starting Issue Email By - Service Dealer Name -S.Manigandan | Task Start | Bobby and Boba Saloons Private Limited | Madurai Electro Controls - Sivakasi | 1 | pending | Closed | Mr. Nanda Gopal | rotor winding got cut . photo atteched. | temperorily restore the site by sholdering the wire , tommorow nydec team will visit to site and have plan to restore the isssue at site itself .
18 | 211092813 | 20-08-24 12:48 | 20 | GP3.8601.../2420073 | Emergency Stop Alarm Issue Call By Customer Name :-Vivek Mobile No :-9940124057 | Task Start | Six Square Sports LLP. | MULTIVISTA GLOBAL PVT LIMITED - Karapakkam | 6 | pending | Closed | Mr. Nanda Gopal | emergency alarm issue , ecu connector found loose partially , fitted the same problem resolved
19 | 211092167 | 20-08-24 10:00 | 0 | GP3.8601.../2420603 | AbnormalSound | Task Start | Genlite Engineering Pvt. Ltd. | G-Care Diesels Private Limited - Ernakulam | LR | abnormal sound found in alternator side , they also change the alternator , but problem is not resolved yet . | Closed | Mr Sanjaymon | they check the alternator , winding area found rubbed , also suspect that some issue in crackshaft so now dimantaling process of engine is going on . | engine replacement
1 | 211098112 | 21-08-2024 17:33 | 20 | GP3.8604.../ 2420116 | WATER PUMP FAULTY | Task Start | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Sasaram | 55 | Water pump bearing loose ,found play in waterpump due to which radiator fan touching the radiator body on running. change the pump issue resolved. | CLOSED | Prabhakar Kumar | Failed part
2 | 211092815 | 20-08-2024 12:48 | 320 | F6.8802.../ 2320052 | Maintenance Due Alram issue Call By Customer Name: Umesh Kumar Number: 8873900917 | Cancelled | Sharan Nursing Home | Globalline India Services Private Limited - Motihari | 51 | SR cancelled as it was open for maintenance of DG, SD has send the quotation. | CANCELLED | Prabhakar Kumar
3 | 211092063 | 20-08-2024 08:27 | 125.4 | 4H.8041.../ 2420557 | ENGINE NOT STARTING Email By - Service Dealer Name -PANKAJ KUMAR HAZARIKA | Closed | Heto Yeptho. | M/s Hindustan Powerkraft - Dimapur | 4.41 | ECU locked out alarm was showing,due to hot shut down flash the ECU,issue resolved. | CLOSED | Subhrajit Roy
1 | 211093192 | 20-08-2024 14:28 | 25 | GP3.8702.../2420290 | Starting Issue Call By Customer Name :- Raju Mobile No :- 8299485660 | Closed | SHIVA ENTERPRISES.. | Deep Jyoti Electricals and Services - Bareilly | 17 | controller not turned ON , due to (2C to 2D ) fuse was blown , replace the same issue resolved. | Closed | Sudhir Awasthi
2 | 211093375 | 20-08-2024 15:05 | 750 | DV2.8501.C4../2320031 | Fan Belt Broken Issue Call by Customer Name - Manish ... Number - 9318482747 | Task Start | Aar Aar Technoplast Private Limited | Paluck Technologies Ltd. - Gurgaon | 216 | Fan belt pully was broken, vibration damper bolt was broken , also damage radiator , fan and lube oil filter , decided to replace the engine. | Open | Kapil Solanki
3 | 211093554 | 20-08-2024 15:46 | 250 | F6.8841.../2420138 | Starting Issue Email By Customer Name:-Subhash Chander | Completed | Vikas Stainless Pvt. Ltd. | M/s OM Diesels Pvt. Ltd. - HISAR | 35.1 | Coolant level low was showing on controller, found coolant level switch 1 pin was burned , need to replace coolant level switch . | Open | Kapil Solanki | Failed part required
4 | 211093566 | 20-08-2024 15:52 | 200 | 6H.8435.../2420079 | Adblue Level Issue Email By - Service Dealer Name -Deepak Kumar | Closed | Neeraj Tyagi Contractor | M/s OM Diesels Pvt. Ltd. - Rohtak | 21 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
5 | 211093592 | 20-08-2024 15:53 | 160 | 6H.8475.../2420020 | Black Smoke Issue Call By Customer Name : Manoj Kumar Mobile No : 9891943363 | Task Start | NEWSUN PLASTIC INDUSTRIES | Paluck Technologies Ltd. - Faridabad | 537 | Black smoke on the starting time , and with out load no smoke , check tapped clearance found ok , checked air line and fuel line found ok , DG was jerk load (about 15 KW ) Keep under | Open | Kapil Solanki
6 | 211093766 | 20-08-2024 16:26 | 500 | DV8.8501.C4../2320033 | Turbo issue Call By Customer Name : M.I. Khan . No:9306952708 | Closed | Thermal Papers Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 168 | Turbo turning red hot , need to checked | Open | Kapil Solanki
7 | 211094311 | 20-08-2024 18:18 | 125.4 | 4H.8041.../2320024 | Red lamp alarm Message By Customer Name : Manish Tyagi No : 9643313743 | Task Start | KW. Security & Services Pvt. Ltd. | Vidyut Engineers - Noida | 302.5 | SPN/FMI -1761/16,3218/20,4095/1 , Found NOX sensor was open condition , and checked the dosing module found ok , DEF level was low top up the DEF, DG cooling down period 30 sec , customer not agree to increase the cooling down time. | Closed | Kapil Solanki
8 | 211096035 | 21-08-2024 10:33 | 400 | DV8.8542.C4../2320009 | Controller side Maal Function Ala ram issue Call By Customer Name : Om Chawhan No:- 9837373669 | Closed | T. C. Health Care Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 91 | SPN/FMI -516166/0 ,1761/15,523584/15 clear the DTC and educated the customer about the same. | Closed | Kapil Solanki
9 | 211096321 | 21-08-2024 11:28 | 57 | T4.8941.../2420016 | Load Issue Call By Customer Name :- Rajkumar NO :- 9873308474 | Task Start | KESHAV GENERATORS PVT LTD | Paluck Technologies Ltd. - Gurgaon | 138 | DG was running over load (87A,43A,63A) educated the customer about the same issue resolved. | Closed | Kapil Solanki
10 | 211096393 | 21-08-2024 11:46 | 250 | F6.8841.../2320019 | Tripping issue Call By Customer Name : -Narendra Nagar No:-9811818373 | Task Start | Recons Power Equipments (P) Ltd. | Paluck Technologies Ltd. - Faridabad | 299 | DG was tripping with showing overcurrent and under voltage alarm , engineer checked on load found ok . Keep under observation | Open | Kapil Solanki | KRM check
11 | 211096563 | 21-08-2024 12:16 | 82.5 | 5H.8901.../2320093 | Lamp On Alarm Issue Call By Customer Name :-Sumit Mongia Mobile No :-9818430800 | Task Start | GENERAL AUTOMOTIVES COMPONENTS | Paluck Technologies Ltd. - Gurgaon | 406.57 | SPN/FMI - 516166/0 , clear the DTC , cooling down period is 30 sec , need to revisit | Open | Kapil Solanki
12 | 211096761 | 21-08-2024 12:52 | 250 | F6.8841.../2320030 | Error Code issue Call By Customer Name : -Pradeep No:-7400440465 | Task Start | TRENT LTD | Vidyut Engineers - New Delhi | 51 | DEF level was low @3% top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
13 | 211097144 | 21-08-2024 14:43 | 125.4 | 4H.8041.../2420067 | Starting Issue Call By Customer Name :-Pritam Mobile No :-9414013952 | Open | Mona Power Trading | M/s OM Diesels Pvt. Ltd. - Sonipat |  | visit pending | Open | Kapil Solanki
14 | 211097180 | 21-08-2024 14:57 | 30 | 3H.8902.../2420647 | Starting Issue Email by KGD Name - Sanjeev Jain | Open | Neofit Udyog | Industrial Power Solutions - LUDHIANA |  | visit pending | Open | Ved Gupta
1 | 211096966 | 21-08-2024 13:39 | 750 | DV2.8501.C4../2320027 | Starting Issue Email By-Service Dealer Name:-Sundar | Task Start | Manipal Academy of Higher Education.. | Prasad Power Engineers - Mangalore | 73 | oil filling cap not fitted properly . | Closed | -- | KRM check
2 | 211095928 | 21-08-2024 09:58 | 0 | 5H.5106.../2300001 | LOW FUEL LEVEL | Task Start | Bull Machines Pvt Ltd | Electro Controls - Coimbatore | 805 | 100/1 , 97/5 shown on controller , thry just clean the sensor and refitted it , all fault code got cleared and engine run in normal condition . | Closed | Mr. Nanda Gopal
1 | 211098361 | 21-08-2024 19:15 | 10 | GP3.8301.../2420053 | Trip_Genset_Low_Voltage | Open | HLS ASIA LIMITED | Unique Techno Services Pvt Ltd. - Surat | NA | Visit Pending | Open | Amit Shandilya | Event log
2 | 211092716 | 20-08-2024 12:27 | 20 | GP3.1021.../2420171 | INSTANCE ID- 100748369 SITE ID- I-GJ-BYAD-ENB-G003 CALL BY CUSTOMER\\ DG ISSUE-DG AUOTATION FAULTY NAME- Varun Patel NUMBER- 9265579987 | Open | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Vadagam | NA | Given for cancellation | Open | Amit Shandilya
1 | 211093997 | 20-08-2024 17:28 | 15 | GP3.8501.../2420018 | Starting Issue Call By Customer Name :-Keshav . Mobile No :- 9812500061 | Task Start | Keshav S/o. Rajender Kumar | M/s OM Diesels Pvt. Ltd. - Sirsa | 25 | Jerk load on DG , customer side AC issue, the DG jerk load was going to 40 A when the AC compressor started. Educated the customer about the same. | Closed | Kapil Solanki | KRM check | Check KRM data and found it Jark load at the time of starting customer use 70 % load at the time of starting.
2 | 211096365 | 21-08-2024 11:31 | 57 | T4.8941.../2420007 | Power Supply Issue Call By Customer Name:-Pankaj Sharma No:-9760283050 | Closed | Brij Satya Associates | R K Engineers - Meerut | 29 | Customer side panel issue R phase output was 0 Volt, DG side no issue , educated the customer about the same issue resolved. | Closed | Sudhir Awasthi
3 | 211096431 | 21-08-2024 11:44 | 250 | F6.8841.../2420063 | Alarm Problem | Task Start | The Kidney Hospital | Vishal Power Systems - PANIPAT | 5.32 |  |  |  | Details awaited
4 | 211097144 | 21-08-2024 14:43 | 125.4 | 4H.8041.../2420067 | Starting Issue Call By Customer Name :-Pritam Mobile No :-9414013952 | Open | Mona Power Trading | M/s OM Diesels Pvt. Ltd. - Sonipat | 546 | Starting issue due to the fuel filter was choke and air filter clean the filter issue resolved. | Closed | Kapil Solanki
5 | 211097180 | 21-08-2024 14:57 | 30 | 3H.8902.../2420647 | Starting Issue Email by KGD Name - Sanjeev Jain | Open | Neofit Udyog | Industrial Power Solutions - LUDHIANA | 4 | DG was tripping with showing emergency stop alarm , engineer checked wiring found 4 PIN Connector was loose tighten the same issue resolved. | Closed | Ved Gupta
6 | 211097254 | 21-08-2024 15:11 | 30 | 3H.8902.../2320065 | Starting Issue Email by KGD Name - Ashutosh Kumar Singh | Task Start | Nippi Kochhar | Vidyut Engineers - New Delhi | 29 | update pending | Open | Kapil Solanki
7 | 211097309 | 21-08-2024 15:23 | 125.4 | 4H.8041.../2320073 | Oil Leakage issue Email By - Service Dealer Name -Saurabh Singh | Task Start | GUPTA SAREES CENTRE | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 274 | lube oil leakage from filter , tighten the same issue resolved. | Closed | Kapil Solanki
8 | 211097323 | 21-08-2024 15:27 | 125.4 | 4H.8041.../2420404 | Starting Issue Call By Customer Name :-Deepak Kumar Mobile No :-9147372801 | Open | Style Baazar Santragachi | Espiem Engines & Machines (P) Limited - Banda | 47 | staring issue due to E- feed pump clamp was loose condition , tighten the same issue resolved. | Closed |  | GEOM issue
9 | 211097430 | 21-08-2024 15:58 | 15 | GP3.8501.../2420010 | Coolant Leakage Issue Call By Customer Name: -Manish Kumar Number: -9034331195 | Open | Bharat X Ray and Ultra Sound Clinic. | Vishal Power Systems - Karnal | 57 | Coolant leakage from radiator out hose pipe (minor leakage) tighten the same issue resolved. | Closed | Kapil Solanki
10 | 211097431 | 21-08-2024 15:58 | 25 | GP3.8702.../2420110 | Tripping Issue Call By Customer Name :-Vivek Agrawal Mobile No :- 9971719027 | Open | The Wash Club | M/s OM Diesels Pvt. Ltd. - Sonipat | 17.1 | DG was tripp with showing under speed alarm , found DG was running unbalanced load , (23A,1A,1A) educated the customer about the same issue resolved. | Closed | Kapil Solanki
11 | 211097989 | 21-08-2024 17:22 | 15 | GP3.8501.../2320024 | Alarm Issue Email By - Service Dealer Name -Akanksha Tyagi | Closed | Shri Panchmukhi Sewa Trust | GLOBALVISION POWER SOLUTIONS PVT LTD - Haridwar | 64 | Starting issue with showing red lamp ON , found lube oil switch wire was loose condition , correct the same issue resolved. | Closed | Kapil Solanki
12 | 211098164 | 21-08-2024 17:41 | 160 | 6H.8475.../2320030 | Abnormal Sound issue Call By Customer Name : Rabbani. No:- 9015201975 | Closed | Deal Infotech Pvt. Ltd. | Vidyut Engineers - Noida | 141.46 | customer complained about abnormal sound issue , engineer did not found any issue , SPN/FMI -1761/17,1761/16 Clear the DTC issue resolved. | Closed | Kapil Solanki
13 | 211098357 | 21-08-2024 18:53 | 125.4 | 4H.8041.../2420118 | AMF Panel Starting Issue Call By Customer Name :- Pintu No :- 9818237427 | Closed | Swastham Medicare LLP. | Vidyut Engineers - Noida | 166.4 | automation issue due to negative sensing wire was loose in DG panel tighten the same issue resolved. | Closed | Kapil Solanki
14 | 211098985 | 22-08-2024 09:19 | 15 | GP3.8501.../2420015 | Maintenance Due Alarm Issue Call By Customer Name:-Manish Gupta No:-Manish Gupta | Task Start | Manish Gupta | Vishal Power Systems - Karnal | 60 | Starting issue due to emergency switch was press condition , correct the same issue resolved. | Closed | Kapil Solanki
15 | 211099239 | 22-08-2024 10:42 | 125.4 | 4H.8041.../2420469 | Tripping Issue Call BY Customer Name :- Rajesh No :- 9468609826 | Task Start | Vanshika Metals | Pratap Diesels Pvt. Ltd. - JAIPUR |  | update pending | Open
16 | 211099291 | 22-08-2024 10:51 |  | T4.8941.../2421651 | Crank sensor damaged | Task Start | Green Field Enterprises | Suraj Motor Store - kathua |  | Crank sensor was damaged.need to be change. | Open | Ved Gupta | GEOM ISSUE
17 | 211099305 | 22-08-2024 10:52 | 500 | DV8.8501.C4../2320054 | Rain water leakage Issue Call By Customer Name : Rashid Khan No : 7906235121 | Open | Rama Vision Ltd. | Deep Jyoti Electricals and Services - Haldwani |  | SR will be cancel , no issue in DG . | cancelled | Sudhir Awasthi
18 | 211099335 | 22-08-2024 11:01 | 500 | DV8.8501.C4../2420074 | Error Code issue Email By - Service Dealer Name -KAJAL | Task Start | Shree Enterprises India Pvt. Ltd. | Industrial Power Solutions - LUDHIANA | 18 | DEF level was low bank A @33% and bank B @45% educated the customer about the same issue resolved. | Closed
19 | 211099415 | 22-08-2024 11:01 |  | T4.8941.../2421672 | Crank Sensor damaged | Task Start | Green Field Enterprises | Suraj Motor Store - kathua |  | Crank sensor was damaged.need to be change. | Open | Ved Gupta | GEOM issue
20 | 211099448 | 22-08-2024 11:08 | 400 | DV8.8542.C4../2320006 | Abnormal Sound Issue Email by Service Dealer Name - Deepak Kumar | Task Start | PUSH UP TOOLS UDYOG (P) LIMITED | M/s OM Diesels Pvt. Ltd. - Rohtak | 135.34 | Starting issue due to battery was discharge , found Fuse blown (MR to MR1 ) replace the same issue resolved. | Closed | Kapil Solanki
21 | 211099470 | 22-08-2024 11:09 | 20 | GP3.8601.../2320024 | Maintenance Due Alarm Issue Call By Customer Name :- Paras Kumar Mobile No :- 7210984804 | Task Start | M/s R G A Exports Pvt Ltd | Vidyut Engineers - Noida | 59.35 | Maintenance due alarm showing on controller reset the alarm also DG was running unbalance load and overload , educated the customer about the same issue resolved.(service due) | Closed | Kapil Solanki
22 | 211099548 | 22-08-2024 11:29 | 500 | DV8.8501.C4../2420058 | Preventive Maintenance Call By Customer Name :-Mohmmad Javed Mobile No :-9953556010 | Task Start | Regal Emporia Infratech Pvt. Ltd. | Vidyut Engineers - Noida | 19.41 | DEF level was low, bank A @14% and bank B @19% educated the customer about the same issue resolved. | Closed | Kapil Solanki
23 | 211099627 | 22-08-2024 11:48 | 57 | T4.8941.../2320261 | Starting Issue Call By Customer Name :-Sanjeev Kumar Mobile No :-9717092665 | Task Start | Kalina Overseas Pvt. Ltd. | Vidyut Engineers - Noida | 114.42 | DG was tripping with showing over current and under speed alarm , Found DG was running unbalance load and overload (17A,54A,28A) | Closed | Kapil Solanki
24 | 211099703 | 22-08-2024 12:06 | 125.4 | 4H.8041.../2420468 | Alarm Problem Email By Service Dealer Name:-Sandeep | Task Start | Kavya Enterprises. | Vishal Power Systems - PANIPAT | 61 | Starting issue , found fuel suction tube bolt was loose condition , tighten the same issue resolved. | Closed | Kapil Solanki | geom issue
25 | 211099740 | 22-08-2024 12:17 |  | GP3.8702.../2420158 | CAM SENCER ISSUE | Task Start | IEC BARWALA | SAAN Royal Power Solutions Private Limited - Zirakpur |  | Cam sensor issue, CAM sensor used to touch cam tone wheel, dismantle the timing wheel and clean it, under observation | Open | Ved Gupta
4 | 211089456 | 18-08-2024 16:01 | 320 | F6.8802.../2320013 | Under Voltage Alarm & ECE Amber issue Call By Customer Name:- Roshanlal Number:- 9672175373 | Open | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar |  | Intake gasket was damage , today will replace the gasket, | Open
| 211098408 | 21-08-2024 19:45 | 400 | DV8.8542.C4../2320002 | Battery and Canopy Issue Call By Customer Name :-Navnath Mobile No :-7304928174 | Task Start | HINDUSTAN UNILIVER LTD | Transcreek Engineers Pvt. Ltd. - Mumbai | 28 | battery water overflow from the battery cap Water level found below from max. check specific G and cell to cell battery voltage voltage | Open | Jagdeep Saini | Under observation
| 211097857 | 21-08-2024 17:03 | 320 | F6.8802.../2420086 | belt issue | Task Start | KALA GENSET PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | V- belt broke replaced the same | Closed | Jagdeep Saini
| 211097294 | 21-08-2024 15:30 | 82.5 | 5H.8901.../2420020 | Tripping Issue Email by Service Dealer Name - Nilesh Dabhade | Closed | Baba International | Transcreek Engineers Pvt. Ltd. - Ambernath | 247 | Low Adblue level showing 6%, top-up the same and educate the customer | Closed | Jagdeep Saini
| 211097293 | 21-08-2024 15:22 | 0 | T4.8941.../2421392 | fuel pipe issue | Task Start | Kala Genset Pvt. Ltd | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | broke rurn pipe dispached from kagal | Closed | Jagdeep Saini
| 211097255 | 21-08-2024 15:10 | 0 | T4.8941.../2421100 | controller issue. | Task Start | KALA GENSET PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | controller faulty dispach today from kagal | Closed | Jagdeep Saini
| 211097156 | 21-08-2024 14:46 | 500 | DV8.8501.C4../2420027 | Contolleor Issue Call By Customer Name :- Kundan Mobile No :- 7000786897 | Closed | Swastik Electrotech Private Limited | Transcreek Engineers Pvt. Ltd. - Mumbai | 21.5 | customer required expansion module, enable and set the parameter as customer requirement | Closed | Jagdeep Saini
| 211096863 | 21-08-2024 13:13 | 125.4 | 4H.8041.../2420644 | Starting issue | Task Start | Aplika Healthcare Pvt. Ltd. | Transcreek Engineers Pvt. Ltd. - Ambernath |  | Can comm. Failed btw GCU and ECU check resistance in GCU H/L- 0ohm instruct to eng. To replace the controller. | Closed | Jagdeep Saini
| 211092199 | 20-08-2024 10:13 | 40 | 3H.8951.../2420152 | Low Speed Alarm and Output Supply issue and Automation issue Call By Customer Name :-Santosh Mobile No :-9309917524 | Closed | Pawman Parinam LLP. M. L. L. | Dhanashree Technocrats Pvt. Ltd. - Nasik | 17.6 | use welding machine, block load 30-40 amp icrease the excitation from 236V to 240V. | Closed | Jagdeep Saini
| 211088369 | 17-08-2024 16:39 | 0 | GP3.8702.../2420518 | Abnormal Sound | Closed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | oil not present in rocker lever comm. To kagal plant person they dennied to dismental and take return the engine. | Closed | Jagdeep Saini
1 | 211100244 | 22-08-2024 14:32 | 58.5 | T4.8941.../2420381 | Starting Issue Email by Service Dealer Name - Surya Power Services | Task Start | UKB. Construction MGT. Pvt. IT. | Surya Power Services - Bangalore | 0.45 | customer wants mains sensing for auto mode . | Closed | --
2 | 211099901 | 22-08-2024 12:54 | 25 | GP3.8702.../2420116 | Starting Issue Email by Service Dealer Name - B.kalyani | Task Start | Vedire Sriram. | Powerlinks Infra Tech Pvt Ltd - Secunderabad | 2.11 | water pump failure , detail update ASE give today . | Closed | Mr. Saleem | Details required | leakage from water pump . photo & video atteched .
3 | 211099496 | 22-08-2024 11:21 | 40 | 3H.8951.../2420184 | engine not start | Task Start | VJS. Phytosanitary Service | Genearth Services - Tuticorin | - | flickring issue | Open | Mr. Nanda Gopal | same case has been opened in Tirunelveli for voltage flickering.We planned to replace the flywheel with high mass inertia flywheel.After resolution of that case we will apply same resolution here.
4 | 211098254 | 21-08-2024 18:09 | 30 | 3H.8902.../2320143 | Voltage Fluctuation Issue Email By - Service Dealer Name -GURUMURTHY | Closed | VESARA HARDWARE & INTERIOR SOLUTIONS | Surya Power Services - Bommasandra, Bangalore | 3 | engine voltage fluctuations due to neutral connection loosing then retight the neutral connection and started the engine running condition found ok a | Closed | -- | Details required
5 | 211097455 | 21-08-2024 16:02 | 25 | GP3.8702.../2420275 | Starting Issue Email by Service Dealer Name - K.Ramya, | Closed | Aditya Recycling Industry | Laxmi Diesels - Kakinada | 3.32 | observed 3 phase sensing problem so rectified the sensing wires and tightened the all electrical connections then started | Closed | Mr. Saleem
6 | 211095793 | 21-08-2024 09:02 | 40 | 3H.8951.../2320041 | Engine not starting Email By - Service Dealer Name -Veena | Task Start | Contrive. | Surya Power Services - Peenya, Bangalore | 2 | engine not star , connection loose( In X2 , 2B1 ,) tightend the same problem resolved | Closed | --
1 | 211097254 | 21-08-2024 15:11 | 30 | 3H.8902.../2320065 | Starting Issue Email by KGD Name - Ashutosh Kumar Singh | Task Start | Nippi Kochhar | Vidyut Engineers - New Delhi | 29 | During SD team, Engine started normally in auto as well as manual mode, no issue found. | closed | Kapil Solanki
2 | 211099239 | 22-08-2024 10:42 | 125.4 | 4H.8041.../2420469 | Tripping Issue Call BY Customer Name :- Rajesh No :- 9468609826 | Task Start | Vanshika Metals | Pratap Diesels Pvt. Ltd. - JAIPUR | 5 | customer side load issue (Customer have heating load ) when customer increase load then DG power factor goes 0.3 , educated the customer about the same issue resolved. | closed | Ved Gupta
3 | 211099974 | 22-08-2024 13:09 | 200 | 6H.8435.../2320031 | AFM Panel issue Call By Customer Name: -Aditya Aryan Number: -8839388441 | Task Start | OIL INDIA LTD. | Rajdhani Diesels and Electricals - Jodhpur | 805 | DG was not start in auto mode , found AMF panel VMR was fault , educated the customer about the same issue resolved. | Closed
4 | 211100075 | 22-08-2024 13:46 | 25 | GP3.8702.../2420378 | Starting Problem | Open | Jakson & Company | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Starting issue with showing SPN/FMI - 3510/3 , checked engine wiring harness and control panel wiring harness found , RRT suggest to replace common rail and crank sensor | Open
5 | 211100078 | 22-08-2024 13:48 | 200 | 6H.8435.../2320035 | Coolant Consumption issue Call By Customer Name :-Subhash Gupta Mobile No :-9810367509 | Closed | EAST WEST RESCUE PRIVATE LIMITED | Vidyut Engineers - New Delhi | 24.46 | Coolant leakage from Loose Hose clip, SD team tigten the same then leakage stopped but needs urgent replacment. | Closed | Kapil Solanki
6 | 211100260 | 22-08-2024 14:38 | 160 | 6H.8475.../2420036 | Starting Issue Call By Customer Name - Satya . Mo No -7974148281 | Task Start | JUBILANT FOOD WORKS LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | Starting issue due to emergency switch was press condition , correct the same issue resolved. | Closed | Kapil Solanki
7 | 211100329 | 22-08-2024 14:52 | 15 | GP3.8501.../2420084 | Low Speed Alarm issue Call By Customer Name :-G. S. Sandhu. Mobile No :-9996610001 | Task Start | G. S. Sandhu. | SAAN Royal Power Solutions Private Limited - Zirakpur | 59 | Starting issue with showing red lamp ON , found lube oil switch wire was loose condition , correct the same issue resolved. | Closed | Ved Gupta | Service check
8 | 211100332 | 22-08-2024 14:55 | 57 | T4.8941.../2420455 | Starting Issue Email By Service Dealer Name:-SUNITA | Task Start | Meerut Ptfe Products Pvt. Ltd | R K Engineers - Meerut | 24 | SPN/FMI - 653/5 ,Found 4 no cylinder injector connector was loose condition, refitted same the issue resolved. | Closed | Sudhir Awasthi | KRM check
9 | 211100354 | 22-08-2024 15:01 | 125.4 | 4H.8041.../2420050 | Red Lamp Alarm issue Call By Customer Name :-Raghuvi Kumar Mobile No :- 8076404542 | Closed | International Automotive Components | Paluck Technologies Ltd. - Faridabad |  | SPN/FMI - 7598/7,4095/1 checked dosing module connector , supply module connector, DEF Tank connector found ok , clear the DTC . | Closed | Kapil Solanki | KRM check
10 | 211100536 | 22-08-2024 15:31 |  | GP3.8702.../2420298 | CAMP SENSOR ISSUE | Task Start | IEC BARWALA | SAAN Royal Power Solutions Private Limited - Zirakpur |  | SPN/FMI - 5838/1,2791/2,2791/5,2791/1 Related to EGR valve , need to replace EGR | Open | Ved Gupta
11 | 211100589 | 22-08-2024 15:35 | 125.4 | 4H.8041.../2320182 | Starting Issue Call By Customer Name :-Balvir Singh Mobile No :-9911175431 | Closed | SS. Generators | Paluck Technologies Ltd. - Faridabad | 227 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
12 | 211100654 | 22-08-2024 15:51 | 125.4 | 4H.8041.../2420675 | Oil Sensor issue Call By Customer Name :-Akshat Mobile No :-9058439345 | Task Start | Mr. Akshat Jain | R K Engineers - Muzaffarnagar | 27 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Sudhir Awasthi
13 | 211101150 | 22-08-2024 17:12 | 82.5 | 5H.8901.../2420010 | Oil Sensor Issue Call By Customer Name :-Manjul Sharma Mobile No :-9654783690 | Task Start | Falcon Autotech Private Limited | Vidyut Engineers - Noida | 56.37 | SPN/FMI - 4095/1, 6595/0, 1761/16, clear the DTC issue resolved. | Closed | Kapil Solanki
14 | 211101223 | 22-08-2024 17:29 | 40 | 3H.8951.../2420270 | Display issue Call By Customer Name: -Satendra Number: -9990085351 | Task Start | Har Shree Nath Service Station | OVN Industries Private Limited - New Delhi | 15.37 | controller not turned ON , Found distribution box XDBK1 2C wire was loose condition tighten the same issue resolved. | Closed | Kapil Solanki
15 | 211101581 | 22-08-2024 20:44 | 125.4 | 4H.8041.../2420099 | White Smoke Issue ,and Urea Issue Call By Customer Name:Mahendra Mobile:9891432295 | Task Start | Service Bazar | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 17 | DEF level was low , @0% educated the customer about the same issue resolved. | Closed | Kapil Solanki
16 | 211101961 | 23-08-2024 08:07 | 62.5 | T4.8941.../2320245 | Starting Issue Call By Customer Name:-Jaspir No:-9729181174 | Task Start | R. P. Stone Clinic Pvt. Ltd. | Vishal Power Systems - PANIPAT | 202 | Door lock issue, adjust the lock issue resolved. | Closed | Kapil Solanki
18 | 211102029 | 23-08-2024 09:36 | 30 | 3H.8902.../2420461 | Emergency stop alarm issue Call By Customer Name :- Jagdish Kumar Mobile No :- 9557001020 | Task Start | ICICI Bank | R K Engineers - Meerut | 11 | DG was tripping with showing emergency stop alarm , engineer checked wiring found 4 PIN Connector was loose tighten the same issue resolved. | Closed | Sudhir Awasthi
19 | 211102291 | 23-08-2024 10:52 | 125.4 | 4H.8041.../2420050 | Red Lamp Alarm Issue Call By Customer Name :-Raghuvi Kumar Mobile No :- 8076404542 | Task Start | International Automotive Components | Paluck Technologies Ltd. - Faridabad | 271 | SPN/FMI - 4095/2 , Checked dosing found ok , checked supply module pump voltage found 5 volt , checked (2A1 TO 2A8 ) fuse box found ok , checked NOx sensor connector found ok , clear the DTC and keep under observation. | Open | Kapil Solanki
20 | 211102373 | 23-08-2024 11:10 | 125.4 | 4H.8041.../2320033 | Tripping Issue & Preventive Maintenance Call By Â KGD Name :-Gurpreet Kaur Mobile No :9311523743 | Task Start | Kumar Generator House | Paluck Technologies Ltd. - Ghaziabad | 320 | SPN/FMI - 51/0 ,3031/14, checked ITV connector found ok , clear the DTC and flash the file issue resolved. | closed | Kapil Solanki
21 | 211102399 | 23-08-2024 11:16 | 15 | GP3.8501.../2420489 | KRM Issue Call By Customer Name :-Furkhan Ansari Mobile No :-9125542667 | Task Start | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW | 78 | KRM live parameter was not showing due to KRM (15,16) NO wire was open condition , correct the same issue resolved. | Closed | Sudhir Awasthi
22 | 211102405 | 23-08-2024 11:16 | 40 | 3H.8951.../2420081 | Silencer issue Call By Customer Name :-Sahil Sharma Mobile No :-9953965999 | Task Start | NEW BHARDWAJ ELECTRICAL WORKS | Paluck Technologies Ltd. - Faridabad |  | Expansion below was damaged need to replace | Open | Kapil Solanki
23 | 211102535 | 23-08-2024 11:53 | 125.4 | 4H.8041.../2420488 | Starting Issue Call By Customer Name :-Kartik Sir Mobile No :-9991773089 | Open | Sagar Steel & Wires | M/s OM Diesels Pvt. Ltd. - Rohtak | 21 | Starting issue due to start delay time was 0 sec , also cooling down period 20 sec , correct the same issue resolved. | Closed | Kapil Solanki
24 | 211102584 | 23-08-2024 11:56 | 500 | DV8.8501.C4../2420022 | Fuel sensor Issue Email by Service Dealer Name - Shiv | Task Start | BVG. India Ltd. | Vidyut Engineers - Noida | 70.15 | Incorrect fuel level was showing , change fuel level direction , and keep it under observation | Closed | Kapil Solanki
25 | 211102617 | 23-08-2024 12:03 | 15 | GP3.8501.../2420570 | KRM Issue Call By Customer Name :-Furkhan Ansari Mobile No :-9125542667 | Task Start | Faiyaz Green Power. | S. R Engines Sales And Service - LUCKNOW | 53 | KRM live parameter was not showing due KRM wire was interchange between 15 no and 16 no , correct the same issue resolved. | Closed | Sudhir Awasthi
26 | 211102622 | 23-08-2024 12:03 | 320 | F6.8802.../2420041 | Filter Issue Call By Customer Name:-Sudhir Narve No:-8447621198 | Closed | M/S EINS TECHNIK PRIVATE LIMITED | Paluck Technologies Ltd. - Ghaziabad | 113 | fuel filter change , at CSP time filter was not available | Closed | Kapil Solanki
27 | 211102753 | 23-08-2024 12:28 | 82.5 | 5H.8901.../2320033 | Starting Issue Call By Customer Name :-Rehan Khan Mobile No :-9667078756 | Task Start | MIRA ENGINEERING PVT LTD | Vidyut Engineers - Noida | 15.6 | starting issue due to battery was discharge , found mains supply wire was open in DG panel , correct the same issue resolved. | Closed | Kapil Solanki
28 | 211102844 | 23-08-2024 12:43 | 57 | T4.8941.../2320004 | Inspection/Maintenance | Open | SUN N SAND INDIA | M/s OM Diesels Pvt. Ltd. - Rohtak |  | visit pending | Open | Kapil Solanki
29 | 211102853 | 23-08-2024 12:49 | 82.5 | 5H.8901.../2420009 | Amber lamp Alarm | Open | ANAND PRAYAG UDYOG | Paluck Technologies Ltd. - Faridabad |  | SR will be cancel ,no issue in DG | cancelled | Kapil Solanki
30 | 211103006 | 23-08-2024 13:38 | 15 | GP3.8501.../2420619 | ENGINE STARTING ISSUE Email By - Service Dealer Name -SUNITA | Task Start | Sandeep Bansal. | R K Engineers - Saharanpur | 14.36 | tripping issue , engineer checked event log found under speed alarm , checked air line and fuel line found ok . Change GCU parametter speed for ECU - Enable to disable | Closed | Kapil Solanki
1 | 211103059 | 23-08-2024 14:05 | 310 hp | F6.8841.../2420207 | ENGINE TRIPPING ISSUE | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | engine run on 100 % load for 9 min. After that it get tripped , due to overheat (engine high temp. alarm came ) engg. check physically , radiator top tank portion found hot. issue is still there. | Open | Mr. Nanda Gopal
2 | 211102470 | 23-08-2024 11:29 | 15 | GP3.8501.../2420313 | Starting Problem Call by : Customer Name : Tara Contact :9741840702 | Task Start | Nawfal N. | Prasad Power Engineers - Puttur | 1.3 | Engine not starting. Crank disconnect timing changed from 3 sec to 6 sec. Engine running OK. | Closed | --
3 | 211102423 | 23-08-2024 11:21 | 200 | 6H.8435.../2420066 | ERROR ISSUE | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | fault code - SPN 363 /8 , engg. flash the ecu , check the continuty , sensor replaced , ecu replacement , camton wheel bolt found loose so tightend the same , problem resolved . | Closed | Mr. Nanda Gopal
4 | 211102416 | 23-08-2024 11:21 | 20 | GP3.8601.../2420062 | Supply problem Call by : customer Name : Senthil Contact : 9787220696 | Task Start | Bobby and Boba Saloons Private Limited | Madurai Electro Controls - Sivakasi | 9 | rotor replacement is in progress along with nidec team | Closed | Mr. Nanda Gopal | DONE
5 | 211105917 | 24-08-2024 11:45 | 125.4 | 4H.8041.../2420322 | STARTING PROBLEM | Open | Rathnakala Jewellery | Electro Controls - Thiruvananthapuram | 24 | ECU fault - Checked the all connections, Reduced the cooldown time 5mins 75secs and increased the load transfer delay 2 sec 15sec | cancelled | Mr. Nanda Gopal | Under observation
6 | 211105914 | 24-08-2024 11:42 | 0 | GP3.8601.../2420493 | fly wheel assly issue | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | visit pending . | Closed | Mr. Nanda Gopal | flywheel replaced with new one , previous flywheel not alliance properly
7 | 211105827 | 24-08-2024 11:20 | 125.4 | 4H.8041.../2420379 | Starting Issue Call By Customer Name :-Bhasker Mobile No :-9840037168 | Task Start | K. K. Precast Concrete Pvt. Ltd. | Madhu Engineering Sales & Service - Teynampet,Chennai | 4 | pending at ASE end . | Closed | Mr. Nanda Gopal | error code issue , refiitted all the connections and clear the error code , problem resolved .
8 | 211105668 | 24-08-2024 10:48 | 250 | F6.8841.../2420128 | .. | Task Start | AKSHAYAKALPA FARMS AND FOODS PRIVATE LIMITED | Surya Power Services - Peenya, Bangalore | 3 | customer raise the SR for auto sensing enable . | Closed | --
9 | 211104674 | 23-08-2024 18:25 | 200 | 6H.8435.../2420070 | Wiring harness | Open | Ripple Developers Pvt. Ltd. | Powerlinks Infra Tech Pvt Ltd - Hyderabad | LR | ambient temp. sensor , continuity not found during troubleshooting.so changed the wiring harness . | Closed | Mr. Saleem | Failed part
1 | 211102703 | 23-08-2024 12:12 |  | 4H.8041.../ 2420527 | Engine failed to start | Task Start | POWERLINE GREEN | Hibreed Engineering Pvt. Ltd . - Nagaon | 0.56 | Found RPM fluction with fault code 3103/14, after inspection found that the fuel suction tube touching the base of fuel tank,hence reuce the length issue resolved. | OPEN | Subhrajit Roy
3 | 211101996 | 23-08-2024 09:28 | 58.5 | T4.8941.../ 2420624 | Error Code Issue Email by Customer Name -Yadav tent house | Task Start | Yadav Tent House | Globalline India Services Private Limited - Darbhanga | 100 | customer raised the SR for error code water in fuel engineer reset the alarm issue resolved. | OPEN | Prabhakar Kumar | KRM check | Check KRM and found it the 2802/ 3 ,5838/1 , related to the Engine Exhaust Gas Recirculation Valve Malfunction-Low - most severe
4 | 211107275 | 24-08-2024 18:05 | 20 | GP3.8604.../ 2420068 | INSTANCE ID:-100740939 SITE ID:- I-BR-AKGL-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-MAINS CONTRACTOR FAULTY NAME:-YADHAV NUMBER:-8700143490 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Sasaram | NA | visit pending | OPEN | Prabhakar Kumar
5 | 211106974 | 24-08-2024 16:40 | 125.4 | 4H.8041.../ 2420557 | VOC- Amber lamp Alaram issue /MALFUNCTIONING/FLASHING/ TAMPERING.Customer Name -Heto Yeptho Customer Number - 8837040440 Mode- SR Generated through CDI calling. | Open | Heto Yeptho. | M/s Hindustan Powerkraft - Dimapur | 3 | SR raised by customer need to discuss with customer on details | OPEN | Subhrajit Roy
6 | 211106846 | 24-08-2024 16:04 | 15 | GP3.8501.../ 2320023 | Earthing Issue Email By - Customer Name -Avijit Saha | Task Start | GHL. Pharma & Diagnostic Pvt. Ltd. | Globalline India Services Private Limited - Muzaffarpur | NA | Customer plan today(monday) joint visit with Electrician team | OPEN | Prabhakar Kumar | Details pending
1 | 211106174 | 24-08-2024 12:51 | 500 | DV8.8501.C4../2320096 | Starting and Abnormal Sound Issue Call By Customer Name :-Omkesh Mobile No :-8698625886 | Closed | Majestique Empire LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Wagholi - Pune | 18 | Battery discharged, battery charger not connect with Mains, correct the same issue resolved | Closed | Jagdeep Saini
2 | 211105645 | 24-08-2024 10:44 | 58.5 | T4.8941.../2420587 | Display issue Call By Customer Name : -Sujit Kapadi No:-9823380189 | Closed | Vrundavan Co. Op Housing Society Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | na | Canopy emergency Switch stucking correct the same and clear the alarm | Closed | Jagdeep Saini
3 | 211101529 | 22-08-2024 18:52 | 20 | GP3.8601.../2420471 | ENGINE NOT START. | Closed | Prakash Uday P. Wing Co. Operative Housing Society. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | na | Amf panel issue, no issue with DG. | Closed | Jagdeep Saini
4 | 211100275 | 22-08-2024 14:47 | 25 | GP3.8702.../2420180 | Oil Leakage Issue, Coolant Leakage Issue Call by Customer Name:Pradip Kumar Shelar Number:8983196943 | Closed | Malpani Retails Private Limited. | Dicksons Engineering Co.Pvt.Ltd. - Ahmednagar | 40 | Oil and coolant leakage from sump and pullley side fix it with proper sealant, issue resolved | Closed | Jagdeep Saini
5 | 211099894 | 22-08-2024 12:49 | 1000 | DV8.8502.C4../2420003 & 2420003 | Starting Issue Email By - Service Dealer Name -Nilesh Kate | Completed | Majestique Homes LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | 6 | spn-523576/0 adblue not received in supply moidule A bank Interchange the supply module and tank header btw A bank and B bank, but issue remain same found dosing module faulty replace the same issue resolved. | OPEN | Jagdeep Saini | Failed part. KRM check
6 | 211098408 | 21-08-2024 19:45 | 400 | DV8.8542.C4../2320002 | Battery and Canopy Issue Call By Customer Name :-Navnath Mobile No :-7304928174 | Task Start | HINDUSTAN UNILIVER LTD | Transcreek Engineers Pvt. Ltd. - Mumbai | na | Battery water overflow again in single cell,Charging alternator voltage- 27V, clean the cell, under observation | OPEN | Jagdeep Saini | Baatery number and photo
7 | 211092308 | 20-08-2024 10:44 | 20 | GP3.1021.../2420127 | CHECKING | Task Start | Reliance Jio Infocomm Limited | Mahalaxmi Diesels - Satara | na | Mains contactor not close replace the same issue resolved | Closed | Jagdeep Saini
8 | 211114386 | 26-08-2024 17:11 | 58.5 | T4.8941.../2421357 | ENGINE NOT START. | Completed | Pushpam Infra LLP. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | LR | fault code 652/5 shown in controller, Injector open, today visit for more details. | OPEN | Jagdeep Saini | Details required
9 | 211114195 | 26-08-2024 16:39 | 0 | 5H.5357.../2400001 | Desox and Ad Blue Error Email By - Service Dealer Name - Tanmay A Shinde | Task Start | Bomag India Private Limited | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | 350 hrs | Desox alarm shown, def tank to supply pipe leakage, replace the same and done desox activity. | Closed | Jagdeep Saini
10 | 211112409 | 26-08-2024 12:53 | 750 | DV2.8501.C4../2320013 | Water Leakage Issue Email by Service Dealer Name - Tanmay A Shinde | Task Start | Faster Hydraulics Pvt. Ltd. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | Canopy water leakage | Closed | Jagdeep Saini
11 | 211112267 | 26-08-2024 12:19 | 160 | 6H.8475.../2420118 | Red Lamp On Alarm Issue Call By Customer Name :- Mobile No :- | Closed | Lifeline Mauli Hospital LLP. | Dicksons Engineering Co.Pvt.Ltd. - Beed | 50 | Low Adblue level, top up and educate the customer | Closed | Jagdeep Saini
12 | 211105275 | 24-08-2024 08:49 | 58.5 | T4.8941.../2420034 | KRM Unit Issue Email by Service Dealer Name - Dharmendrasinh | Closed | Pravesh Paper Pvt. Ltd. | Unique Techno Services Pvt Ltd. - Gandhidham | 4 | KRM Issue. | Closed | Amit Shandilya
13 | 211105274 | 24-08-2024 08:46 | 625 | DV2.8552.C4../2320005 | Breather Pipe Clamp Issue Email by Service Dealer Name - Dharmendrasinh Zala | Closed | ADANI RENEWABLE ENERGY FIFTY SEVEN LIMITED | Unique Techno Services Pvt Ltd. - Gandhidham | 1022 | Breather pipe clamp was loose. | Closed | Amit Shandilya
1 | 211102844 | 23-08-2024 12:43 | 57 | T4.8941.../2320004 | Inspection/Maintenance | Task Start | SUN N SAND INDIA | M/s OM Diesels Pvt. Ltd. - Rohtak | 336 | Maintenance due alarm, just reset the same, DG Service due. | Closed | Kapil Solanki
2 | 211103924 | 23-08-2024 15:40 | 250 | F6.8841.../2420050 | Water in fuel | Closed | Hinata Polymers | Vidyut Engineers - Noida | 55.15 | DG tripping due to Water in Fuel safety, No Physical water present, bypass the same issue resolved, suspected WIF Sensor faulty | Closed | Kapil Solanki | Details required
3 | 211103948 | 23-08-2024 15:45 | 125.4 | 4H.8041.../2420619 | Automation Issue Email by Customer Name - Sangeeta Malhotra | Closed | Shekhar Gupta. | Vidyut Engineers - New Delhi | 3.9 | Stopping Failure alarm in auto panel, Issue in Other vendor Auto Panel, Customer will arrange visit from Auto Panel vendor. | Closed | Kapil Solanki
4 | 211104230 | 23-08-2024 16:46 | 25 | GP3.8702.../2420302 | Error Code Issue Email By Service Dealer Name:-Rahul Sharma | Task Start | Aryadhenu Misthanshala | M/s OM Diesels Pvt. Ltd. - HISAR |  | Cam Sensor related DTC, Voltage Supply & continuity missing, EDO placed for Harness. | Open | Kapil Solanki
5 | 211104480 | 23-08-2024 17:39 | 750 | DV2.8501.C4../2320003 | Oil Leakage Issue Call By Customer Name :- Vinod Sharma Mobile No :-9953098687 | Task Start | MRS. Bectors Food Specialities Ltd. | Paluck Technologies Ltd. - Gurgaon | 114 | Engine Oil leakage from Cam sealing cap, Place EDO for new Sealing Cap, Under transit. | Open | Kapil Solanki
6 | 211104734 | 23-08-2024 19:00 | 160 | 6H.8475.../2420036 | High Voltage Alarm Issue Call By Customer Name :- Singh .. Number :- 9667593079 | Task Start | JUBILANT FOOD WORKS LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 5 | Main Alternator Output Voltage Low, R : 150, Y : 160 & B : 150, Checked in By pass condition found OK, suspecetd AVR acrd faulty | Open | Kapil Solanki
7 | 211105305 | 24-08-2024 09:20 | 125.4 | 4H.8041.../2320134 | Error code Issue Call By Customer Name :- Kasidh Ahmad Mobile No :- 8445820675 | Closed | M/S SWASTIK PESTICIDES LIMITED | R K Engineers - Muzaffarnagar | 773 | SPN/FMI 51/2 (ETV Jam) Checked Voltage supply & continuity, found Ok, Chceked for its butterfly valve for any restriction, no abnormality observed, Just reset the DTC & kept under observation | Open | Sudhir Awasthi | iTV need to check
8 | 211105452 | 24-08-2024 10:10 | 125.4 | 4H.8041.../2320004 | Stopping Issue Call By Customer Name:-Indersen Yadav Mobile No.8826817371 | Closed | ARIHANT INDUSTRIAL EQUIPMENT | Vidyut Engineers - New Delhi | 173 | DG start/stop normally, no issue observed during visit, SD team highlited Oil bkeackening issue | Closed | Kapil Solanki | KRM data
9 | 211105654 | 24-08-2024 10:44 | 58.5 | T4.8941.../2420289 | Automation Issue Call By Customer Name :- Bharat Kumar Mobile No :- 7879001370 | Task Start | Geeta Kanwar. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 27 | Issue in Auto panel (Other Vendor), Customer will arrange their Visit | Closed | Kapil Solanki
10 | 211105658 | 24-08-2024 10:45 | 500 | DV8.8501.C4../2420046 | Starting Problem | Task Start | Advantec Wheels Pvt. Ltd. | Suraj Motor Store - Jammu |  | SPN/FMI : 97/5 WIF DTC because of Wire break in Panel also no DEF consumption in 2 Bank, Clean the Dosing module with Hot Water, Issue resolved. | Closed | Ved Gupta
11 | 211105659 | 24-08-2024 10:46 | 25 | GP3.8702.../2420067 | Starting Issue Email By - Service Dealer Name -Priya Dogra | Task Start | Instrumentation and Survey Innovative Solutions | Suraj Motor Store - Jammu |  | Oil leakage from Flywheel end Oil seal, Part not reflecting in Pluse, matter takeup with EDO team. | Open | Ved Gupta
12 | 211105749 | 24-08-2024 11:05 | 160 | 6H.8475.../2320012 | Starting Issue Call By Customer Name :-Dharam Pal Singh Mobile No :- 9887007215 | Task Start | FLEXIPOL FOMAS PVT LTD | Pratap Diesels Pvt. Ltd. - Bhiwadi | 151 | DG Starting issue because of Water traces & other impurites observed in Water Separator, Just clean the Filter & suggested Customer for Fuel tank cleaning. | Open | Gaurav Sharma | Fuel sample
13 | 211105834 | 24-08-2024 11:25 | 25 | GP3.8702.../2420008 | Starting Issue Email by Service Dealer Name - Suman Yadav | Task Start | Godrej Projects Development Limited | Paluck Technologies Ltd. - Gurgaon | 644 | SPN/FMI 110/16 (High Coolant temp) because of Low coolant level, Just topup the same, taken trial no any overheating observed. | Closed | Kapil Solanki | KRM check
14 | 211105960 | 24-08-2024 11:58 | 15 | GP3.8501.../2420184 | Diesel Leakage Issue Call by customer Name:Mahendra . Mobile No.7988030751 | Task Start | Sanjay Corporate Services | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Visit pending | Open | Gaurav Sharma
15 | 211105984 | 24-08-2024 11:58 | 125.4 | 4H.8041.../2320062 | Alarm Issue Call By Customer Name :- Sunil No :- 9871579643 | Task Start | Shiv Industries | M/s OM Diesels Pvt. Ltd. - Sonipat | 293 | ECU fault also low DEF level, SD team not carrying iKonnect Tool, Will revisit the site with Tool. | Open | Kapil Solanki
16 | 211106100 | 24-08-2024 12:27 | 125.4 | 4H.8041.../2420241 | Starting Issue Call By Customer Name :- Vijay Shankar Mobile No :- 8604463502 | Closed | MALABAR GOLD PRIVATE LIMITED | OVN Industries Private Limited - New Delhi | Wrong Hrs | LOW DFE level & DTC 2761, Top up DEF, also DG servive due. | Closed | Kapil Solanki
17 | 211106102 | 24-08-2024 12:27 | 15 | GP3.8501.../2420018 | Starting issue Call By Customer Name : -Keshav No:-9812500061 | Closed | Keshav S/o. Rajender Kumar | M/s OM Diesels Pvt. Ltd. - Sirsa | 67 | DG tripping due to OverLoad, Event log alos indicate the same, Educated Customer to manage the Load. | Closed | Kapil Solanki
18 | 211106262 | 24-08-2024 13:04 | 250 | F6.8841.../2420042 | Tripping Â Issue Call By Customer Name :-Vijay Kumar Mobile No :-9795586504 | Closed | Bharat Petroleum Corporation Ltd. Loni | Paluck Technologies Ltd. - Ghaziabad | 34 | Visit to demonstrate all Safety system in DG, Requierment Customer Safety/Audit Dept | Closed | Kapil Solanki
19 | 211106265 | 24-08-2024 13:04 | 750 | DV2.8501.C4../2420014 | Tripping Â Issue Call By Customer Name :-Vijay Kumar Mobile No :-9795586504 | Closed | Bharat Petroleum Corporation Ltd | Paluck Technologies Ltd. - Ghaziabad | 173 | Visit to demonstrate all Safety system in DG, Requierment Customer Safety/Audit Dept | Closed | Kapil Solanki | Will update with demonstration
20 | 211106668 | 24-08-2024 15:10 | 250 | F6.8841.../2420146 | ECU AMBER WARNING | Open | ATLAS POWER & EQUIPMENTS | M/s OM Diesels Pvt. Ltd. - Sonipat | 32.38 | SPN/FMI : 516166/0 (ECU internal malfunction) As Customer doing Hot Shutdown also DEF Level low, Top up DEF & Educated Customer, Issue resolved. | Closed | Kapil Solanki
21 | 211107026 | 24-08-2024 17:04 | 30 | 3H.8902.../2320106 | Inspection/Maintenance | Cancelled | Aggarwal The Handloom Shop | OVN Industries Private Limited - New Delhi |  | SR Cancelled | Cancelled | Kapil Solanki
22 | 211107084 | 24-08-2024 17:10 | 200 | 6H.8435.../2320025 | Coolant leakage & Abnormal sound issue Email By - Customer Name -castnylonindia | Task Start | M. Safe India | Pratap Diesels Pvt. Ltd. - Bhiwadi | 74 | Oil leakage from Loose Filter & Abnormal sound from V-belt, Tighten the same, Issue resolved. | Closed | Gaurav Sharma
23 | 211107282 | 24-08-2024 18:01 | 20 | GP3.8601.../2320024 | Over Heating issue Call By Customer Name : Paras .. No:- 9871594029 | Closed | M/s R G A Exports Pvt Ltd | Vidyut Engineers - Noida | 60 | High Coolant temp because of Low coolant level, Just topup the same, taken trial no any overheating observed. | Closed | Kapil Solanki | KRM check | KRM data does not avavilbe in protal so check KRM wire and send mail of KRM team.
24 | 211107853 | 25-08-2024 08:56 | 320 | F6.8802.../2320013 | ECE Amber issue Call By Customer Name:- Roshanlal Number:- 9672175373 | Open | TINA ORGANICS PVT LTD | Pratap Diesels Pvt. Ltd. - Alwar |  | Visit pending | Open | Gaurav Sharma
25 | 211107870 | 25-08-2024 10:20 | 125.4 | 4H.8041.../2420451 | Load issue Call by customer Name:-Rahul No:- 9216518995 | Closed | R. K. Tower. | Pratap Diesels Pvt. Ltd. - Ajmer | 7.11 | Some DTC in iKonnect, Just reset by SD team (Need proper update) | Closed | Gaurav Sharma
26 | 211109985 | 25-08-2024 15:41 | 250 | F6.8841.../2420050 | Warning showing Water in fuel & ECU Protect Email By KGD Name:- Ashutosh kumar Singh | Task Start | Hinata Polymers | Vidyut Engineers - Noida | 69 | WIF & ECU protection lamp alarm, SD team found Water traces in Fuel, Cleaned Fuel Tank, Water Seperator & Pre Filter then 1 hour trial, Issue resolved, DEF Level @ 49 %, DFE topup also done. | Closed | Kapil Solanki | Details Pending
27 | 211110021 | 25-08-2024 17:31 | 160 | 6H.8475.../2420031 | Fan Belt Issue Call By Â Customer Name :-Rohit Malik Mobile No :-9999637245 | Task Start | TRAIN HIGH | OVN Industries Private Limited - New Delhi | 640 | 6K V-belt broke, Replaced the same, Issue resolved | Closed | Kapil Solanki
28 | 211110042 | 25-08-2024 17:36 | 160 | 6H.8475.../2420007 | Red Lamp Alarm Issue Call by Customer Name:Shanvaj No:6397306121 | Closed | OMNIE SOLUTIONS INDIA PRIVATE LIMITED | Vidyut Engineers - Noida | 123 | Low DEF Level, Abnormal sound from V-belt also Battery Voltage low (11.8 volts) as Battery charger connection not done, Battery connection done, tighten V-Belt & Top Up DEF, Issue resolved. | Closed | Kapil Solanki
29 | 211110872 | 25-08-2024 20:54 | 125.4 | 4H.8041.../2320021 | DG not start | Open | Kavita Gupta & Sushil Gupta | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 40 | Starting issue due to 2C wire loose in XDBK1 block, tighten the same, Issue resolved. | Closed | Kapil Solanki
30 | 211111628 | 26-08-2024 09:12 | 160 | 6H.8475.../2420007 | ECU Protect Email By - KGD Name - Ashutosh Kumar | Open | OMNIE SOLUTIONS INDIA PRIVATE LIMITED | Vidyut Engineers - Noida | 123 | Duplicate SR | Cancelled | Kapil Solanki
31 | 211111641 | 26-08-2024 09:34 | 750 | DV2.8501.C4../2320047 | Automation issue Call By Customer Name :-Rakesh Mobile No :- 8708612594 | Task Start | Merino Industries Ltd. | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Thermal Shield fitment also issue in Fuel Gauge, corrected the same. | Closed | Kapil Solanki
32 | 211111823 | 26-08-2024 10:24 | 250 | F6.8841.../2420123 | Synchronization Issue Call By Service Dealer Name :-Poonam Singh Mobile No :-7722070569 | Cancelled | Kids Clinic India Pvt Ltd | S. R Engines Sales And Service - LUCKNOW |  | SR Cancelled | Cancelled | Sudhir Awasthi
32 | 211111885 | 26-08-2024 10:38 | 125.4 | 4H.8041.../2420439 | Door Lock issue Call by customer Name: Charan Singh No:-9812754609 | Open | Baba Amarnath Enterprises. | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Visit pending | Open | Gaurav Sharma
34 | 211111982 | 26-08-2024 11:00 | 500 | DV8.8501.C4../2420048 | Alternator Issue Call By Customer Name:Rajkumar Mobile No:9467425910 | Closed | Shahi Dyeing Pvt. Ltd. | Paluck Technologies Ltd. - Faridabad | 266 | Visit with NIDEC to Excessive Vibration issue, axial,Horigental.dg checked without load and on load by nidec person .limit at NDE SITE V=11.2 MM,H=12.2MM ,A=5.0MM, No excessive Vibration observed, Issue resolved. | Closed | Kapil Solanki
35 | 211112045 | 26-08-2024 11:15 | 125 | F6.9840.../2420006 | Starting Issue Call By Customer Name :-Kamlesh Mobile No :-9211196063 | Open | C. S. Export Noida Uttar Pradesh. | Vidyut Engineers - Noida |  | PNG Set, Oil leakage from Flywheel end Oil seal, Replaced Oil seal, this SR generated by Customer for CC. | Closed | Kapil Solanki
36 | 211112146 | 26-08-2024 11:48 | 125.4 | 4H.8041.../2320187 | Starting Issue Call By Customer Name :-SK Bhingraj Mobile No :-9837313870 | Task Start | Rush Enterprises | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 45 | SPN/FMI 6595/0, Just reset the DTC also 3P VPR Faulty in Auto Panel (Non-KOEL) | Closed | Kapil Solanki | Details required about SCR system. ikonnect log
37 | 211112235 | 26-08-2024 12:06 | 200 | 6H.8435.../2320031 | Failure of VMR Email By - KGD Name - Mayur Vira | Open | OIL INDIA LTD. | Rajdhani Diesels and Electricals - Jodhpur |  | Visit pending | Open | Gaurav Sharma
38 | 211112268 | 26-08-2024 12:19 | 500 | DV8.8501.C4../2320035 | Tripping Issue Call by Customer Name - Hari Om Number - 8447703201 | Closed | Sidhi International Metal Alloys P. Ltd. | Paluck Technologies Ltd. - Faridabad | 144 | No DEF Consumption in Bank 2 (Dosing Pressure not build up), SD team just cleared the DTC | Closed | Kapil Solanki | ECU alert check
39 | 211112451 | 26-08-2024 13:06 | 15 | GP3.8501.../2420293 | Starting Issue Email By - Service Dealer Name -Rahul Sharma | Task Start | Dr. Sandeep Malik. | M/s OM Diesels Pvt. Ltd. - HISAR | 8 | Visit for Auto Panel connections | Closed | Kapil Solanki
40 | 211112808 | 26-08-2024 14:49 | 320 | F6.8802.../2320018 | ECU Alarm and Tripping Issue Call By Customer Name :-Manoj Mobile No :-9660005612 | Open | Geeta Metal | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | Visit pending | Open | Gaurav Sharma
41 | 211114730 | 26-08-2024 18:18 | 250 | F6.8841.../2420015 | Maintenance Due Alram Issue Call By Customer Name :-Kamal Mobile No :-9810725601 | Task Start | Nestle Cooprative Appartment Group Housing | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 46 | Low DEF level, Top up done also educated Customer to fill itself. | Closed | Kapil Solanki
1 | 211107275 | 24-08-2024 18:05 | 20 | GP3.8604.../ 2420068 | INSTANCE ID:-100740939 SITE ID:- I-BR-AKGL-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-MAINS CONTRACTOR FAULTY NAME:-YADHAV NUMBER:-8700143490 | Open | Reliance Jio Infocomm Limited | Globalline India Services Private Limited - Sasaram | NA | Required to cancel the SR, change the mains contactor in AMC instead of warranty. | OPEN | Prabhakar Kumar
2 | 211112832 | 26-08-2024 15:03 | 125.4 | 4H.8041.../ 2320003 | Display Issue Email By Service Dealer Name:-Bitupon Bora | Task Start | N.K. CONSTRUCTION & SUPPLIERS | Hibreed Engineering Pvt. Ltd . - Nagaon | 54.6 | DEF level showing NA in controller also fault code 1761/16 was showing after inspection found that controller(KG640C) of version R00 is installed,hence place the EDO for suitable version R01 controller. | OPEN | Subhrajit Roy
1 | 211111912 | 26-08-2024 10:49 | 25 | GP3.8702.../2420093 | Starting Problem Call by : Customer Name : Shibin Sir Contact : 9048183466 | Open | S.B.J. Associates. | G-Care Diesels Private Limited - Thrissur | 9 | Battery connection was loose ,retightened the same. Issue resolved. | Closed | Mr Sanjaymon
2 | 211110898 | 25-08-2024 20:53 | 40 | 3H.8951.../2320046 | Starting Issue Call By Customer Name - Sence Kurian Number - 9446066944 | Task Start | Pavithra Gold | Madurai Electro Controls - Theni | 7 | Neutral link found blown due to load unbalancing. | Closed | Mr. Nanda Gopal
3 | 211107013 | 24-08-2024 16:51 | 15 | GP3.8501.../2420644 | EARTING NOT DONE | Task Start | Capella Restaurant. | Prasad Power Engineers - Mangalore | 1 | Earthing connection was not done during commissioning. | Closed | -
4 | 211106091 | 24-08-2024 12:23 | 15 | GP3.8501.../2420111 | Charging Alternator Issue Email By - Service Dealer Name -G. SRIDEVI | Closed | Ms. Anjani Foods Limited. | Laxmi Diesels - Visakhapatnam | 1.6 | Battery discharged because 40 A fuse found blown. | Closed | Mr. Saleem
1 | 211112763 | 26-08-2024 14:35 | 40 | 3H.8951.../ 2420018 | Black Smoke Issue Call by customer Name:Prashant .. Mobile No. 6287971824 | Closed | R. K. Dayal Nursing Home & Resarch Center | Globalline India Services Private Limited - Muzaffarpur | 39 | customer raise the SR for smoke, engineer start the engine no such issue found. | CLOSED | Prabhakar Kumar
2 | 211112731 | 26-08-2024 14:27 | 125.4 | 4H.8041.../ 2420405 | CODE ISSUE | Task Start | Pir Baba Enterprise | K.C. Diesel Services - SILIGURI | 6 | Engineer attended the site and found that customer do hot shut down ,SPN- 516166 was showing in display hence engineer just stop the engine and again start issue resolved. | CLOSED | Prosanjit saha
3 | 211112359 | 26-08-2024 12:47 | 15 | GP3.8501.../ 2420558 | Starting Issue Call By Customer Name :-Arbaz Khan Mobile No :-9354530087 | Task Start | Dr. Raj Kkumar Jha | Globalline India Services Private Limited - Muzaffarpur | 2.45 | VOC- that engine not starting in auto mode after inspection engineer found that mains monitoring is disable hence enable the mains monitoring,issue resolved. | CLOSED | Prabhakar Kumar | GCU program check
4 | 211106846 | 24-08-2024 16:04 | 15 | GP3.8501.../ 2320023 | Earthing Issue Email By - Customer Name -Avijit Saha | Closed | GHL. Pharma & Diagnostic Pvt. Ltd. | Globalline India Services Private Limited - Muzaffarpur | 53 | issue from Customer UPS system,no issue from DG side customer open the SR for joint Visit. | CLOSED | Prabhakar Kumar
1 | 211117738 | 27-08-2024 18:00 | 58.5 | T4.8941.../2421375 | oil pressure issue | Completed | KALA GENSET PVT LTD | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | Take full load trail but no issue observed in DG, DG running Ok. | Closed | Jagdeep Saini
2 | 211115675 | 27-08-2024 10:50 | 400 | DV8.8542.C4../2320003 | Led Lamp Issue Call BY Customer Name :- Pranay No :- 8767046579 | Closed | KINGVISH PRIVATE LIMITED | Transcreek Engineers Pvt. Ltd. - Vasai | 49.2 | Low adblue level, top up and educate the customer | Closed | Jagdeep Saini
| 211117008 | 27-08-2024 16:25 | 20 | GP3.1021.../2420245 | INSTANCE ID- 100750227 SITE ID- I-MH-SGMR-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE-DG OVER LOAD ALRAM NAME-RAJEEV NUMBER- 7040809016 | Task Start | Reliance Jio Infocomm Limited | Dicksons Engineering Co.Pvt.Ltd. - Ahmednagar | na | Visit pending | OPEN | Jagdeep Saini
3 | 211112798 | 26-08-2024 14:58 | 750 | DV2.8501.C4../2320020 | Canopy Issue Call By Customer Name :-Vishal Mobile No :-9023111868 | Open | Comed Chemicals Limited | Unique Techno Services Pvt Ltd. - Baroda | 122 | Canopy Issue. Given For cancellation. | Closed | Amit Shandilya
4 | 211112642 | 26-08-2024 14:07 | 40 | 3H.8951.../2420253 | Emergency Stop Alarm Issue Call By Customer Name :-Mahadev Patel Mobile No :-6268242888 | Task Start | Mahadev Patel | Natraj Power Tech - Barwani | Na | Given For cancellation because problem solved by phone. | Closed | Vijay Patil
5 | 211104196 | 23-08-2024 16:43 | 20 | GP3.8601.../2420313 | KRM Issue Call By Customer Name :-Om Patel ... Mobile No :-9099905626 | Task Start | Indigo. | Unique Techno Services Pvt Ltd. - Ahmedabad | Na | KRM Issue.Genset parameter are not showing in KRM portal. | OPEN | Amit Shandilya
6 | 211099775 | 22-08-2024 12:28 | 750 | DV2.9312.../2300002 | Error Code Issue & Starting Issue Call By Customer Name :- Ashwin No :- 9979091137 | Closed | Shree Ganesh Remedies Limited. | Unique Techno Services Pvt Ltd. - Ankleshwar | na | ECU malfunction,ECU protect and ECU Amber alarm are showing .Problem solved after falsh the ECU. | Closed | Amit Shandilya | KRM check
7 | 211116411 | 27-08-2024 13:42 | 20 | GP3.1021.../2420013 | INSTANCE ID :- 100744671 SITE ID :-I-GJ-THRD-ENB-G002 CALL BY CUSTOMER// DG ISSUE :- DG COMMON ALARM FAULTY NAME :- MAHENDRA NUMBER :-9265437219 | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Mahesana | 17 | Common fault alarm showing in the controller.Checked the wiring continuity and voltage found OK.Problem solved after replacing LLOP switch. | Closed | Amit Shandilya
1 | 211116588 | 27-08-2024 14:43 | 15 | GP3.8501.../2420053 | Preventive Maintenance Call by : Customer Name : Mahesh Contact : 9578274149 | Open | S. R. A. Agencies | Bharath Diesel Sales and Service - Pudukottai | 414 | Customer requested for oil service | Closed | Mr. Nanda Gopal
2 | 211116248 | 27-08-2024 13:08 | 250 | F6.8841.../2420147 | In Display Fuel Level Not seen Problem Call by : Customer Name :Sujith Sir Contact :6282505191 | Open | AR. Handlooms | G-Care Diesels Private Limited - Thrissur | 49 | Visit Pending | Closed | Mr Sanjaymon |  | Connector issue. Reconnected the connectors. Issue resolved
3 | 211115874 | 27-08-2024 11:37 | 500 | DV8.8501.C4../2320090 | Line Rejection | Task Start | T. T. P. Technologies Pvt. Limited. | Prasad Power Engineers - Tumkur | LR | ECU anti vibration spring damage while attending for CC | Closed | -- | Photos of failre part | Spring photo attached.
4 | 211115687 | 27-08-2024 10:48 | 15 | GP3.8501.../2420654 | LINE REJECTION | Task Start | K. G. D. Vidyuth. | Prasad Power Engineers - Hassan | LR | earthing connection is not done by KGD | Closed | --
5 | 211114226 | 26-08-2024 16:44 | 58.5 | T4.8941.../2421006 | Starting Issue Email By KGD Name:-M.K.GURUMURTHY | Task Start | Aarka Construction | Surya Power Services - Peenya, Bangalore | 1 | 633 fault code related to metering unit .shown on controller ,issue facing to connect, I-connect tool , so today again enng. visit the site | Closed | -- | Update pending | 2A wire found loose in XDBK4 distribution block.Photo attached
6 | 211113199 | 26-08-2024 16:16 | 0 | 3H.8902.../2420896 | FUEL LEAKAGE | Task Start | SUNBEAM GENERATORS PVT LTD | Bharath Diesel Sales and Service - Puducherry | LR | injector fuel return hose damage, at GOEM end, EDO placed. | Closed | Mr. Nanda Gopal
1 | 211115341 | 27-08-2024 04:33 | 25 | GP3.8702.../2420086 | Starting Issue Call By Customer Name :-Amkiuj Jindal Mobile No :-9888202615 | Closed | Shree Luxmi Fasteners. | Industrial Power Solutions - LUDHIANA | 13 | DG was tripping with showing under speed alarm engineer checked air line fuel line found ok , then reset the alarm issue resolved. | Closed | Kapil Solanki | Under observation
2 | 211115354 | 27-08-2024 08:22 | 30 | 3H.8902.../2420177 | Error Code issue Call By Customer Name :-S.K. Bajaj Mobile No :-8233604489 | Task Start | U. M. A. Bajaj | Pratap Diesels Pvt. Ltd. - Alwar |  | SR cancel no issue in DG | cancelled
3 | 211115496 | 27-08-2024 09:54 | 57 | T4.8941.../2420055 | Auto Panel Issue Preventive Maintenance Call By Customer Name :-Dr. Ashok Kumar Gupta Mobile No :-9811182011 | Closed | JP. Memorial Hospital | Vidyut Engineers - New Delhi | 39.1 | automation issue , some time DG was start with out power cut , found mains high voltage , educated the customer about the same issue resolved . | Closed | Kapil Solanki
4 | 211115521 | 27-08-2024 10:12 | 125.4 | 4H.8041.../2420367 | Ad blue issue Call BY Customer Name :- Dhanish No :- 9810350842 | Closed | Jain Metal. | Paluck Technologies Ltd. - Faridabad | 19 | Customer want to know who to open the DEF cap , educated the customer about the same issue resolved | Closed | Kapil Solanki
5 | 211115555 | 27-08-2024 10:22 | 750 | DV2.8501.C4../2320033 | Diesel Leakage Issue Email By - Service Dealer Name -Deepak Kumar | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 202.51 | Fuel leakage from , fuel filter banjo , tighten the same issue resolved . | Closed | Kapil Solanki
6 | 211115582 | 27-08-2024 10:23 | 750 | DV2.8501.C4../2320024 | Diesel Leakage Issue Email By - Service Dealer Name -Deepak Kumar | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 204 | SR open for DG check purpose | Closed | Kapil Solanki
7 | 211115584 | 27-08-2024 10:23 | 750 | DV2.8501.C4../2320005 | Diesel Leakage Issue Email By - Service Dealer Name -Deepak Kumar | Task Start | BHARAT RASAYAN LTD | M/s OM Diesels Pvt. Ltd. - Rohtak | 291.34 | as previous discussion , exhaust gas leakage from exhaust below , change the gasket , turbo red hot issue remain same. | Closed | Kapil Solanki
8 | 211115615 | 27-08-2024 10:34 | 250 | F6.8841.../2320038 | Controller faulty Call By Customer Name : -Tej Pratap Singh No:-7428506588 | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Visit pending | Open | Kapil Solanki
9 | 211115617 | 27-08-2024 10:34 | 250 | F6.8841.../2420004 | Diesel Consumption issue Call By Customer Name : -Tej Pratap Singh No:-7428506588 | Task Start | TATA TELESERVICES LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Visit pending | Open | Kapil Solanki
10 | 211115729 | 27-08-2024 10:58 | 40 | 3H.8951.../2420096 | Preventive Maintenance Call BY Customer Name :- Ramjna NO :- 8130797147 | Closed | Purvanchal Projects Pvt Ltd | Vidyut Engineers - Noida | 809.2 | Preventive maintenance alarm showing on controller , reset the alarm and issue resolved . | Closed | Kapil Solanki
11 | 211115956 | 27-08-2024 11:59 | 25 | GP3.8702.../2420008 | Oil Leakage Issue Email By Service Dealer Name:-Saurabh Rajput | Closed | Godrej Projects Development Limited | Paluck Technologies Ltd. - Gurgaon | 645 | Fuel filter and air filter change , at CSP time fuel filter not available | Closed | Kapil Solanki
12 | 211115972 | 27-08-2024 11:56 | 320 | F6.8802.../2320024 | ECU Amber Alarm Call By Customer Name :-Kali Shankar Warma Mobile No :-9871170836 | Closed | KLK. Venture Pvt. Ltd. | Vidyut Engineers - Noida | 117.14 | DEF level was low , top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
13 | 211116023 | 27-08-2024 12:11 | 125.4 | 4H.8041.../2420671 | Add blue issue Call By Customer Name :- Rajesh Kumar Mobile No :- 9452389413 | Open | Archit Enterprises | S. R Engines Sales And Service - LUCKNOW |  | Visit pending | Open
14 | 211116025 | 27-08-2024 12:11 | 500 | DV8.8501.C4../2420058 | Starting Issue Call By Customer Name:Rohit Kumar Number:9920868795 | Closed | Regal Emporia Infratech Pvt. Ltd. | Vidyut Engineers - Noida | 22.33 | DEF level was low , educated the customer about the same issue resolved. | Closed | Kapil Solanki
15 | 211116148 | 27-08-2024 12:40 | 15 | GP3.8501.../2420174 | DG not starting-462038 | Closed | ICICI Bank Limited | Pratap Diesels Pvt. Ltd. - Bhilwara | 17.5 | SPN/FMI - 96/4 Related to fuel level , found fuel level was low top the fuel and educated the customer about the same issue resolved. | Closed
16 | 211116304 | 27-08-2024 13:20 | 250 | F6.8841.../2420117 | automation Issue call By Customer name ;Mukesh Saroj Number ;9873521845 | Closed | Zivore Apparel Private Limited | Vidyut Engineers - Noida | 14.46 | customer have non koel auto panel , but load cable and mains connection was not done , engineer suggest to customer checked auto panel supplier | Closed | Kapil Solanki
17 | 211116576 | 27-08-2024 14:35 | 15 | GP3.8501.../2420183 | Automation Issue Call By Customer Name :- Girdas Singh Mobile No :- 8586860155 | Task Start | CIPL. Corporate Infotech Pvt. Ltd. | Vidyut Engineers - Noida |  | Automation issue ,DG was not stop in auto mode found AMF panel wiring was wrong correct the same issue resolved (Jakson AMF panel) | Closed | Kapil Solanki
18 | 211116654 | 27-08-2024 14:59 | 250 | F6.8841.../2420144 | White Smoke issue call by KGD Name - Gurpreet Kaur Mo No -9311523743 | Task Start | S. S. Buildwell Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 18.1 | Customer complain about starting issue , engineer did not found any issue . Checked fuel line found ok . | Closed | Kapil Solanki | KRM check | Due Low FUEL genset trip.
1 | 211115509 | 27-08-2024 10:00 | 15 | GP3.8501.../2320026 | AVR | Task Start | Superwave Communication & Infrasolution Pvt. Ltd. | Excel Diesel Private Limited - Sultanpur |  | In Load Line There is UPS connected with DG Power Supply load Line, so there is flickering in voltage. DG 15 KVA but UPS Load is 10 Kva. | Closed | Sudhir Awasthi
2 | 211115615 | 27-08-2024 10:34 | 250 | F6.8841.../2320038 | Controller faulty Call By Customer Name : -Tej Pratap Singh No:-7428506588 | Task Start | Tata Tele services | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | No issue in DG | Closed | Kapil Solanki | KRM check
3 | 211115617 | 27-08-2024 10:34 | 250 | F6.8841.../2420004 | Diesel Consumption issue Call By Customer Name : -Tej Pratap Singh No:-7428506588 | Task Start | TATA TELESERVICES LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Customer want to know fuel consumption , educated the customer about the same issue resolved . | Closed | Kapil Solanki
4 | 211115950 | 27-08-2024 11:56 | 57 | T4.8941.../2420085 | Starting Issue Email By Service Dealer Name:-Akash | Task Start | MK. Tubes Industries Pvt. Ltd. | Espiem Engines & Machines (P) Limited - Aligarh | 92
5 | 211116023 | 27-08-2024 12:11 | 125.4 | 4H.8041.../2420671 | Add blue issue Call By Customer Name :- Rajesh Kumar Mobile No :- 9452389413 | Open | Archit Enterprises | S. R Engines Sales And Service - LUCKNOW |  | Visit pending | Open | Sudhir Awasthi
6 | 211116410 | 27-08-2024 13:41 | 40 | 3H.8951.../2320050 | Silencer issue bd Call By Customer Name:- Omveer Singh Number:- 7011204885 | Task Start | Chaudhary Generator Service | Paluck Technologies Ltd. - Ghaziabad | 1679 | expansion below change under warranty | Closed | Kapil Solanki
7 | 211116468 | 27-08-2024 13:58 | 15 | GP3.8501.../2420006 | DG automation required | Task Start | BHARTI AIRTEL LIMITED | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 4 | starting issue due to MPU connector was loose, correct the same issue resolved. | Closed | Kapil Solanki
8 | 211116705 | 27-08-2024 15:01 | 200 | 6H.8435.../2420006 | Power Supply Issue Call By Customer Name :-Sumit Mobile No :-9873609379 | Task Start | Cut Sharp Machine Knives Manufacturing Co. LLP. | Vidyut Engineers - Noida | 12.2 | Load cable was wrong connection , correct the same issue resolved. | Closed | Kapil Solanki
9 | 211116714 | 27-08-2024 15:04 | 125.4 | 4H.8041.../2420066 | Voltage Fluctuation | Task Start | Welcome Crop Sciences Pvt. Ltd. | OVN Industries Private Limited - New Delhi | 25.7 | SR opened by mistake , no issue in DG | Closed | Kapil Solanki
10 | 211117101 | 27-08-2024 16:54 | 125.4 | 4H.8041.../2420150 | Lighting Issue & Alarm Issue Call By Customer Name :- Rameshvar No :- 9810388104 | Task Start | Anshuman Jain HUF | Vidyut Engineers - New Delhi | 18 | SPN/FMI - 516166/0 just clear the DTC and educated the customer about the same issue resolved. | Closed | Kapil Solanki | Need to check pulse record
11 | 211118226 | 28-08-2024 07:53 | 125.4 | 4H.8041.../2420070 | Inspection/Maintenance | Open | Rivah Industries | Pratap Diesels Pvt. Ltd. - Bhiwadi |  | SR cancel . Need to CSP | cancelled
12 | 211118445 | 28-08-2024 08:08 | 30 | 3H.8902.../2420174 | Starting Issue Call By Â Customer Name :-Harshdeep .. Mobile No :-8434133684 | Closed | Radiance Infraprojects Pvt. Ltd. | Paluck Technologies Ltd. - Gurgaon | 11.18 | starting issue with showing emergency stop alarm , found emergency switch was pressed condition , correct the same issue resolved. | Closed | Kapil Solanki
13 | 211118463 | 28-08-2024 09:08 | 125.4 | 4H.8041.../2420669 | Fuel Sensor Issue Call By Customer Name - Mandal .. Mo No -9599332686.. | Closed | NCC LImited | M/s OM Diesels Pvt. Ltd. - Sonipat | 82 | Update pending | Open
14 | 211118573 | 28-08-2024 10:04 | 20 | GP3.8601.../2420026 | Maintenance Due Alarm Issue Call by Customer Name - Pande .. Number - 9871548462 | Closed | Dr. Avdhesh Bansal. | Vidyut Engineers - Noida | 51.2 | Maintenance due alarm was showing on controller , just reset the alarm issue resolved . | Closed | Kapil Solanki
15 | 211119112 | 28-08-2024 12:12 | 125.4 | 4H.8041.../2420066 | Starting/Stopping Issue | Cancelled | Welcome Crop Sciences Pvt. Ltd. | OVN Industries Private Limited - New Delhi |  | No issue in DG | cancelled | Kapil Solanki
16 | 211119274 | 28-08-2024 12:44 | 62.5 | T4.8941.../2420635 | Tripping Issue Call by customer Name: Shweta . Mobile No. 9958891400 | Closed | Green Energy Diesel Engines Private Limited. | Paluck Technologies Ltd. - Faridabad | 47 | As per customer requirement 225 volt . So reset the V port of AVR 240 volt to 225 volt , issue resolved | Closed | Kapil Solanki
17 | 211119292 | 28-08-2024 12:48 | 500 | DV8.8501.C4../2420022 | Synchronisation Issue Call By Customer Name :-Ramanand .. Mobile No :-9318488758 | Task Start | BVG. India Ltd. | Vidyut Engineers - Noida |  | SR opened for synchronization between 750 kva and 500 kva . | Open | Kapil Solanki
18 | 211120063 | 28-08-2024 16:20 | 125.4 | 4H.8041.../2420107 | Starting/Stopping Issue | Task Start | SNV Overseas | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Visit pending | Open | Kapil Solanki |  | Battery was discharge due to battery charger mains switch off condition correct the same and educated the customer about the same issue resolved
1 | 211119176 | 28-08-2024 12:24 | 20 | GP3.8601.../2420485 | MCB issue Call By Customer Name :- Rohit Matre Mobile No :-Â 8655219880 | Closed | C. S. Petroleum. | Transcreek Engineers Pvt. Ltd. - Panvel | 30 | Not getting output from panel Y phase loose the connection and retighten the same issue resolved | Closed | Jagdeep Saini
2 | 211118555 | 28-08-2024 10:04 | 82.5 | 5H.8901.../2420110 | Starting Issue Email by KGD Name - Samadhan Payghan | Completed | Mr. Dilip Dattaatray Mohite | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan |  | DG start in auto mode whenever mains voltage down as per customer why dg starts when mains is present, educate the customer. | Closed | Jagdeep Saini
3 | 211117008 | 27-08-2024 16:25 | 20 | GP3.1021.../2420245 | INSTANCE ID- 100750227 SITE ID- I-MH-SGMR-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE-DG OVER LOAD ALRAM NAME-RAJEEV NUMBER- 7040809016 | Closed | Reliance Jio Infocomm Limited | Dicksons Engineering Co.Pvt.Ltd. - Ahmednagar | 72 | Òverload tripping issue, trip at 69amp, taken load upto 58 amp. | Open | Jagdeep Saini
4 | 211116088 | 27-08-2024 12:28 | 40 | 3H.8951.../2420196 | LIGHTS FLUCTUATION PROBLEM. | Task Start | Avinash Patil & Associates. | DYNAPULSE ENGINEERING PRIVATE LIMITED - Pune | LR | LED lights fluctuations on DG | Open | Jagdeep Saini
5 | 211119738 | 28-08-2024 15:00 | 30 | 3H.8902.../2420123 | Display Issue Email By Service Dealer Name:-kareena namdev | Closed | Jasprit Singh Bhatia | Natraj Power Tech - Indore | 4 | The battery was discharged because the mains supply was not coming to the battery charger.So genset was not starting. | Closed | Vijay Patil | Does not matain any problem in CC.
6 | 211119512 | 28-08-2024 13:43 | 20 | GP3.1021.../2420144 | INSTANCE ID:-100748384 SITE ID:-I-GJ-MGRL-ENB-G001 CALL BY CUSTOMER\\ DG ISSUE:-dg not starting NAME:-MENSHI NUMBER:-7016523540 | Task Start | Reliance Jio Infocomm Limited | Unique Techno Services Pvt Ltd. - Junagadh | 42 | Visit Pending | Open | Amit Shandilya
7 | 211118447 | 28-08-2024 08:42 | 625 | DV2.8552.C4../2320005 | MAIN ALTERNATOR VOLTAGE PROBLEM Email by Service Dealer Name - Dharmendrasinh Zala | Task Start | ADANI RENEWABLE ENERGY FIFTY SEVEN LIMITED | Unique Techno Services Pvt Ltd. - Gandhidham | 1022 | The output of the main alternator was only 50V to 60V.Genset tripping on under voltage due to terminal burnt at PT connector internally. | Open | Amit Shandilya | Load check
1 | 211118775 | 28-08-2024 10:56 | 0 | 6H.8475.../2420196 | CHARGING ALTERNATOR PROBLEM | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | New Charging alternator Fitted. Previous charging alternator was fitted to another assset. | Closed | Mr. Nanda Gopal
2 | 211118458 | 28-08-2024 09:25 | 58.5 | T4.8941.../2420792 | Starting Issue Email by Service Dealer Name - Laxmi Diesels | Task Start | Sri Vasavi Aarya Vysya Sankshema Sangam | Laxmi Diesels - Kakinada | 2 | Air lock issue | Closed | Mr. Saleem
3 | 211117686 | 27-08-2024 17:41 | 320 | F6.8802.../2420088 | ERROR CODE ISSUE | Open | Bojjaiah Convention | Ultimate Power Source - Ananthapuramu | LR | Visit Pending | Open | Mr. Saleem | Ecu malfunction alarm popup in controller , ECU procurement pending
1 | 211101996 | 23-08-2024 09:28 | 58.5 | T4.8941.../ 2420624 | Error Code Issue Email by Customer Name -Yadav tent house | Task Start | Yadav Tent House | Globalline India Services Private Limited - Darbhanga | na | as per KRM exhaust gas recirculation alarm was showing, today engineer will visit | OPEN | Prabhakar Kumar | Details required
East zone
1 | 211123052 | 29-08-2024 14:08 | 125.4 | 4H.8041.../2420277 | Starting and Plug Point Issue Call By Service Dealer Name: Sharni Mobile No:6292253538 | Open | GBC. Infrastructure Pvt. Ltd. | DIVERSE TECHNO SERVICES PRIVATE LIMITED - Malda | NA | Visit pending | OPEN | Prosanjit saha
1 | 211121609 | 29-08-2024 00:45 | 320 | F6.8802.../2320006 | Trip_Genset_Low_Voltage | Open | Super Seal India Ltd. | Paluck Technologies Ltd. - Faridabad |  | SR cancel , load issue already mail communicated to customer | cancelled | Kapil Solanki
2 | 211121661 | 29-08-2024 07:53 | 20 | GP3.8601.../2320064 | Genset gone into the water Call By Â Service Dealer Name :-Ravindra Singh Mobile No :-9711410917 | Task Start | SR. Power Engineers | Vidyut Engineers - Noida | 55.18 | Water entry in the canopy (silencer side ) just educated the customer about the same. | Closed | Kapil Solanki
3 | 211121851 | 29-08-2024 07:12 | 250 | F6.8841.../2420063 | Starting Issue Call By Customer Name:-Sanjay Agarwal No:-9812192720 | Task Start | The Kidney Hospital | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 7 | "Starting issue , ECU NOT Respond showing ,Checked voltage supply & CAN communication at OBD tool connector & found Excessive voltage in CAN communication, Checked Harness & found CAN high & Low both wire shorted to each other, corrected the same, Issue resolved" | closed | Ved Gupta
4 | 211121866 | 29-08-2024 09:12 | 15 | GP3.8501.../2420015 | Low speed Alarm Call By Customer Name : Manish Gupta No:-9996640702 | Task Start | Manish Gupta | SAAN Royal Power Solutions Private Limited - Yamuna Nagar |  | DG was tripping with showing under speed alarm , checked on load found DG was running jerk load and overload educated the customer about the same issue resolved. | Closed | Kapil Solanki | KRM check
5 | 211121868 | 29-08-2024 09:13 | 15 | GP3.8501.../2420190 | Red Lamp On alarm And Canopy door issue Call By Customer Name:- Rajiv Sood Number:- 9910111991 | Task Start | HIMALAYA GENERATORS | Vidyut Engineers - Noida | 52.39 | maintenance due Alarm showing on Controller , just reset the and door lock issue adjust the lock issue resolved | Closed | Kapil Solanki
6 | 211121979 | 29-08-2024 09:52 | 125.4 | 4H.8041.../2320120 | Exhaustfan issue Call By Customer Name :-Shukla Mobile No :-9368233581 | Task Start | Sundeep Electrodes Pvt. Ltd. | Paluck Technologies Ltd. - Ghaziabad | 201 | abnormal sound from fan side ,found Fan belt support guard was broken , replace the same issue resolved. | Closed | Kapil Solanki | Failed part. Deails of other site
7 | 211122104 | 29-08-2024 10:13 | 125.4 | 4H.8041.../2420103 | Alarm issue Call by customer Name:-Ritesh rakha No:-9999655904 | Task Start | Neelkanth Engineering | Paluck Technologies Ltd. - Mata Mandir, Gurgaon |  | Visit pending | Closed | Kapil Solanki |  | SPN/FMI - 636/8 ,5461/0 , clear the DTC and flashing the cal file issue resolved.
8 | 211122142 | 29-08-2024 10:21 | 200 | 6H.8435.../2420016 | Abnormal Sound Issue and Coolant Consumption Call by Customer Name - Mahendra Singh Number - 8607190606 | Task Start | Berkeley Motors Limited | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 85 | Abnormal sound from radiator side , found fan belt was loose condition tighten the same and coolant leakage from coolant hose pipe tighten the same issue resolved. | Closed | Kapil Solanki | Belt check
9 | 211122191 | 29-08-2024 10:35 | 58.5 | T4.8941.../2421521 | Starting Issue Email by KGD Name - Sanjeev Jain | Open | Sant Nam Dev Sabha. | Industrial Power Solutions - LUDHIANA |  | Visit pending | Open | Ved Gupta |  | Customer not responding on call .may this SR will be cancelled
10 | 211122205 | 29-08-2024 10:35 | 320 | F6.8802.../2320058 | Coolant Leakage Issue Call By Customer Name :-Avneet Kumar Mobile No :-8178330681 | Open | Popcorn Furniture and Lifestyle Pvt. Ltd. | Vidyut Engineers - Noida | 184 | Rain water entry in the canopy , water mixed with fuel cleaned the tank ,and SR opened the GOEM portal. | Closed | Kapil Solanki | QA will share SOP for water drain
11 | 211122208 | 29-08-2024 10:35 | 20 | GP3.8601.../2320063 | emergency switch off Issue Call By Customer Name :-Bharat Bhushan Mobile No :-9810314268 | Task Start | ASHA NAND SR. SEC. SCHOOL | Paluck Technologies Ltd. - Faridabad | 45.3 | DG was tripping with showing emergency stop alarm , engineer provided extra negative supply to emergency switch issue resolved . | Closed | Kapil Solanki
12 | 211116301 | 27-08-2024 13:20 | 125.4 | 4H.8041.../2420722 | Stopping Issue Call By Customer Name:- shaker jain Mo No:9812611999 | Closed | Dhani Power Solutions | SAAN Royal Power Solutions Private Limited - Yamuna Nagar | 2 | Update pending | cancelled
13 | 211122388 | 29-08-2024 11:21 | 30 | 3H.8902.../2320065 | Automation Issue Email by Service Dealer Name - VINAY KUMAR | Closed | Nippi Kochhar | Vidyut Engineers - New Delhi | 29.23 | Starting issue with showing under speed alarm , checked fuel line and air line found ok , just reset the alarm issue resolved. | Closed | Kapil Solanki | KRM check | Check KRM data and found it unblanced load and if visit the site then check the Event log and if problem with load then crroect the load.
14 | 211122495 | 29-08-2024 11:48 | 625 | DV0.8501.C4../2420001 | Battery Charger issue Call by customer Name: Sajan Kumar jha Number:7352065048 | Task Start | VKR. Constructions Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 11 | Customer need to automation , engineer suggest to customer checked auto panel supplier | Closed | Kapil Solanki
15 | 211122499 | 29-08-2024 11:49 | 400 | DV8.8542.C4../2320004 | Charging Charger issue Call by customer Name: Sajan Kumar jha Number:7352065048 | Task Start | VKR. Construction Pvt. Ltd. | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 51 | Customer need to automation , engineer suggest to customer checked auto panel supplier | Closed | Kapil Solanki
16 | 211122556 | 29-08-2024 12:02 | 125.4 | 4H.8041.../2320052 | Starting Issue And KRM Call By Customer Name :- Nikhil Singla Mobile No :- 9971857680 | Closed | Singla Trading Company | Paluck Technologies Ltd. - Faridabad | 64 | SPN/FMI - 5461/0 flash the cal file also coolant level was low . | Closed | Kapil Solanki
17 | 211122600 | 29-08-2024 12:09 | 750 | DV2.8501.C4../2420029 | Amber lamp Alarm Issue Call By Customer Name :-Arjun Singh Mobile No :-9045060805 | Task Start | Capital Developers | Paluck Technologies Ltd. - Mata Mandir, Gurgaon | 11 | Communication Fault related ERROR code need to visit required. | Open | Kapil Solanki
18 | 211122731 | 29-08-2024 12:44 | 40 | 3H.8951.../2320049 | Voltage issue Call By Customer Name : -Rajveershing No:-9810937200 | Task Start | Ruchika Service Station | Vidyut Engineers - New Delhi |  | Update pending | Open
19 | 211122736 | 29-08-2024 12:44 | 320 | F6.8802.../2420023 | ECU Malfunction Alarm And Error Code Issue Â Call By Customer Name :-Virendra ... Mobile No :-9213085622 | Task Start | Pioneer Hose & Hydraulic Pvt. Ltd. | Vidyut Engineers - Noida | 30.4 | DEF level was low, top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
20 | 211122762 | 29-08-2024 12:44 | 160 | 6H.8475.../2320025 | Sound issue Call by customer Name:-Surendra Singh No:-9871932703 | Open | STRIKER INDUSTRIES PRIVATE LIMITED | M/s OM Diesels Pvt. Ltd. - Bahadurgarh |  | Visit pending |  |  |  | DEF level low top up the DEF but DTC not clear , ikonnect tool issue.
22 | 211123039 | 29-08-2024 14:09 | 500 | DV8.8501.C4../2420135 | Load Problem | Task Start | Madhu Shree Industries | Pratap Diesels Pvt. Ltd. - Alwar | 4 | Line rejection SR , DG was tripping with showing under voltage and under speed alarm , need to check load analyzer Data | Open | Kapil Solanki | Load study
23 | 211123095 | 29-08-2024 14:22 | 125.4 | 4H.8041.../2320163 | Starting Issue & Alarm issue Call By Customer Name :- Rajeev No :- 8459775078 | Task Start | Panchachuli Sehkari Aavak Samiti | Vidyut Engineers - Noida | 98.21 | DEF level was low, top up the DEF and educated the customer about the same issue resolved. | Closed | Kapil Solanki
24 | 211123408 | 29-08-2024 15:25 | 20 | GP3.8604.../2420139 | Problem.DG Starting Kapsiter faulty | Task Start | Reliance Jio Infocomm Limited | S. R Engines Sales And Service - Gorakhpur |  | Visit pending | Open | Sudhir Awasthi
25 | 211123637 | 29-08-2024 16:13 | 320 | F6.8802.../2420006 | Automation Issue Email By Service Dealer Name:-VINAY KUMAR | Task Start | MODICARE LIMITED | Vidyut Engineers - New Delhi |  | SPN/FMI - 5461/0 , Tool was not connecting , will visit today | Closed | Kapil Solanki |  | SPN/FMI 5461/0 Just clear the DTC issue resolved.
1 | 211122899 | 29-08-2024 13:26 | 20 | GP3.8601.../2420050 | Panel MCL burn issue Call by customer Name:-Ganesh Vishwakarma No:-9309114782 | Task Start | Suzanne Merwanji. | Mahalaxmi Diesels - Goa | 32 | Mains contactor Burnt in AMF panel | Closed | Jagdeep Saini
2 | 211122439 | 29-08-2024 11:41 | 20 | GP3.1021.../2420178 | DG automation Fail. | Cancelled | Reliance Jio Infocomm Limited | Dicksons Engineering Co.Pvt.Ltd. - Aurangabad | na | Control panel wiring burn open in AMC | Closed | Jagdeep Saini | Detail required
3 | 211122037 | 29-08-2024 10:01 | 15 | GP3.8501.../2420466 | Automation Issue Call By Customer Name :-Uday Mobile No :-9960650088 | Closed | Udaykirti Steel | Mahalaxmi Diesels - Pandharpur | na | red lamp on due to low fuel, educate the customer. | Closed | Jagdeep Saini
4 | 211121970 | 29-08-2024 09:51 | 320 | F6.8802.../2420063 | Starting Issue Email by Service Dealer Name - Mahalaxmi Diesels | Closed | HARSHIT TRADE LINK PVT LTD | Mahalaxmi Diesels - Goa | na | Injector wiring Lug replaced. | Closed | Jagdeep Saini
5 | 211119831 | 28-08-2024 15:28 | 82.5 | 5H.8901.../2420252 | SUPPLY MODULE | Completed | KALA GENSET PRIVATE LIMITED | DYNAPULSE ENGINEERING PRIVATE LIMITED - Chakan | na | Supply module connector damage | Closed | Jagdeep Saini
6 | 211119141 | 28-08-2024 12:24 | 15 | GP3.8501.../2420283 | Red Lamp ON Alarm Issue Call by Customer Name - Dattatray Nana Fate Number - 9730302330 | Closed | Dattatray Nana Fate | Mahalaxmi Diesels - Solapur | na | emergency stop in pressed condition. | Closed | Jagdeep Saini
1 | 211122618 | 29-08-2024 12:14 | 250 | F6.8841.../2420155 | Water Mixing in Fuel Issue Email by Service Dealer Name - G. SRIDEVI | Task Start | Ramesh Avantel | Laxmi Diesels - Visakhapatnam | 1.28 | Got the alarm, water in fuel, found Rain water entry inside the canopy, so that water and fuel has mixed. Cleaned the full tank. Video/Photo attached. | Closed | Mr. Saleem | GOEM visit with our ASE
2 | 211122311 | 29-08-2024 10:59 | 320 | F6.8802.../2320071 | Belt Issue Email By Service Dealer Name:-Genearth Services, PM | Task Start | LIFAA SEA FOOD EXPORTS | Genearth Services - Tuticorin | 2.1 | belt cut and oil leakage through fuel pump . change the belt . | Closed | Mr. Nanda Gopal | Details | photo attached.
3 | 211122261 | 29-08-2024 10:49 | 320 | F6.8802.../2420090 | Display problem Call by : Customer Name : Raju Contact :8555073011 | Open | The Name of Nord Angilia Education Infrastructure Pvt. Ltd. | Laxmi Diesels - Visakhapatnam | 13.14 | Customer raised SR for Low adblue level alarm. | Closed | Mr. Saleem
4 | 211121068 | 28-08-2024 18:14 | 58.5 | T4.8941.../2420381 | Starting Issue Email by KGD Name - G S Power Systems | Open | UKB. Construction MGT. Pvt. IT. | Surya Power Services - Bangalore | 74 | Customer raised the SR for mains sensing enable | Closed | --
5 | 211103059 | 23-08-2024 14:05 | 0 | F6.8841.../2420207 | ENGINE TRIPPING ISSUE | Task Start | GENLITE ENGINEERING PRIVATE LIMITED | MULTIVISTA GLOBAL PRIVATE LIMITED - Chennai | LR | at 100% load coolant temp. goes to 98 degree C. and at 110% load controller popup engine high temp. and trip . , Mr. kaleshawar suggest to change the thermostate , tommorow may be change it. | Closed | Mr. Nanda Gopal | They change the thermostate and radiator